When an IO error is detected, the I/O LED is steady.

In the case of non configured IO bus, no errors are reported.

SRS5.7 The system provides module health bit in %SW128 and %SW129 . %SW128.0 is module #1 health; %SW129.15 is module #32 health. A health bit is at 1 if the module is healthy, at 0 if not healthy or not configured.

A compatibility error status is provided in %SW132 with following content. This content is significant only if %S118 is set to 0.

Bits 0 to 14: These bits contain a value from 1 to 64, signifying the network position of the module that cannot be reached. For example, a value of 8 indicates a communications failure in accessing the 8th module on the network.

Bit 15: A value of zero indicates a general communication failure, for example, no power to the module or a break in its input cable.

A value of 1 indicates that communication is possible, but the I/O bus ID received from the module does not match the module type contained in the configuration for that position.

The type of bus error is stored in %SW134 with following values:

| Error Name | Error Value | Description |
| --- | --- | --- |
| IBS_BUS_ERR_NONE | 0 | No error |
| IBS_BUS_ERR_PROBE | 1 | Probe IO base ID error in id cycle |
| IBS_BUS_ERR_IDMISMATCH | 2 | The IO base ID is not match with application configuration |
| IBS_BUS_ERR_IO | 3 | There is error in Interbus data cycle |
| IBS_BUS_ERR_IDCYCLE_ACTIV | 4 | It means that id cycle is active currently. |
| IBS_BUS_ERR_CABLE | 5 | IBS cable is not connected well to CPU. |

Note: %SW134 stores the last detected error; it  is not set to 0 by the system when the error disappears. The user can set this word to 0 after processing the error

Cable disconnection

For the above picture, the user configures 4 Interbus IO bases, but the system can only detect the 1st device.

| System word | Value |
| --- | --- |
| %SW128 | 0x01 |
| %SW129 | 0x00 |
| %SW132 | 2 |

If a connection is established again between Device#1 and Device#2,  then:

| System word | Value |
| --- | --- |
| %SW128 | 0x0F |
| %SW129 | 0x00 |
| %SW132 | 0 |
| %SW134 | IBS_BUS_ERR_PROBE |

Note: %SW134 stores the last detected error; it is not set to 0 by the system when the error disappears.

Error during ID cycle

| System word | Value |
| --- | --- |
| %SW128 | 0x00 |
| %SW129 | 0x00 |
| %SW132 | 1 |
| %SW134 | IBS_BUS_ERR_PROBE |

Cable not plugged into CPU

| System word | Value |
| --- | --- |
| %SW128 | 0x00 |
| %SW129 | 0x00 |
| %SW132 | 1 |
| %SW134 | IBS_BUS_ERR_CABLE |

Configuration mismatch errors

In the above picture, the 3rd device is different from the configuration.

| System word | Value |
| --- | --- |
| %SW128 | 0x0B |
| %SW129 | 0x00 |
| %SW132 | 3 |
| %SW134 | IBS_BUS_ERR_IDMISMATCH |

In the above picture, modules 2 and 3 are mismatched at the same time.

| System word | Value |
| --- | --- |
| %SW128 | 0x09 |
| %SW129 | 0x00 |
| %SW132 | 2 |
| %SW134 | IBS_BUS_ERR_IDMISMATCH |

Configuration mismatch and cable disconnected

If there are probe and mismatch errors at the same time, the system will report the mismatch error first.

After all the mismatch errors have disappeared, then the system will report the probe error.

In the above picture, the device 2 is different from the configuration.

| System word | Value |
| --- | --- |
| %SW128 | 0x01 |
| %SW129 | 0x00 |
| %SW132 | 2 |
| %SW134 | IBS_BUS_ERR_IDMISMATCH |

When the user replaces device 2 with the correct device:

| System word | Value |
| --- | --- |
| %SW128 | 0x03 |
| %SW129 | 0x00 |
| %SW132 | 3 |
| %SW134 | IBS_BUS_ERR_PROBE |

Devices connected and not configured

If the real module number on the Interbus is more than the configuration, the system will report a probe error:

| System word | Value |
| --- | --- |
| %SW128 | 0x03 |
| %SW129 | 0x00 |
| %SW132 | 3 |
| %SW134 | IBS_BUS_ERR_PROBE |