| M340 | System Bits & Words |  |
| --- | --- | --- |
| %S0 coldstart | Cold Start | Normally at 0, this bit is set to 1 by: - power restore with loss of data (battery fault), - the user program, - the terminal, - a change of cartridge, - program loading. |
| %S1 warmstart | Warm Restart | Normally at 0, this bit is set to 1 by: - power restore with data save, - the user program, - the terminal, - a change of cartridge, It is reset to 0 by the system at the end of the 1st complete cycle & before the outputs are updated. |
| %S4 TB10MS | time base 10 ms | An internal timer regulates the change in status of this bit. It is asynchronous in relation to the PLC cycle. |
| %S5 TB100MS | time base 100 ms | Same as %S4 |
| %S6 TB1SEC | time base 1 s | Same as %S4 |
| %S7 TB1MIN | Time base 1 min | Same as %S4 |
| %S10 |  | Watchdog Overflow. ON if task exec. time > max. execution time. |
| %S11 WDG | Watchdog overflow error | Normally at 0, this bit is set to 1 by: - power restore with data save, - the user program, - the terminal, - action on change of cartridge. It is reset to 0 by the system at the end of the 1st complete cycle & before the outputs are updated. |
| %S12 PLCRUNNING | PLC in RUN | This bit is set to 1 by the system when the PLC is in RUN. It is set to 0 by the system as soon as the PLC is no longer in RUN (STOP, INIT) |
| %S13 1RSTSCANRUN | 1st cycle after switching to RUN | First scan bit. Normally set to 0, this is set to 1 by the system during the 1st cycle of the master task after the PLC is set to RUN. |
| %S15 STRNGERROR | Char. String fault | Normally set to 0, this bit is set to 1 when the dest. Zone for a char. String transfer is not of sufficient size (including the # of chars *& the end of string char.) to receive this char. string. The application stops in error state if the %S78 bit has been set to 1. This bit must be set to 0 by the application. |
| %S17 CARRY | Rotate or shift output | Normally at 0. During a rotate or shift operation, this bit take the state of the outgoing bit. |
| %S18 OVERFLOW | Overflow or arithmetic error | Normally set to 0; Set to 1 in the event of a capacity overflow if there is: - result > +32767 or < -32768, in single length - result > +65535, in UINT - result > +2147483647 or < -2147483648, in Double Length - result > +4294967296, in double length or UINT - real values outside limits - division by 0 - the root of a negative number, - forcing to a non-existent step on a drum - stacking up of an already full register, empty of an already empty register. It must be tested by the user program after each operation where there is a risk of overflow, & then reset to 0 by the user if there is indeed an overflow. When the %S18 bit switches to 1, the application stops in error state if the %S78 bit has been set to 1. |
| %S19 OVERRUN | Task period overrun (periodical scanning) | Normally set to 0, this bit is set to 1 by the system in the event of a time period overrun (i.e. task execution time is > the period defined by the user in the configuration or programmed into the %SW word associated with the task). The user must reset this bit to 0. Each task manages its own %S19 bit. |
| %S20 INDEXOVF | Index overflow | Normally set to 0m, this bit is set to 1 when the address of the indexed object becomes < 0 or exceeds. The number of objects declared in the configuration. In this case, it is as if the index were = 0. It must be tested by the user program after each operation. Where there is a risk of overflow & then reset to 0 if there is indeed an overflow. When the %S20 bit switches to 1, the application stops in error state if the %S78 bit has been set to 1. |
| %S21 |  | 1st cycle |
| %S30 MASTACT | Activation/deactivation of the master task | Normally set to 1. The master task is deactivated when the user sets the bit to 0. This bit is taken into consideration by the system at the end of each MAST task cycle. |
| %S31 FASTACT | Activation/deactivation of the FAST task | Normally set to 1 when the user creates the task. The task is deactivated when the user sets the bit to 0. |
| %S38 ACTIVEVT | Enabling/inhibition of events ( | Normally set to 1. Events are inhibited when the user sets the bit to 0. |
| %S39 EVTOVR | Saturation in event processing | This bit is set to 1 by the system to indicate that one or more events cannot be processed following saturation of the queues. The user must reset this bit to 0. |
| %S40 RACK0ERR | Rack 0 input/output fault | Normally set to 1. Set to 0 when fault occurs on rack’s IOs. %S10 is set to 0, IO processor LED is on, %Ir.m.c.Err is set to 0. Reset to 1 when fault disappears. Currently, M340 supports 4 racks of IO. |
| %S41 Rack1Err |  | Same as %S40 |
| %S42 Rack2Err |  | “ |
| %S43 Rack3Err |  | “ |
| %S44 Rack4Err |  | “ |
| %S45 Rack5Err |  | “ |
| %S46 Rack6Err |  | “ |
| %S47 Rack7Err |  | “ |
| %S50 RTCWRITE | Update time & data via words %SW50-%SW53 | Normally set to 0. Set to 1 or 0 by program or terminal. 0 = update of system words %SW53 by date & time supplied by PLC real time clock 1 = system words %SW50 - %SW53 no longer updated making it possible to modify them. Switch from 1 to 0 update the real time clock with values in %SW50 - %SW53. |
| %S51 RTCERR | Time loss in real time clock | System managed bit set to 1 indicates real time clock is missing or that %SW50 - %SW53 are meaningless. Clock must be reset to the correct time. |
| %S59 RTCTUNING | Incremental update of time & date via %SW59 | Normally set to 0. Can be set to 1 or 0 by program or terminal. 0 = system does not manage the system word %SW59. 1 = System manages edges on word %SW59 to adjust date & current time (by increment). |
| %S65 CARDIS | Card disable (M340) | Set to 1 by the user to disable access to the card. The system will detect a rising edge on this bit. Then all current access are finished (i.e., application save in progress), then the access LED will be OFF indicating that extraction is possible. The user has to reset the bit after extracting the card. |
| %S66 LEDBAIT APPLIBCK | Application backup | Set to 1 by user to start backup (transfer app. From RAM to card). System detects rising edge to start backup. NOTE: Test that bit %S66 has been set to 0 by system meaning that previous back up has finished. Never use %S66 if it is set to 1. Useful after replacement of int. value %S94 and save parameters. |
| %S76 DIAGBUFFCONF | Configured diagnostics buffer | Bit is set to 1 by the system when the diagnostics option has been configured. Then a diagnostics buffer for storage of errors found by diagnostics DFBs is reserved. This bit is READ ONLY. |

| %S77 DIAGBUFFFULL | Full diagnostics buffer | Bit is set to 1 by the system when the buffer that receives errors from the diagnostics function blocks is full. This bit is READ ONLY. |
| --- | --- | --- |
| %S78 HALTIFERROR | Stop in the event of error | Normally at 0, this bit can be set to 1 by the user, to program a PLC stop on application fault: %S15, %S18, %S20 |
| %S80 RSTMSGCNT | Reset message counters | Normally set to 0, this bit can be set to 1 by the user to reset the message counters %SW80 to %SW86. |
| %S94 SAVECURRVAL | Saving adjustment values Update initial values with current values. | Normally at 0, this bit can be set to 1 by the user to replace the initial values of the declared variables with a ‘Save’ option (i.e. DFB variables) with the current values. M340, on a %S94 rising edge, the internal RAM & the memory card content are different (%S96 = 0 & the CARDERR LELD is ON.) On cold start, the current values are replaced by the most recent Initial values only if a save to memory card function (Backup Save or %S66 rising edge) was done. The system resets the bit %S94 to 0 when the replacement has been made. Note: this must be used with card. Do not set this bit permanently to 1 & use the master task only. |
| %S92 EXCHGTIME | Measure mode of comm.. function | Normally set to 0. Can be set to 0 by user to set comm.. function to performance measurement mode. Comm. Functions timeout parameter then display the round trip exchange time in milliseconds. |
| %S96 BACKUPPROGOK | Backup program OK | M340: - Set to 0 by the system when the card is missing or not usable (bad format, unrecognized type) or card content Inconsistent with internal application RAM. Set to 1 when the card is correct & application is consistent with the CPU internal application RAM. |
| %S118 REMIOERR | General Remote I/O fault | Normally set to 1, this bit is set to 0 by the system when a fault occurs on a device connected to the RIO. Reset to 1 by the system when the fault disappears. |
| %S119 LOCIOERR | General in-rack I/O fault | Normally set to 1, this bit is set to 0 by the system when a fault occurs on an I/O module placed in one of the racks. This bit is reset to 1 by the system when the fault disappears. |
| %S123 ADJBX | Adjust Bux X | Used by system. Cannot be used by appl. |

| %SW0 MASTPERIOD | Master task scanning period | Used to modify the period of the master task via the user program or via the terminal |
| --- | --- | --- |
| %SW1 FASTPERIOD | Fast task scanning period | Used to modify the period of the fast task via the user program or via the terminal. Expressed in milliseconds (1..255). On a cold restart, it takes the value defined by the configuration. |
| %SW6 %SW7 | IP Address | IP address of CPU native Ethernet port. 0 = CPU does not have an Ethernet link. |
| %SW8 TSKINHIBIN | Acquisition of task input monitoring | Normally set to 0. Can be set to 1 or 0 by program or terminal. Inhibits input acquisition phase of each task: %SW8.0 = 1 inhibits acquisition of inputs %SW8.1 = inhibits acquisition of inputs. Related to FAST task %SW8.2-5 = 1 inhibits acquisition of inputs related to the AUX 0-3 tasks. |
| %SW9 TSKINHIBOUT | Monitoring of task output update | Normally set to 0. Can be set to 1 or 0 by program or terminal. Inhibits input acquisition phase of each task: %SW9.0 = 1 assigned to MAST task; outputs related to this task are no longer managed. %SW9.1 = 1 assigned to FAST task; outputs related to this task are no longer managed. %SW9.2-5 = 1 assigned to the AUX 0-3 tasks; outputs related to this task are no longer managed. |
| %SW10 TSKINIT | 1st cycle after cold start | 0 = task is performing its 1st cycle after a cold start. %SW10.0 MAST task; %SW10.1 FAST task; %SW10.2-5 AUX 0-3 tasks |
| %SW11 WDGVALUE | Watchdog duration | Read the duration of the watchdog. The duration is expressed in milliseconds (10…1500 ms). The word cannot be modified. |
| %SW12 UTWPORTADDR | Processor serial port address | MB slave address of the CPU serial port. Modification is not taken in to account. 0 = CPU does not have a serial port link. |
| %SW14 OSCOMMVERS | Commercial version of PLC processor | Current OS of PLC Example: 16#1335 Version: 01 Issue number: 35 |
| %SW15 OSCOMMPATCH | PLC processor patch version | LS byte of word Coding: 0 = no patch 1 = a 2 = b |
| %SW16 OSINTVERS | Firmware version # | Firmware version in hex of PLC processor firmware. Example: 16#0011 Version 2.1 VN 17 |
| %SW17 FLOATSTAT | Error stat on floating operation | Error in floating arithmetic sets %S18 to 1 and %SW17 error stat is updated. %SW17.0 = invalid op/result is not a number. %SW17.1 = denormalized operand/result is acceptable (flag not currently managed byM340) %SW17.2 = division by 0 / result is infinity. %SW17.3 = overflow/result is infinity. %SW17.4 – underflow / result is 0 %SW17.5-15 not used. |
| %SW18 & SW19 100MSCOUNTER (double word %SW18) | Absolute time counter | %SW18 = LS bytes %SW19 = MS bytes Incremented by system ever 1/10th of a second. Application can read/write these words to perform duration calculations. %SD18 incremented systematically, even in STOP mode. However, times when the PLC is switched off are not taken into account since the function is not linked to the real time scheduler, but only to the real time clock. |

| %SW20 & %SW21 MSCOUNTER (double word %SW20) | Absolute time counter | %SD20 is incremented every 1/1000th of a second by the system even when the PLC is in STOP. %SD20 is not incremented if the PLC is powered down. %SD20 can be read by the program or by the terminal. %SD20 is reset on cold start. %SD20 is not reset on warm start. |
| --- | --- | --- |
| %SW23 | Rotary switch value | LS byte contains Ethernet processor rotary switch. Can be read by the program or the terminal. |
| %SW26 | # of requests processed | Allows verification on the server side the # of requests process by the PLC per second. |
| %SW27 %SW28 %SW29 | System overhead time | %SW27 = last system overhead time %SW28 = maximum system overhead time. %SW29 = minimum system overhead time. Depends on the configuration (# of IO.) & the current cycle requests (comm. diagnostics.) System overhead time = MAST cycle time – User code execution time. Can be read/write by user program or terminal. |
| %SW30 MASTCURRTIME | Master task execution time | Indicates the execution time of the last master task cycle (in ms.) NOTE: In general %SW30 works, but keep in mind that a PC is much faster as a PLC. For a short application a scan time less than 1ms is possible, in such a case %SW30 remains at 0. %SW30 will not be updated when an exception (division by 0, overflow, etc.) occurs during execution of the user logic or after any user debug activity. If an application throws an exception in each cycle, %SW30 will remain at 0 and %SW31, %SW32 will remain at 32768 and 32767 from the beginning. (Level3: 10/2011. Cycle time includes internal processing on input, program processing and internal processing on output. Measures complete scan time including I/O.) |
| %SW31 MASTMAXTIME | Max. master task execution time | Longest master task execution time since lsat cold start (in ms.). |
| %SW32 MASTMINTIME | Min. master task execution time | Shortest master task execution time since the last code start (in ms.) |
| %SW33 FASTCURRTIME | FAST task execution time | Indicates FAST task execution time of the last FAST task cycle (in ms.) |
| %SW34 FASTMAXTIME | Max .FAST task execution time | Indicates longest FAST task execution time the last code start (in ms.) |
| %SW35 FASTMINTIME | Min. FAST task execution time | Indicates shortest FAST task execution time the last code start (in ms.) |
| %SW48 IOEVTNB | # of events | IO events processed since the last cold start. Can be written by program or terminal. |
| %SW49 DAYOFWEEK %SW50 SEC %SW52 HOURMIN %SW52 MONTHDAY %SW53 YEAR | Real-time clock function | System words containing date & current time (in BCD): %SW49: day of the week: 1 = Monday, 2 = Tuesday, 3 = Wednesday, 4 = Thursday, 5 = Friday, 6 = Saturday, 7 = Sunday %SW50: Seconds (16#SS00), %SW51: Hours & Minutes (16##HHMM), %SW52: Month & Day (16##MMDD), %SW53: Year (16##YYYY). These words are managed by the system when the bit %S50 is set to 0. These words can be written by the user programmer by the terminal when the bit %S50 is set to 1. |

| %SW54 STOPSEC %SW55 STOPHM %SW56 STPMD %SW57 STOPYEAR %SW58 STOPDAY | Real-time clock function on last stop | System words contain data & time of the last power failure or PLC stop (BCD) %SW54: Seconds (00SS) %SW55: Hours & Minutes (HHMM) %SW56: Monty & day (MMDD), %SW57: Year (YYYY), %SW58: most significant byte contains the day of the week (1 = Monday); Least significant byte contains the code or the last stop: - 1 = change from RUN to STOP by the terminal or the dedicated input, - 2 = stop by watchdog (PLC task or SFC overrun), - 4 = power outage or memory card lock operation, - 6 = stop on software fault. Details on the type of sfw fault are stored in %SW125 |
| --- | --- | --- |
| %Sw59 ADJDATETIME | Adjust current date | Two 8-bit series to adjust the current date. Performed on rising edge of bit. Enabled by bit %S59=1. Bits 0 – 7 increment the value; bits 8 – 15 decrement value. Bit 0 , 8 - day of week Bit 1 , 9 - seconds Bit 2, 10 – minutes Bit 3, 11 - hours Bit 4, 12 – days Bit 5, 13 – months Bit 6, 14 – years Bit 7, 15 – centuries |
| %SW70 WEEKOFYEAR | Real-time clock function | Contains the number of the week in the year: 1 to 52 |
| %SW75 TIMEREVTNB | Timer-type event counter | Contains the number timer type events in the queue. |
| %SW76 DLASTREG | Diagnostics fcn: recording | Results o the last registration: = 0 if the recording was successful, = 1 if the diagnostics buffer has not been configured, = 21 if the error identifier is invalid, = 22 if the error has not been recorded. |
| %SW77 DLASTDEREG | Diagnostics fcn: non-recording | Result of last deregistration = 0 non-recording was successful = 1 diagnostics buffer has not been configured = 21 error identifier is invalid = 22 error has not been recorded |
| %SW78 DNBERRBUF | Diagnostics function: # of errors | Number of errors currently in the diagnostics buffer. |
| %SW80 %SW81 | Message management | Updated by system. Can also be preset by using %S80. %SW80 = # of messages sent by system to terminal port %SW81 = # of ,messages received by the system to the terminal port (MB serial port) |
| %SW84 %SW85 | Message management | %SW84 = # of messages sent to the USB port %SW85 = # of messages received by the USB port |
| %SW86 | Message management | Updated by system. Can be reset using %S80. % of messages refused by the system, not treated because of lack of resources , for example. If the message is refused by MB Server, it corresponds to MB exception messages, sent by the CPU to the remove MB client. |
| %SW87 MSTSERVCNT | Communication flow management | # of requests processed by synchronous server per master (MAST) task cycle. The requests processed may come from all communication ports (having access to the server Modbus/UNI-TE, each of them having its own limitation). This means also that requests from other clients, then communication EFs like IO Scanner, connected HMI and so on should be counted. |
| %SW88 %SW89 | HTTP & FTP requests rec’d. by the processor’s Web server & FTP server | %SW88 = # of HTTP requests received by the processor’s Web server per second %SW89 = # of FTP requests received by the FTP server per second. |

| %SW90 MAXREQNB | Max. # of requests processed per master task cycle | Used to set a maximum number of requests which can be processed by the PLC per master task cycle. (NOT Requests sent by PLC as client) # of requests must be between min & max (defined as N+4) depending on model.. BMXP34 10../20../:N=8 (minimum 2, maximum 8+4 = 12) Requests may come from various modules or embedded comm.. ports. Comm. Exchange capacity of each port is limited. Max. request value set in %SW90 might not be reached. Initialized by the system. (See Unity OnlineHelp for detail.) |
| --- | --- | --- |
| %SW91 %SW92 | Function blocks message rates | %SW91 # of blocks messages sent per second %SW92 # of function block messages received per second. Can be read by program or terminal. Does not include other outgoing requests coming from an IO scanner, for example. |
| %SW93 | Memory card file system format command and status | Can be read and written by the user program or the terminal. Used by the customer to format the memory card. Formatting is possible only in Stop mode: %SW93.0 = 1 a rising edge starts the Format operation %SW93.1 Provides file system status after a formatting request: %SW93.1 = 0 invalid files system (bad formatting, formatting in progress), %SW93.1 = 1 valid files system. |
| %SW94 %SW95 | Application modification signature | Contain a 32-bit values that changes at every appl. Modification except: - Updating upload info - - replacing the in it value with the current value - - saving the parameter command. |
| %SW96 CMDDIAGSAVEREST | Command & diagnostic of save and restore | Used to copy or delete the current value of %MW to or from internal flash memory and to give the action’s status. It can be read by the user program or by the terminal: %SW96.0 Request to copy current value of %MW to internal Flash memory. Set to 0 by the user to request a save, and set to 0 by the system when a save is in progress. %SW96.1 Set to 1 by the system, when a save is finished, and set to 0 by the system when a save is in progress. %SW96.2 = 1 indicates an error on a save or restore operation (see %SW96.8 to 15 for error code definitions). %SW96.3 = 1 indicates that a restore operation is in progress. %SW96.4 may be set to 1 by the user to delete %MW area in internal Flash memory. %SW96.7 = 1 indicates that internal memory has valid %MW backup. %SW96.8 to 15 are error codes when %SW96.2 is set to 1. 96.9 = 1 indicates that the saved %MW number is less than the configured number. 96.8 AND 96.9 = 1 indicates that the saved %MW number is greater than the configured number 96.8 AND 96.9 AND 96.10 = 1 indicates a write error in internal Flash memory. |
| %SW97 CARDSTS | Card status | Can be read by the user program or by the terminal. Indicates the status of the card: 0000 = no error 0001 = appl. Backup or file write sent to a write-protected card. 0002 = card not recognized, or appl. Backup damaged. 0003 = backup of the appl. Requested, but no card available. 0004 = card access error, for example, after a card has been removed improperly. 0005 = no file system present in the card, or file system not compatible. Use #SW93.0 to format the card. |

| %SW108 FORCEDIOIM | Number of forced I/O module bits | Increments each time a discrete bit %I, %Q, %M, is forced. Decrements each time a discrete bit is unforced. |
| --- | --- | --- |
| %SW109 FORCEDANA | Number of forced analog channels | Increments each time an analog channel is forced. Decrements each time an analog channel is unforced. |
| %SW123 ADJBUSX | System allowance to BUS X | Used by the system. Cannot be used by the user’s application. |
| %SW124 CPUERR | Type of processor or system error | 16#30 = system code fault 16#53 = time out fault during IO excjanges 16#60 – 64 = stack overrun 16#65 = FAST task period of execution is too slow 16#81 = detection of backplane error (If this error is detected, all racks have to be reinitialized.) 16#90= system switch fault Unforeseen IT |
| %SW125 BLKERRTYPE | Last fault detected | Code of the last fault detected. The following error codes cause the PLC to stop if %S78 is set to 1. %S15, %S18 and %S20 are always activated independently of S78: 16#2258: execution of HALT instruction 16#DE87: calculation error on floating point numbers (%S18 these errors are listed in word %SW17 16#DEB0: watchdog overflow (%S11) 16#DEF0: division by 0 (%S18) 16#DEF1: character string transfer error (%S15) 16#DEF2: arithmetic error (%S18) 16#DEF3: index overflow (%S20) NOE: Codes 16#8xxx and 16#7xxx do not stop the application & indicate an error on function blocks. |
| %SW126 ERRADDR0 %SW127ERRADDR1 | Block fault instruction address | Address of the instruction that generated the application blocking fault. For 32 bit processors: %SW126 contains the least significant word for this address %SW127 contains the most significant word for this address. For a STOP due to watchdog overflow: %SW126 contains # of MAST task with overflow %SW127 contains value of the MAST task with overflow. |
| %SW160-%SW167 | Premium/M340 IO health racks 0-7 errors | Associated with racks 0 -7. Bits 0 – 15 of each word associated with the modules located in positions 0 – 15. 0 indicates a fault. 1 indicates IO health. Example: %SW163.5 = 0 module in position 5 on rack 3 is in fault. |