How to connect a pressure transducer to Altivar Process for PID control?

24VDC, 4-20mA output

Terminal 1 of transducer to be connected 24V

Terminal 3 to be connected to AI1 or AI2 or AI3 for feedback

(please make sure to change the Analogue input type to current)

24VDC, 0-10VDC output

Terminal 1 of transducer to be connected 24V

Terminal 3 to be connected to COM

Terminal 4 to be connected to AI1 or AI2 or AI3 for feedback

(please make sure to change the Analogue input type to voltage)