[bookmark: _GoBack]Is there a way to use a physical switch to on/off ERMS, like in the case of Masterpact NT/NW?
Yes you can use ESM module:
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Please note that if you install ESM module you can not install M2C module;
The reference of this module is LV836300SP. 

This module will allow you to use a push button to engage and disengage ERMS.
See schematic below:
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The installation is described in the doc attached.
	LV836300SP IS.pdf



NOTE: to be operational, ESM-ERMS must be declared with Ecoreach.
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ESM: ERMS switch module

‘The ESM optional hardware module is used with an external lockable selector switch
to engage/disengage the ERMS function. Itis equipped with one input dedicated to the.
ERMS selector swilch and one output to activate an external pilot light when the ERMS
is engaged. The ESM optional hardware module requires the MicroLogic X control unit
to be supplied by an external 24 V dc power supply. When the ESM optional hardware
module is installed, the M2C optional module 2 contacts cannot be installed

0 MTZ1, MTZ2, MTZ3 Output __Input
Rated voltage VAC 250V/3A 24110V
vDC 30V/I3A 24V
Max breaking voltage VAC 27VI3A -
Maxload breaking capacity VAC 277VI3A -
vDC 0VIIA -
Minimurm load voc 5V/10mA -
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