## Sheet1
Device type: VAMP 50 |  | Feeder mode
Program version: V10.107
Note: The Addresses of the items are customizable.
ModBusMstr |  | Also, the data items must be enabled in the protocol configuration before they can be read/written to.
Address | Item
402001 | Alive indicator
402002 | DI
402003 | DIs after DI16 for ModBus
402034 | Phase current IL
402004 | Phase current IL1
402005 | Phase current IL2
402006 | Phase current IL3
402007 | Io1 residual current
402016 | Frequency
402037 | Obj1 state
402038 | Obj2 state
402039 | Obj3 state
402040 | Obj4 state
402041 | Obj5 state
402042 | Obj6 state
402044 | Obj7 state
402045 | Obj8 state
402043 | Remote/Local State
402101 | Release latches
402102 | NewModBusEventReq
402103 | NewModBusEventSent
402104 | Events
402105 | Events
402106 | Events
402107 | Events
402108 | Events
402109 | Open select Obj1
402110 | Close select Obj1
402111 | Execute operation Obj1
402112 | Max ctrl pulse length
402113 | Open select Obj2
402114 | Close select Obj2
402115 | Execute operation Obj2
402116 | Max ctrl pulse length
402119 | Open select Obj3
402120 | Close select Obj3
402121 | Execute operation Obj3
402122 | Max ctrl pulse length
402123 | Open select Obj4
402124 | Close select Obj4
402125 | Execute operation Obj4
402126 | Max ctrl pulse length
402130 | Open select Obj5
402131 | Close select Obj5
402132 | Execute operation Obj5
402133 | Max ctrl pulse length
402134 | Open select Obj6
402135 | Close select Obj6
402136 | Execute operation Obj6
402137 | Max ctrl pulse length
402117 | Cancel selected operation
402118 | Synchronize minutes