## Sheet1
Device type: VAMP 50
Program version: V10.107 |  | Motor mode
ProfibusDP
Continuous Mode:
ProfiBus Tx Buffer |  | Note: Continuous mode buffers are customizable
Offset | Name | Length
0 | Phase current IL1 | 2
2 | Phase current IL2 | 2
4 | Phase current IL3 | 2
6 | Frequency | 2
8 | DI | 3
11 | Output relays | 2
13 | Io1 residual current | 2
17 | Alive indicator | 1
18 | Phase current IL | 2
ProfiBus Rx Buffer
Offset | Name | Length
0 | 1st byte reserved | 1
1 | Open select Obj1 | 1
2 | Close select Obj1 | 1
3 | Execute operation Obj1 | 1
4 | Open select Obj2 | 1
5 | Close select Obj2 | 1
6 | Execute operation Obj2 | 1
7 | Open select Obj3 | 1
8 | Close select Obj3 | 1
9 | Execute operation Obj3 | 1
10 | Open select Obj4 | 1
11 | Close select Obj4 | 1
12 | Execute operation Obj4 | 1
13 | Open select Obj5 | 1
14 | Close select Obj5 | 1
15 | Execute operation Obj5 | 1
16 | Open select Obj6 | 1
17 | Close select Obj6 | 1
18 | Execute operation Obj6 | 1
19 | DirectO1O | 1
20 | DirectO1C | 1
21 | DirectO2O | 1
22 | DirectO2C | 1
23 | DirectO3O | 1
24 | DirectO3C | 1
25 | DirectO4O | 1
26 | DirectO4C | 1
27 | DirectO5O | 1
28 | DirectO5C | 1
29 | DirectO6O | 1
30 | DirectO6C | 1
31 | Virtual input 1 | 1
32 | Virtual input 2 | 1
33 | Virtual input 3 | 1
34 | Virtual input 4 | 1
ProfiBus Request Mode
Data number | Name | Length | Read | Write | Cont.mode
0 | Phase current IL1 | 2 | 1 | 0 | 1
1 | Phase current IL2 | 2 | 1 | 0 | 1
2 | Phase current IL3 | 2 | 1 | 0 | 1
3 | Frequency | 2 | 1 | 0 | 1
4 | DI | 3 | 1 | 0 | 1
5 | Output relays | 2 | 1 | 0 | 1
6 | Io1 residual current | 2 | 1 | 0 | 1
9 | Alive indicator | 1 | 1 | 0 | 1
13 | Events | 4 | 1 | 0 | 0
26 | Phase current IL | 2 | 1 | 0 | 1
29 | Obj1 state | 1 | 1 | 0 | 1
30 | Obj2 state | 1 | 1 | 0 | 1
31 | Obj3 state | 1 | 1 | 0 | 1
32 | Obj4 state | 1 | 1 | 0 | 1
33 | Obj5 state | 1 | 1 | 0 | 1
34 | Obj6 state | 1 | 1 | 0 | 1
35 | Remote/Local State | 1 | 1 | 1 | 1
36 | Open select Obj1 | 1 | 1 | 1 | 1
37 | Close select Obj1 | 1 | 1 | 1 | 1
38 | Execute operation Obj1 | 1 | 0 | 1 | 1
39 | Cancel selected operation | 1 | 0 | 1 | 1
40 | Max ctrl pulse length of Obj1 | 1 | 1 | 1 | 0
41 | Open select Obj2 | 1 | 1 | 1 | 1
42 | Close select Obj2 | 1 | 1 | 1 | 1
43 | Execute operation Obj2 | 1 | 0 | 1 | 1
44 | Max ctrl pulse length of Obj2 | 1 | 1 | 1 | 0
45 | OM_MB_ResetLatches | 1 | 1 | 1 | 0
46 | Synchronize minutes | 1 | 1 | 1 | 0
47 | Set time & date | 4 | 0 | 1 | 0
48 | Open select Obj3 | 1 | 1 | 1 | 1
49 | Close select Obj3 | 1 | 1 | 1 | 1
50 | Execute operation Obj3 | 1 | 0 | 1 | 1
51 | Max ctrl pulse length of Obj3 | 1 | 1 | 1 | 0
52 | Open select Obj4 | 1 | 1 | 1 | 1
53 | Close select Obj4 | 1 | 1 | 1 | 1
54 | Execute operation Obj4 | 1 | 0 | 1 | 1
55 | Max ctrl pulse length of Obj4 | 1 | 1 | 1 | 0
56 | Pos. sequence I1 | 2 | 1 | 0 | 1
57 | Neg. sequence I2 | 2 | 1 | 0 | 1
58 | Current -seq./+seq. | 2 | 1 | 0 | 1
59 | Current phase seq. | 1 | 1 | 0 | 1
60 | Phase current THD | 2 | 1 | 0 | 1
61 | IL1 THD | 2 | 1 | 0 | 1
62 | IL2 THD | 2 | 1 | 0 | 1
63 | IL3 THD | 2 | 1 | 0 | 1
64 | HARMONICS of IL1 | 1 | 1 | 0 | 0
65 | HARMONICS of IL2 | 1 | 1 | 0 | 0
66 | HARMONICS of IL3 | 1 | 1 | 0 | 0
67 | Min. of IL1 IL2 IL3 | 2 | 1 | 0 | 1
68 | Max. of IL1 IL2 IL3 | 2 | 1 | 0 | 1
69 | Phase current ILRMS | 2 | 1 | 0 | 1
70 | Phase current IL1RMS | 2 | 1 | 0 | 1
71 | Phase current IL2RMS | 2 | 1 | 0 | 1
72 | Phase current IL3RMS | 2 | 1 | 0 | 1
73 | Temperature rise | 2 | 1 | 1 | 1
74 | Ambient temperature | 1 | 1 | 1 | 0
75 | IL1da demand | 2 | 1 | 0 | 1
76 | IL2da demand | 2 | 1 | 0 | 1
77 | IL3da demand | 2 | 1 | 0 | 1
78 | IoCalc demand | 2 | 1 | 0 | 1
79 | Io1 demand | 2 | 1 | 0 | 1
130 | Calculated Io | 2 | 1 | 0 | 1
131 | Fault current of I> | 2 | 1 | 0 | 1
132 | Fault current of I>> | 2 | 1 | 0 | 1
133 | Fault current of I>>> | 2 | 1 | 0 | 1
135 | DI1 counter | 2 | 1 | 1 | 1
136 | DI2 counter | 2 | 1 | 1 | 1
168 | Stage start state | 1 | 1 | 0 | 0
169 | Stage trip state | 1 | 1 | 0 | 0
177 | N> alarm | 1 | 1 | 0 | 1
178 | Motor start disabled | 1 | 1 | 0 | 1
179 | Motor starting | 1 | 1 | 0 | 1
180 | Motor running | 1 | 1 | 0 | 1
187 | Logic output states 1...10 | 1 | 1 | 0 | 1
188 | CBWAlarm 1 | 1 | 1 | 0 | 1
189 | CBWAlarm 2 | 1 | 1 | 0 | 1
190 | Alarm L1..L3 | 1 | 1 | 0 | 1
191 | Fault L1..L3 | 1 | 1 | 0 | 1
196 | SetGrp common change | 1 | 1 | 1 | 0
199 | Open select Obj5 | 1 | 1 | 1 | 1
200 | Close select Obj5 | 1 | 1 | 1 | 1
201 | Execute operation Obj5 | 1 | 0 | 1 | 1
202 | Max ctrl pulse length of Obj5 | 1 | 1 | 1 | 0
203 | Open select Obj6 | 1 | 1 | 1 | 1
204 | Close select Obj6 | 1 | 1 | 1 | 1
205 | Execute operation Obj6 | 1 | 0 | 1 | 1
206 | Max ctrl pulse length of Obj6 | 1 | 1 | 1 | 0
225 | DirectO1O | 1 | 0 | 1 | 1
226 | DirectO1C | 1 | 0 | 1 | 1
227 | DirectO2O | 1 | 0 | 1 | 1
228 | DirectO2C | 1 | 0 | 1 | 1
229 | DirectO3O | 1 | 0 | 1 | 1
230 | DirectO3C | 1 | 0 | 1 | 1
231 | DirectO4O | 1 | 0 | 1 | 1
232 | DirectO4C | 1 | 0 | 1 | 1
233 | DirectO5O | 1 | 0 | 1 | 1
234 | DirectO5C | 1 | 0 | 1 | 1
235 | DirectO6O | 1 | 0 | 1 | 1
236 | DirectO6C | 1 | 0 | 1 | 1
241 | Virtual input 1 | 1 | 1 | 1 | 1
242 | Virtual input 2 | 1 | 1 | 1 | 1
243 | Virtual input 3 | 1 | 1 | 1 | 1
244 | Virtual input 4 | 1 | 1 | 1 | 1
245 | Obj7 state | 1 | 1 | 0 | 1
246 | Obj8 state | 1 | 1 | 0 | 1
260 | Logic output states 9...16 | 1 | 1 | 0 | 1
261 | Logic output states 17...20 | 1 | 1 | 0 | 1
264 | Virtual outputs | 1 | 1 | 0 | 1
288 | Diagnostic register 1 | 2 | 1 | 0 | 1
289 | Diagnostic register 2 | 2 | 1 | 0 | 1
290 | Diagnostic register 3 | 2 | 1 | 0 | 1
291 | Diagnostic register 4 | 2 | 1 | 0 | 1
295 | Reset diagnostics | 1 | 1 | 1 | 1
296 | Clear min & max | 1 | 1 | 1 | 1
297 | Minimum frequency | 2 | 1 | 1 | 1
302 | Minimum of Io | 2 | 1 | 1 | 1
303 | Minimum of Io2 | 2 | 1 | 1 | 1
311 | Minimum of IL1 | 2 | 1 | 1 | 1
312 | Minimum of IL2 | 2 | 1 | 1 | 1
313 | Minimum of IL3 | 2 | 1 | 1 | 1
314 | RMS minimum of IL1 | 2 | 1 | 1 | 1
315 | RMS minimum of IL2 | 2 | 1 | 1 | 1
316 | RMS minimum of IL3 | 2 | 1 | 1 | 1
317 | Minimum of IL1 | 2 | 1 | 1 | 1
318 | Minimum of IL2 | 2 | 1 | 1 | 1
319 | Minimum of IL3 | 2 | 1 | 1 | 1
320 | RMS minimum of IL1 | 2 | 1 | 1 | 1
321 | RMS minimum of IL2 | 2 | 1 | 1 | 1
322 | RMS minimum of IL3 | 2 | 1 | 1 | 1
338 | Maximum frequency | 2 | 1 | 1 | 1
343 | Maximum of Io | 2 | 1 | 1 | 1
344 | Maximum of Io2 | 2 | 1 | 1 | 1
352 | Maximum of IL1 | 2 | 1 | 1 | 1
353 | Maximum of IL2 | 2 | 1 | 1 | 1
354 | Maximum of IL3 | 2 | 1 | 1 | 1
355 | RMS maximum of IL1 | 2 | 1 | 1 | 1
356 | RMS maximum of IL2 | 2 | 1 | 1 | 1
357 | RMS maximum of IL3 | 2 | 1 | 1 | 1
358 | Maximum of IL1 | 2 | 1 | 1 | 1
359 | Maximum of IL2 | 2 | 1 | 1 | 1
360 | Maximum of IL3 | 2 | 1 | 1 | 1
361 | RMS maximum of IL1 | 2 | 1 | 1 | 1
362 | RMS maximum of IL2 | 2 | 1 | 1 | 1
363 | RMS maximum of IL3 | 2 | 1 | 1 | 1
388 | 1st byte reserved | 1 | 0 | 1 | 1
400 | Grp. 2 remote scaling | 1 | 1 | 1 | 1