## Slide 1
PLS012 Rev26.PPT 5-30-2014
Page 1 of 2
AC
DC
AC
DC
Char. | Option
9* | none
2 | shutters
3** | Shutters with padlocking provision
5 | Shutters with padlock provision and shutter position indicator
  *Standard offer for UL and ANSI cradle
  ** Standard offer for IEC NT & NW cradle

## Slide 2
Page 2 of 2
18
11
19
25
PLS012 Rev26.PPT 5-30-2014
Position | Description | Wiring Code | Character
11 | Communication | COM 1) | A
12 | ZSI/ MDGF/ Neutral Sensor/ 24 Vdc supply | UC1+UC2+UC3 1) | B
13 | Programmable contact module (2PCM or 6PCM) | M2C/M6C 2) | C
14 | 2nd Alarm trip switch or Electrical Reset | SDE2/RES 4) 6) | D
15 | Undervoltage or 2nd shunt trip | MN/MX2 | E
16 | Shunt trip + Shunt close + Spring charging motor | MX1+XF+MCH 5) | F
17 | Ready to close contact (PF) for B1/B2, or early break-make contacts (CAO-CAF) for C4D | PF/ CAO-CAF | G
18 | Additional 4 form C (Wago) or 2a+2b (ring tongue) auxiliary contacts | OF 11-14 3) 4) 7) | H
 | Additional 8 form C (Wago) aux. contacts | OF 21-24 3) 4) 7) | J
 | 4 form C “Connected and Closed” switches | EF 11-14 3) 4) 7) | K
 | 8 form C “Connected and Closed” switches | EF 21-24 3) 4) 7) | L
 | 4 low level form C “Connected and Closed” switches | EF 11-14 3) 4) 7) | M
 | 8 low level form C “Connected and Closed” switches | EF 21-24 3) 4) 7) | N
 | 4 additional form C auxiliary switches + 4 form C “connected and closed” switches | OF 11-14 and EF 11-14 3) 4) 7) | P
 | 4 additional form C auxiliary switches + 4 low level form C “connected and closed” switches | OF 11-14 and EF 11-14 3) 4) 7) | R
COM, UC1 and UC2 will be supplied with 6-wire push-in terminals as standard even if Position 11 and 12 are X, and also when Ring terminals are specified. This is done so that the jumpers can be installed for ZSI and NCT to prevent issues with coms or restraint signals if trip unit is upgraded, etc.
Not compatible with External voltage sensing on NT cradle
Not available for NT cradle
Not available for C4D cradle
XF and MCH are not available for C4D cradle
An SDE switch comes standard on NT, NW and C4D.
NT comes standard with 4 form C (OF1-4) aux. contacts and none can be added. NW comes standard with 4 form C (OF 1-4) aux. Contacts and more can be added as above. C4D comes standard with wirings for 5 form C contacts (OF 1-3 aux. contacts, SD alarm contact and SDE overcurrent trip switch as shown in note 6).