## PM3250
PM3250 Translator Details
Data Recorder | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | ModbusAddr | Format | RequestType | IONHandle | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | 400090 | UINT16 | R | 4864
|  | Factory Information | Factory 1 | FAC1 Compliance |  |  |  |  | 4865
|  | Factory Information | Factory 1 | FAC1 Options |  |  |  |  | 4866
|  | Factory Information | Factory 1 | FAC1 Revision | FAC1 Revision | 401637 | UINT16 | R | 4867
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | 400130 | UINT32 | R | 4868
|  | Factory Information | Factory 1 | FAC1 ION Version |  |  |  |  | 30510
|  | Factory Information | Factory 1 | FAC1 Template |  |  |  |  | 4989
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | 400030 | ASCII | R | 22340 |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 Manuf Date Time | FAC1 Manuf Date Time | 400132 | DateTime3_IEC870_LOCAL | R | 30129
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | 401845 | DateTime3_IEC870_LOCAL | R | 65546
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | 401845 | DateTime3_IEC870_LOCAL | R | 23420
|  | Resets and Triggers | Resets | Energy Reset | Energy Reset | 405250 | U16-21-ARRAY | CW | 156237828
|  | Resets and Triggers | Resets | Min Max Reset | Min Max Reset | 405250 | U16-21-ARRAY | CW | 156237826
|  | Resets and Triggers | Resets | Peak Demand Reset | Peak Demand Reset | 405250 | U16-21-ARRAY | CW | 156237825
|  | Resets and Triggers | Time Of Use Rate Control | Time Of Use Rate Control | Time Of Use Rate Control | 404191 | UINT16 | RW | 156238081
|  | Alarms - Over Under | Alarms - Global Setup | Over Under Global Alarm Dropout Setpoint | Over Under Global Alarm Dropout Setpoint | 414009 | F32-4321 | RW | 160433665
|  | Alarms - Over Under | Alarms - Global Setup | Over Under Global Alarm Pickup Delay | Over Under Global Alarm Pickup Delay | 414007 | UINT32 | RW | 160433666
|  | Alarms - Over Under | Over Active Power | Over Active Power Alarm | Over Active Power Alarm | 411021 | MaskedBool | R | 160432129 | 0x0100 | 256
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Priority | Over Active Power-Alarm Priority | 414160 | UINT32 | R | 160432131 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Delay | Over Active Power-Dropout Delay | 414171 | UINT32 | R | 160432135
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Setpoint | Over Active Power-Dropout Setpoint | 414169 | F32-4321 | R | 160432134
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Delay | Over Active Power-Pickup Delay | 414167 | UINT32 | R | 160432133
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Enabled | Over Active Power-Alarm Enabled | 414160 | UINT32 | RW | 160432130 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Setpoint | Over Active Power-Pickup Setpoint | 414165 | F32-4321 | RW | 160432132
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power Alarm | Over Apparent Power Alarm | 411021 | MaskedBool | R | 160433153 | 0x0400 | 1024
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Priority | Over Apparent Power-Alarm Priority | 414200 | UINT32 | R | 160433155 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Delay | Over Apparent Power-Dropout Delay | 414211 | UINT32 | R | 160433159
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Setpoint | Over Apparent Power-Dropout Setpoint | 414209 | F32-4321 | R | 160433158
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Delay | Over Apparent Power-Pickup Delay | 414207 | UINT32 | R | 160433157
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Enabled | Over Apparent Power-Alarm Enabled | 414200 | UINT32 | RW | 160433154 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Setpoint | Over Apparent Power-Pickup Setpoint | 414205 | F32-4321 | RW | 160433156
|  | Alarms - Over Under | Over Current Phase | Over Current Phase Alarm | Over Current Phase Alarm | 411021 | MaskedBool | R | 160432385 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Priority | Over Current Phase-Alarm Priority | 414000 | UINT32 | R | 160432387 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Delay | Over Current Phase-Dropout Delay | 414011 | UINT32 | R | 160432391
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Setpoint | Over Current Phase-Dropout Setpoint | 414009 | F32-4321 | R | 160432390
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Delay | Over Current Phase-Pickup Delay | 414007 | UINT32 | R | 160432389
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Enabled | Over Current Phase-Alarm Enabled | 414000 | UINT32 | RW | 160432386 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Setpoint | Over Current Phase-Pickup Setpoint | 414005 | F32-4321 | RW | 160432388
|  | Alarms - Over Under | Under Active Power | Under Active Power Alarm | Under Active Power Alarm | 411022 | MaskedBool | R | 160433409 | 0x2000 | 8192
|  | Alarms - Over Under | Under Active Power | Under Active Power-Alarm Priority | Under Active Power-Alarm Priority | 414820 | UINT32 | R | 160433411 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Active Power | Under Active Power-Dropout Delay | Under Active Power-Dropout Delay | 414831 | UINT32 | R | 160433415
|  | Alarms - Over Under | Under Active Power | Under Active Power-Dropout Setpoint | Under Active Power-Dropout Setpoint | 414829 | F32-4321 | R | 160433414
|  | Alarms - Over Under | Under Active Power | Under Active Power-Pickup Delay | Under Active Power-Pickup Delay | 414827 | UINT32 | R | 160433413
|  | Alarms - Over Under | Under Active Power | Under Active Power-Alarm Enabled | Under Active Power-Alarm Enabled | 414820 | UINT32 | RW | 160433410 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Active Power | Under Active Power-Pickup Setpoint | Under Active Power-Pickup Setpoint | 414825 | F32-4321 | RW | 160433412
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L Alarm | Under Voltage L-L Alarm | 411021 | MaskedBool | R | 160432641 | 0x0020 | 32
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Priority | Under Voltage L-L-Alarm Priority | 414100 | UINT32 | R | 160432643 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Delay | Under Voltage L-L-Dropout Delay | 414111 | UINT32 | R | 160432647
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Setpoint | Under Voltage L-L-Dropout Setpoint | 414109 | F32-4321 | R | 160432646
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Delay | Under Voltage L-L-Pickup Delay | 414107 | UINT32 | R | 160432645
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Enabled | Under Voltage L-L-Alarm Enabled | 414100 | UINT32 | RW | 160432642 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Setpoint | Under Voltage L-L-Pickup Setpoint | 414105 | F32-4321 | RW | 160432644
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N Alarm | Under Voltage L-N Alarm | 411021 | MaskedBool | R | 160432897 | 0x0080 | 128
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Priority | Under Voltage L-N-Alarm Priority | 414140 | UINT32 | R | 160432899 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Delay | Under Voltage L-N-Dropout Delay | 414151 | UINT32 | R | 160432903
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Setpoint | Under Voltage L-N-Dropout Setpoint | 414149 | F32-4321 | R | 160432902
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Delay | Under Voltage L-N-Pickup Delay | 414147 | UINT32 | R | 160432901
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Enabled | Under Voltage L-N-Alarm Enabled | 414140 | UINT32 | RW | 160432898 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Setpoint | Under Voltage L-N-Pickup Setpoint | 414145 | F32-4321 | RW | 160432900
DR1 | 900 | Currents | Current | Current Phase A | Current Phase A | 403000 | F32-4321 | R | 164626433
|  | Currents | Current | Current Phase Average | Current Phase Average | 403010 | F32-4321 | R | 164626439
DR1 | 900 | Currents | Current | Current Phase B | Current Phase B | 403002 | F32-4321 | R | 164626434
DR1 | 900 | Currents | Current | Current Phase C | Current Phase C | 403004 | F32-4321 | R | 164626435
|  | Currents | Current | Neutral Current | Neutral Current | 403006 | F32-4321 | R | 164626436
|  | Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | 403252 | DateTime3_IEC870_LOCAL | R | 169870337
DR1 | 900 | Energies | Energy | Active Energy Delivered | Active Energy Delivered | 403204 | S64-87-21 | R | 169869313 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase A | Active Energy Delivered Phase A | 403518 | S64-87-21 | R | 169869322 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase B | Active Energy Delivered Phase B | 403522 | S64-87-21 | R | 169869323 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase C | Active Energy Delivered Phase C | 403526 | S64-87-21 | R | 169869324 |  | 1000
DR1 | 900 | Energies | Energy | Active Energy Received | Active Energy Received | 403208 | S64-87-21 | R | 169869314 |  | 1000
DR1 | 900 | Energies | Energy | Apparent Energy Delivered | Apparent Energy Delivered | 403236 | S64-87-21 | R | 169869315 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase A | Apparent Energy Delivered Phase A | 403542 | S64-87-21 | R | 169869325 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase B | Apparent Energy Delivered Phase B | 403546 | S64-87-21 | R | 169869326 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase C | Apparent Energy Delivered Phase C | 403550 | S64-87-21 | R | 169869327 |  | 1000
DR1 | 900 | Energies | Energy | Apparent Energy Received | Apparent Energy Received | 403240 | S64-87-21 | R | 169869318 |  | 1000
DR1 | 900 | Energies | Energy | Reactive Energy Delivered | Reactive Energy Delivered | 403220 | S64-87-21 | R | 169869316 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase A | Reactive Energy Delivered Phase A | 403530 | S64-87-21 | R | 169869319 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase B | Reactive Energy Delivered Phase B | 403534 | S64-87-21 | R | 169869320 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase C | Reactive Energy Delivered Phase C | 403538 | S64-87-21 | R | 169869321 |  | 1000
DR1 | 900 | Energies | Energy | Reactive Energy Received | Reactive Energy Received | 403224 | S64-87-21 | R | 169869317 |  | 1000
|  | Energies | Energy Since Last Reset | Active Energy Delivered Since Last Reset | Active Energy Delivered Since Last Reset | 403256 | S64-87-21 | R | 169869825 |  | 1000
|  | Energies | Energy Since Last Reset | Apparent Energy Delivered Since Last Reset | Apparent Energy Delivered Since Last Reset | 403288 | S64-87-21 | R | 169869827 |  | 1000
|  | Energies | Energy Since Last Reset | Reactive Energy Delivered Since Last Reset | Reactive Energy Delivered Since Last Reset | 403272 | S64-87-21 | R | 169869826 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate A | Active Energy Delivered Rate A | 404196 | S64-87-21 | R | 169870084 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate B | Active Energy Delivered Rate B | 404200 | S64-87-21 | R | 169870085 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate C | Active Energy Delivered Rate C | 404204 | S64-87-21 | R | 169870086 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate D | Active Energy Delivered Rate D | 404208 | S64-87-21 | R | 169870087 |  | 1000
|  | Energies | Time of Use | Time of Use Active Rate | Time of Use Active Rate | 404191 | UINT16 | R | 169870082
|  | Miscellaneous | DT Last Reset MinMax | DT Last Reset MinMax | DT Last Reset MinMax | 427214 | DateTime3_IEC870_LOCAL | R | 179307265
|  | Miscellaneous | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | 403716 | DateTime3_IEC870_LOCAL | R | 179307777
|  | Miscellaneous | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | 403706 | DateTime3_IEC870_LOCAL | R | 179307521
|  | Miscellaneous | Frequency | Frequency | Frequency | 403110 | F32-4321 | R | 179306497
|  | Miscellaneous | Reactive Factor Total | Reactive Factor Total | Reactive Factor Total | 403108 | F32-4321 | R | 179307009
|  | Miscellaneous | Temperature | Temperature Celsius | Temperature Celsius | 403132 | F32-4321 | R | 179306753
|  | Power Factors | Power Factor A | Power Factor A Load Direction | Power Factor A Load Direction | 403078 | F32-4321 | R | 186646786
|  | Power Factors | Power Factor A | Power Factor Signed Phase A | Power Factor Signed Phase A | 403078 | PF32 | R | 186646785
|  | Power Factors | Power Factor B | Power Factor B Load Direction | Power Factor B Load Direction | 403080 | F32-4321 | R | 186647042
|  | Power Factors | Power Factor B | Power Factor Signed Phase B | Power Factor Signed Phase B | 403080 | PF32 | R | 186647041
|  | Power Factors | Power Factor C | Power Factor C Load Direction | Power Factor C Load Direction | 403082 | F32-4321 | R | 186647298
|  | Power Factors | Power Factor C | Power Factor Signed Phase C | Power Factor Singed Phase C | 403082 | PF32 | R | 186647297
|  | Power Factors | Power Factor Total | Power Factor Signed | Power Factor Signed | 403084 | PF32 | R | 186646532
|  | Power Factors | Power Factor Total | Power Factor Total Load Direction | Power Factor Total Load Direction | 403084 | F32-4321 | R | 186646534
|  | Powers | Power | Apparent Power A | Apparent Power A | 403070 | F32-4321 | R | 190840841
|  | Powers | Power | Apparent Power B | Apparent Power B | 403072 | F32-4321 | R | 190840842
|  | Powers | Power | Apparent Power C | Apparent Power C | 403074 | F32-4321 | R | 190840843
DR1 | 900 | Powers | Power | Apparent Power Total | Apparent Power Total | 403076 | F32-4321 | R | 190840844
|  | Powers | Power | Reactive Power A | Reactive Power A | 403062 | F32-4321 | R | 190840837
|  | Powers | Power | Reactive Power B | Reactive Power B | 403064 | F32-4321 | R | 190840838
|  | Powers | Power | Reactive Power C | Reactive Power C | 403066 | F32-4321 | R | 190840839
|  | Powers | Power | Reactive Power Total | Reactive Power Total | 403068 | F32-4321 | R | 190840840
|  | Powers | Power | Real Power A | Real Power A | 403054 | F32-4321 | R | 190840833
|  | Powers | Power | Real Power B | Real Power B | 403056 | F32-4321 | R | 190840834
|  | Powers | Power | Real Power C | Real Power C | 403058 | F32-4321 | R | 190840835
DR1 | 900 | Powers | Power | Real Power Total | Real Power Total | 403060 | F32-4321 | R | 190840836
|  | Voltages | Voltage | Average Voltage Line-to-Line | Average Voltage Line-to-Line | 403026 | F32-4321 | R | 201326596
|  | Voltages | Voltage | Average Voltage Line-to-Neutral | Average Voltage Line-to-Neutral | 403036 | F32-4321 | R | 201326600
|  | Voltages | Voltage | Voltage Phases AB | Voltage Phases AB | 403020 | F32-4321 | R | 201326593
|  | Voltages | Voltage | Voltage Phases AN | Voltage Phases AN | 403028 | F32-4321 | R | 201326597
|  | Voltages | Voltage | Voltage Phases BC | Voltage Phases BC | 403022 | F32-4321 | R | 201326594
|  | Voltages | Voltage | Voltage Phases BN | Voltage Phases BN | 403030 | F32-4321 | R | 201326598
|  | Voltages | Voltage | Voltage Phases CA | Voltage Phases CA | 403024 | F32-4321 | R | 201326595
|  | Voltages | Voltage | Voltage Phases CN | Voltage Phases CN | 403032 | F32-4321 | R | 201326599
|  | Diagnostics | Meter | Calibration Error | Calibration Error | 445000 | MaskedBool | R | 205520898 | 0x0002 | 2
|  | Diagnostics | Meter | Current Reversed | Current Reversed | 445000 | MaskedBool | R | 205520904 | 0x0020 | 32
|  | Diagnostics | Meter | Energy Pulse Overrun | Energy Pulse Overrun | 445000 | MaskedBool | R | 205520899 | 0x0080 | 128
|  | Diagnostics | Meter | Frequency Setting Error | Frequency Setting Error | 445000 | MaskedBool | R | 205520900 | 0x0004 | 4
|  | Diagnostics | Meter | Meter ON Duration | Meter ON Duration | 402004 | UINT32 | R | 205520897 |  | 3600
|  | Diagnostics | Meter | NVRAM Error | NVRAM Error | 445000 | MaskedBool | R | 205520901 | 0x0001
|  | Diagnostics | Meter | Oscillator Error | Oscillator Error | 445000 | MaskedBool | R | 205520902 | 0x0100 | 256
|  | Diagnostics | Meter | Phase Sequence Reversed | Phase Sequence Reversed | 445000 | MaskedBool | R | 205520903 | 0x0010 | 16
|  | Diagnostics | Meter | RTC Error | RTC Error | 445000 | MaskedBool | R | 205520905 | 0x0040 | 64
|  | Diagnostics | Meter | Wiring Error | Wiring Error | 445000 | MaskedBool | R | 205520906 | 0x0008 | 8
|  | Power Meters | Power Meter | PM1 Nominal Frequency | PM1 Nominal Frequency | 402017 | UINT16 | R | 65547
|  | Power Meters | Power Meter | PM1 CT Primary | PM1 CT Primary | 402030 | UINT16 | R | 65550
|  | Power Meters | Power Meter | PM1 CT Secondary | PM1 CT Secondary | 402031 | UINT16 | R | 65551
|  | Power Meters | Power Meter | PM1 Nominal Phase Rotation | PM1 Nominal Phase Rotation | 402024 | UINT16 | R | 65537
|  | Power Meters | Power Meter | PM1 Volts Mode | PM1 Volts Mode | 402016 | UINT16 | R | 30720
|  | Power Meters | Power Meter | PM1 VT Primary | PM1 VT Primary | 402026 | F32-4321 | R | 65548
|  | Power Meters | Power Meter | PM1 VT Secondary | PM1 VT Secondary | 402028 | UINT16 | R | 65549
|  | Unbalances | Current Unbalance | Current Unbalance A | Current Unbalance A | 403012 | F32-4321 | R | 157286401
|  | Unbalances | Current Unbalance | Current Unbalance B | Current Unbalance B | 403014 | F32-4321 | R | 157286402
|  | Unbalances | Current Unbalance | Current Unbalance C | Current Unbalance C | 403016 | F32-4321 | R | 157286403
|  | Unbalances | Current Unbalance | Current Unbalance Worst | Current Unbalance Worst | 403018 | F32-4321 | R | 157286404
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-B | Voltage Unbalance A-B | 403038 | F32-4321 | R | 157286657
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-N | Voltage Unbalance A-N | 403046 | F32-4321 | R | 157286661
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-C | Voltage Unbalance B-C | 403040 | F32-4321 | R | 157286658
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-N | Voltage Unbalance B-N | 403048 | F32-4321 | R | 157286662
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-A | Voltage Unbalance C-A | 403042 | F32-4321 | R | 157286659
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-N | Voltage Unbalance C-N | 403050 | F32-4321 | R | 157286663
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-L Worst | Voltage Unbalance L-L Worst | 403044 | F32-4321 | R | 157286660
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-N Worst | Voltage Unbalance L-N Worst | 403052 | F32-4321 | R | 157286664
|  | Demand Readings and History | Demand Current | Block Demand Current N | Block Demand Current N | 403862 | F32-4321 | R | 159383816
|  | Demand Readings and History | Demand Current | Current Demand Interval | Current Demand Interval | 403712 | UINT16 | R | 159383815
|  | Demand Readings and History | Demand Current | Current Phase A Sliding Window Demand Delivered-Received | Current Phase A Sliding Window Demand Delivered-Received | 403814 | F32-4321 | R | 159383809
|  | Demand Readings and History | Demand Current | Current Phase Average Sliding Window Demand Delivered-Received | Current Phase Average Sliding Window Demand Delivered-Received | 403878 | F32-4321 | R | 159383813
|  | Demand Readings and History | Demand Current | Current Phase B Sliding Window Demand Delivered-Received | Current Phase B Sliding Window Demand Delivered-Received | 403830 | F32-4321 | R | 159383810
|  | Demand Readings and History | Demand Current | Current Phase C Sliding Window Demand Delivered-Received | Current Phase C Sliding Window Demand Delivered-Received | 403846 | F32-4321 | R | 159383811
|  | Demand Readings and History | Demand Current | Current Demand Calculation Method | Current Demand Calculation Method | 403711 | UINT16 | R | 159383814
DR1 | 900 | Demand Readings and History | Demand Power | Active Power Sliding Window Demand Delivered-Received | Active Power Sliding Window Demand Delivered-Received | 403766 | F32-4321 | R | 159384065
|  | Demand Readings and History | Demand Power | Apparent Power Sliding Window Demand Delivered-Received | Apparent Power Sliding Window Demand Delivered-Received | 403798 | F32-4321 | R | 159384067
|  | Demand Readings and History | Demand Power | Power Demand Interval | Power Demand Interval | 403702 | UINT16 | R | 159384069
|  | Demand Readings and History | Demand Power | Reactive Power Sliding Window Demand Delivered - Received | Reactive Power Sliding Window Demand Delivered - Received | 403782 | F32-4321 | R | 159384066
|  | Demand Readings and History | Demand Power | Power Demand Calculation Method | Power Demand Calculation Method | 403701 | UINT16 | R | 159384068
|  | Demand Readings and History | Peak Demand Apparent Power | Apparent Power Sliding Window Demand Delivered-Received Maximum | Apparent Power Sliding Window Demand Delivered-Received Maximum | 403802 | F32-4321 | R | 159385345
|  | Demand Readings and History | Peak Demand Apparent Power | DT Peak Demand Apparent Power | DT Peak Demand Apparent Power | 403804 | DateTime3_IEC870_LOCAL | R | 159385346
|  | Demand Readings and History | Peak Demand Current A | Current Phase A Sliding Window Demand Delivered-Received Maximum | Current Phase A Sliding Window Demand Delivered-Received Maximum | 403818 | F32-4321 | R | 159383553
|  | Demand Readings and History | Peak Demand Current A | DT Peak Demand Current A | DT Peak Demand Current A | 403820 | DateTime3_IEC870_LOCAL | R | 159383554
|  | Demand Readings and History | Peak Demand Current Avg | Current Phase Average Sliding Window Demand Delivered-Received Maximum | Current Phase Average Sliding Window Demand Delivered-Received Maximum | 403882 | F32-4321 | R | 159385857
|  | Demand Readings and History | Peak Demand Current Avg | DT Peak Demand Current Avg | DT Peak Demand Current Avg | 403884 | DateTime3_IEC870_LOCAL | R | 159385858
|  | Demand Readings and History | Peak Demand Current B | Current Phase B Sliding Window Demand Delivered-Received Maximum | Current Phase B Sliding Window Demand Delivered-Received Maximum | 403834 | F32-4321 | R | 159384321
|  | Demand Readings and History | Peak Demand Current B | DT Peak Demand Current B | DT Peak Demand Current B | 403836 | DateTime3_IEC870_LOCAL | R | 159384322
|  | Demand Readings and History | Peak Demand Current C | Current Phase C Sliding Window Demand Delivered-Received Maximum | Current Phase C Sliding Window Demand Delivered-Received Maximum | 403850 | F32-4321 | R | 159384577
|  | Demand Readings and History | Peak Demand Current C | DT Peak Demand Current C | DT Peak Demand Current C | 403852 | DateTime3_IEC870_LOCAL | R | 159384578
|  | Demand Readings and History | Peak Demand Current N | Current Phase N Sliding Window Demand Delivered-Received Maximum | Current Phase N Sliding Window Demand Delivered-Received Maximum | 403866 | F32-4321 | R | 159385601
|  | Demand Readings and History | Peak Demand Current N | DT Peak Demand Current N | DT Peak Demand Current N | 403868 | DateTime3_IEC870_LOCAL | R | 159385602
|  | Demand Readings and History | Peak Demand Reactive Power | DT Peak Demand Reactive Power | DT Peak Demand Reactive Power | 403788 | DateTime3_IEC870_LOCAL | R | 159385090
|  | Demand Readings and History | Peak Demand Reactive Power | Reactive Power Sliding Window Demand Delivered - Received Maximum | Reactive Power Sliding Window Demand Delivered - Received Maximum | 403786 | F32-4321 | R | 159385089
|  | Demand Readings and History | Peak Demand Real Power | Active Power Sliding Window Demand Delivered-Received Maximum | Active Power Sliding Window Demand Delivered-Received Maximum | 403770 | F32-4321 | R | 159384833
|  | Demand Readings and History | Peak Demand Real Power | DT Peak Demand Real Power | DT Peak Demand Real Power | 403772 | DateTime3_IEC870_LOCAL | R | 159384834
|  | Power Quality | THD Current | Current Total Harmonic Distortion Neutral | Current Total Harmonic Distortion Neutral | 421306 | F32-4321 | R | 161480708
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase A | Current Total Harmonic Distortion Phase A | 421300 | F32-4321 | R | 161480705
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase B | Current Total Harmonic Distortion Phase B | 421302 | F32-4321 | R | 161480706
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase C | Current Total Harmonic Distortion Phase C | 421304 | F32-4321 | R | 161480707
|  | Power Quality | THD Current | Current Total Harmonic Distortion Worst | Current Total Harmonic Distortion Worst | 445108 | F32-4321 | R | 161480709
|  | Power Quality | THD Voltage | THD Voltage A-B | THD Voltage A-B | 421322 | F32-4321 | R | 161480961
|  | Power Quality | THD Voltage | THD Voltage A-N | THD Voltage A-N | 421330 | F32-4321 | R | 161480965
|  | Power Quality | THD Voltage | THD Voltage B-C | THD Voltage B-C | 421324 | F32-4321 | R | 161480962
|  | Power Quality | THD Voltage | THD Voltage B-N | THD Voltage B-N | 421332 | F32-4321 | R | 161480966
|  | Power Quality | THD Voltage | THD Voltage C-A | THD Voltage C-A | 421326 | F32-4321 | R | 161480963
|  | Power Quality | THD Voltage | THD Voltage C-N | THD Voltage C-N | 421334 | F32-4321 | R | 161480967
|  | Power Quality | THD Voltage | THD Voltage L-L | THD Voltage L-L | 421328 | F32-4321 | R | 161480964
|  | Power Quality | THD Voltage | THD Voltage L-L Worst | THD Voltage L-L Worst | 445118 | F32-4321 | R | 161480969
|  | Power Quality | THD Voltage | THD Voltage L-N | THD Voltage L-N | 421338 | F32-4321 | R | 161480968
|  | Power Quality | THD Voltage | THD Voltage L-N Worst | THD Voltage L-N Worst | 445128 | F32-4321 | R | 161480970
|  | Minimum Readings | Min Current | Current Phase A Minimum | Current Phase A Minimum | 427218 | F32-4321 | R | 162529281
|  | Minimum Readings | Min Current | Current Phase Average Minimum | Current Phase Average Minimum | 427228 | F32-4321 | R | 162529285
|  | Minimum Readings | Min Current | Current Phase B Minimum | Current Phase B Minimum | 427220 | F32-4321 | R | 162529282
|  | Minimum Readings | Min Current | Current Phase C Minimum | Current Phase C Minimum | 427222 | F32-4321 | R | 162529283
|  | Minimum Readings | Min Current | Min Current | Min Current | 445134 | F32-4321 | R | 162529286
|  | Minimum Readings | Min Current | Neutral Current Minimum | Neutral Current Minimum | 427224 | F32-4321 | R | 162529284
|  | Minimum Readings | Min Frequency | Frequency Minimum | Frequency Minimum | 427616 | F32-4321 | R | 162531585
|  | Minimum Readings | Min Power | Active Power Minimum | Active Power Minimum | 427278 | F32-4321 | R | 162530052
|  | Minimum Readings | Min Power | Active Power Phase A Minimum | Active Power Phase A Minimum | 427272 | F32-4321 | R | 162530049
|  | Minimum Readings | Min Power | Active Power Phase B Minimum | Active Power Phase B Minimum | 427274 | F32-4321 | R | 162530050
|  | Minimum Readings | Min Power | Active Power Phase C Minimum | Active Power Phase C Minimum | 427276 | F32-4321 | R | 162530051
|  | Minimum Readings | Min Power | Apparent Power Minimum | Apparent Power Minimum | 427294 | F32-4321 | R | 162530060
|  | Minimum Readings | Min Power | Apparent Power Phase A Minimum | Apparent Power Phase A Minimum | 427288 | F32-4321 | R | 162530057
|  | Minimum Readings | Min Power | Apparent Power Phase B Minimum | Apparent Power Phase B Minimum | 427290 | F32-4321 | R | 162530058
|  | Minimum Readings | Min Power | Apparent Power Phase C Minimum | Apparent Power Phase C Minimum | 427292 | F32-4321 | R | 162530059
|  | Minimum Readings | Min Power | Reactive Power Minimum | Reactive Power Minimum | 427286 | F32-4321 | R | 162530056
|  | Minimum Readings | Min Power | Reactive Power Phase A Minimum | Reactive Power Phase A Minimum | 427280 | F32-4321 | R | 162530053
|  | Minimum Readings | Min Power | Reactive Power Phase B Minimum | Reactive Power Phase B Minimum | 427282 | F32-4321 | R | 162530054
|  | Minimum Readings | Min Power | Reactive Power Phase C Minimum | Reactive Power Phase C Minimum | 427284 | F32-4321 | R | 162530055
|  | Minimum Readings | Min Power Factor A | Min Power Factor A | Min Power Factor A | 427306 | PF32 | R | 162530305
|  | Minimum Readings | Min Power Factor A | Min Power Factor A Load Direction | Min Power Factor A Load Direction | 427306 | F32-4321 | R | 162530306
|  | Minimum Readings | Min Power Factor B | Min Power Factor B | Min Power Factor B | 427308 | PF32 | R | 162530561
|  | Minimum Readings | Min Power Factor B | Min Power Factor B Load Direction | Min Power Factor B Load Direction | 427308 | F32-4321 | R | 162530562
|  | Minimum Readings | Min Power Factor C | Min Power Factor C | Min Power Factor C | 427310 | PF32 | R | 162530817
|  | Minimum Readings | Min Power Factor C | Min Power Factor C Load Direction | Min Power Factor C Load Direction | 427310 | F32-4321 | R | 162530818
|  | Minimum Readings | Min Power Factor Total | Min Power Factor | Min Power Factor | 427312 | PF32 | R | 162531073
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total Load Direction | Min Power Factor Total Load Direction | 427312 | F32-4321 | R | 162531074
|  | Minimum Readings | Min Reactive Factor Total | Min Reactive Factor Total | Min Reactive Factor Total | 427336 | F32-4321 | R | 162531329
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase A Minimum | Current Total Harmonic Distortion Phase A Minimum | 427338 | F32-4321 | R | 162529537
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase B Minimum | Current Total Harmonic Distortion Phase B Minimum | 427340 | F32-4321 | R | 162529538
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase C Minimum | Current Total Harmonic Distortion Phase C Minimum | 427342 | F32-4321 | R | 162529539
|  | Minimum Readings | Min THD Current | Min THD Current N | Min THD Current N | 427344 | F32-4321 | R | 162529540
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-L | Min THD Voltage L-L | 427366 | F32-4321 | R | 162531847
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-N | Min THD Voltage L-N | 427376 | F32-4321 | R | 162531848
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Minimum | 427368 | F32-4321 | R | 162531844
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Minimum | 427370 | F32-4321 | R | 162531845
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Minimum | 427372 | F32-4321 | R | 162531846
|  | Minimum Readings | Min THD Voltage | Voltage Phases AB Total Harmonic Distortion Minimum | Voltage Phases AB Total Harmonic Distortion Minimum | 427360 | F32-4321 | R | 162531841
|  | Minimum Readings | Min THD Voltage | Voltage Phases BC Total Harmonic Distortion Minimum | Voltage Phases BC Total Harmonic Distortion Minimum | 427362 | F32-4321 | R | 162531842
|  | Minimum Readings | Min THD Voltage | Voltage Phases CA Total Harmonic Distortion Minimum | Voltage Phases CA Total Harmonic Distortion Minimum | 427364 | F32-4321 | R | 162531843
|  | Minimum Readings | Min Voltage | Average Voltage Line-to-Line Minimum | Average Voltage Line-to-Line Minimum | 427244 | F32-4321 | R | 162529799
|  | Minimum Readings | Min Voltage | Average Voltage Line-to-Neutral Minimum | Average Voltage Line-to-Neutral Minimum | 427254 | F32-4321 | R | 162529800
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase A Minimum | Voltage Line-to-Neutral Phase A Minimum | 427246 | F32-4321 | R | 162529796
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase B Minimum | Voltage Line-to-Neutral Phase B Minimum | 427248 | F32-4321 | R | 162529797
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase C Minimum | Voltage Line-to-Neutral Phase C Minimum | 427250 | F32-4321 | R | 162529798
|  | Minimum Readings | Min Voltage | Voltage Phases AB Minimum | Voltage Phases AB Minimum | 427238 | F32-4321 | R | 162529793
|  | Minimum Readings | Min Voltage | Voltage Phases BC Minimum | Voltage Phases BC Minimum | 427240 | F32-4321 | R | 162529794
|  | Minimum Readings | Min Voltage | Voltage Phases CA Minimum | Voltage Phases CA Minimum | 427242 | F32-4321 | R | 162529795
|  | Minimum Readings | Minimum Readings Date Time | Min Current Date Time | Min Current Date Time | 445130 | DateTime3_IEC870_LOCAL | R | 162532097
|  | Minimum Readings | Minimum Readings Date Time | Min Power Factor Date Time | Min Power Factor Date Time | 445136 | DateTime3_IEC870_LOCAL | R | 162532098
|  | Maximum Readings | Max Current | Average Current Maximum | Average Current Maximum | 427704 | F32-4321 | R | 163577861
|  | Maximum Readings | Max Current | Current Phase A Maximum | Current Phase A Maximum | 427694 | F32-4321 | R | 163577857
|  | Maximum Readings | Max Current | Current Phase B Maximum | Current Phase B Maximum | 427696 | F32-4321 | R | 163577858
|  | Maximum Readings | Max Current | Current Phase C Maximum | Current Phase C Maximum | 427698 | F32-4321 | R | 163577859
|  | Maximum Readings | Max Current | Max Current | Max Current | 445146 | F32-4321 | R | 163577862
|  | Maximum Readings | Max Current | Neutral Current Maximum | Neutral Current Maximum | 427700 | F32-4321 | R | 163577860
|  | Maximum Readings | Max Frequency | Frequency Maximum | Frequency Maximum | 428092 | F32-4321 | R | 163580161
|  | Maximum Readings | Max Power | Active Power Maximum | Active Power Maximum | 427754 | F32-4321 | R | 163578628
|  | Maximum Readings | Max Power | Active Power Phase A Maximum | Active Power Phase A Maximum | 427748 | F32-4321 | R | 163578625
|  | Maximum Readings | Max Power | Active Power Phase B Maximum | Active Power Phase B Maximum | 427750 | F32-4321 | R | 163578626
|  | Maximum Readings | Max Power | Active Power Phase C Maximum | Active Power Phase C Maximum | 427752 | F32-4321 | R | 163578627
|  | Maximum Readings | Max Power | Apparent Power Maximum | Apparent Power Maximum | 427770 | F32-4321 | R | 163578636
|  | Maximum Readings | Max Power | Apparent Power Phase A Maximum | Apparent Power Phase A Maximum | 427764 | F32-4321 | R | 163578633
|  | Maximum Readings | Max Power | Apparent Power Phase B Maximum | Apparent Power Phase B Maximum | 427766 | F32-4321 | R | 163578634
|  | Maximum Readings | Max Power | Apparent Power Phase C Maximum | Apparent Power Phase C Maximum | 427768 | F32-4321 | R | 163578635
|  | Maximum Readings | Max Power | Reactive Power Maximum | Reactive Power Maximum | 427762 | F32-4321 | R | 163578632
|  | Maximum Readings | Max Power | Reactive Power Phase A Maximum | Reactive Power Phase A Maximum | 427756 | F32-4321 | R | 163578629
|  | Maximum Readings | Max Power | Reactive Power Phase B Maximum | Reactive Power Phase B Maximum | 427758 | F32-4321 | R | 163578630
|  | Maximum Readings | Max Power | Reactive Power Phase C Maximum | Reactive Power Phase C Maximum | 427760 | F32-4321 | R | 163578631
|  | Maximum Readings | Max Power Factor A | Max Power Factor A | Max Power Factor A | 427782 | PF32 | R | 163578881
|  | Maximum Readings | Max Power Factor A | Max Power Factor A Load Direction | Max Power Factor A Load Direction | 427782 | F32-4321 | R | 163578882
|  | Maximum Readings | Max Power Factor B | Max Power Factor B | Max Power Factor B | 427784 | PF32 | R | 163579137
|  | Maximum Readings | Max Power Factor B | Max Power Factor B Load Direction | Max Power Factor B Load Direction | 427784 | F32-4321 | R | 163579138
|  | Maximum Readings | Max Power Factor C | Max Power Factor C | Max Power Factor C | 427786 | PF32 | R | 163579393
|  | Maximum Readings | Max Power Factor C | Max Power Factor C Load Direction | Max Power Factor C Load Direction | 427786 | F32-4321 | R | 163579394
|  | Maximum Readings | Max Power Factor Total | Max Power Factor | Max Power Factor | 427788 | PF32 | R | 163579649
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total Load Direction | Max Power Factor Total Load Direction | 427788 | F32-4321 | R | 163579650
|  | Maximum Readings | Max Reactive Factor Total | Max Reactive Factor Total | Max Reactive Factor Total | 427812 | F32-4321 | R | 163579905
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase A Maximum | Current Total Harmonic Distortion Phase A Maximum | 427814 | F32-4321 | R | 163578113
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase B Maximum | Current Total Harmonic Distortion Phase B Maximum | 427816 | F32-4321 | R | 163578114
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase C Maximum | Current Total Harmonic Distortion Phase C Maximum | 427818 | F32-4321 | R | 163578115
|  | Maximum Readings | Max THD Current | Max THD Current N | Max THD Current N | 427820 | F32-4321 | R | 163578116
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-L | Max THD Voltage L-L | 427842 | F32-4321 | R | 163580422
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-N | Max THD Voltage L-N | 427852 | F32-4321 | R | 163580423
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Maximum | 427844 | F32-4321 | R | 163580420
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Maximum | 427846 | F32-4321 | R | 163580421
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Maximum | 427848 | F32-4321 | R | 163580424
|  | Maximum Readings | Max THD Voltage | Voltage Phases AB Total Harmonic Distortion Maximum | Voltage Phases AB Total Harmonic Distortion Maximum | 427836 | F32-4321 | R | 163580417
|  | Maximum Readings | Max THD Voltage | Voltage Phases BC Total Harmonic Distortion Maximum | Voltage Phases BC Total Harmonic Distortion Maximum | 427838 | F32-4321 | R | 163580418
|  | Maximum Readings | Max THD Voltage | Voltage Phases CA Total Harmonic Distortion Maximum | Voltage Phases CA Total Harmonic Distortion Maximum | 427840 | F32-4321 | R | 163580419
|  | Maximum Readings | Max Voltage | Average Voltage Line-to-Line Maximum | Average Voltage Line-to-Line Maximum | 427720 | F32-4321 | R | 163578375
|  | Maximum Readings | Max Voltage | Average Voltage Line-to-Neutral Maximum | Average Voltage Line-to-Neutral Maximum | 427730 | F32-4321 | R | 163578376
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase A Maximum | Voltage Line-to-Neutral Phase A Maximum | 427722 | F32-4321 | R | 163578372
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase B Maximum | Voltage Line-to-Neutral Phase B Maximum | 427724 | F32-4321 | R | 163578373
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase C Maximum | Voltage Line-to-Neutral Phase C Maximum | 427726 | F32-4321 | R | 163578374
|  | Maximum Readings | Max Voltage | Voltage Phases AB Maximum | Voltage Phases AB Maximum | 427714 | F32-4321 | R | 163578369
|  | Maximum Readings | Max Voltage | Voltage Phases BC Maximum | Voltage Phases BC Maximum | 427716 | F32-4321 | R | 163578370
|  | Maximum Readings | Max Voltage | Voltage Phases CA Maximum | Voltage Phases CA Maximum | 427718 | F32-4321 | R | 163578371
|  | Maximum Readings | Maximum Readings Date Time | Max Apparent Power Total Date Time | Max Apparent Power Total Date Time | 445154 | DateTime3_IEC870_LOCAL | R | 163580674
|  | Maximum Readings | Maximum Readings Date Time | Max Power Factor Date Time | Max Power Factor Date Time | 445160 | DateTime3_IEC870_LOCAL | R | 163580675
|  | Maximum Readings | Maximum Readings Date Time | Max Real Power Total Date Time | Max Real Power Total Date Time | 445148 | DateTime3_IEC870_LOCAL | R | 163580673
|  | Labels | Alarm Labels | Over Current Alarm |  |  |  |  | 14000
|  | Labels | Alarm Labels | Under Current Alarm |  |  |  |  | 14020
|  | Labels | Alarm Labels | Over Voltage L-L Alarm |  |  |  |  | 14080
|  | Labels | Alarm Labels | Under Voltage L-L Alarm |  |  |  |  | 14100
|  | Labels | Alarm Labels | Over Voltage L-N Alarm |  |  |  |  | 14120
|  | Labels | Alarm Labels | Under Voltage L-N Alarm |  |  |  |  | 14140
|  | Labels | Alarm Labels | Over Active Power Alarm |  |  |  |  | 14160
|  | Labels | Alarm Labels | Over Reactive Power Alarm |  |  |  |  | 14180
|  | Labels | Alarm Labels | Over Apparent Power Alarm |  |  |  |  | 14200
|  | Labels | Alarm Labels | Leading Power Factor Alarm |  |  |  |  | 14220
|  | Labels | Alarm Labels | Lagging Power Factor Alarm |  |  |  |  | 14240
|  | Labels | Alarm Labels | Over Demand Active Power Present Alarm |  |  |  |  | 14300
|  | Labels | Alarm Labels | Over Demand Apparent Power Present Alarm |  |  |  |  | 14420
|  | Labels | Alarm Labels | Over THD Voltage Alarm |  |  |  |  | 14540
|  | Labels | Alarm Labels | Under Active Power Alarm |  |  |  |  | 14820
|  | Labels | Alarm Labels | Over THD Current Alarm |  |  |  |  | 14860
|  | Labels | Alarm Labels | Over THD Voltage L-N Alarm |  |  |  |  | 14900
|  | Labels | Alarm Labels | Over Active Energy Alarm |  |  |  |  | 14940
|  | Labels | Alarm Labels | [5 empty] | 2543
|  | Labels | Alarm Labels | Phase A |  |  |  |  | 2544
|  | Labels | Alarm Labels | Phase B |  |  |  |  | 2545
|  | Labels | Alarm Labels | Phase C |  |  |  |  | 2546
|  | Labels | Alarm Labels | Phases A and B |  |  |  |  | 2547
|  | Labels | Alarm Labels | Phases B and C |  |  |  |  | 2548
|  | Labels | Alarm Labels | Phases A and C |  |  |  |  | 2549
|  | Labels | Alarm Labels | Phases A, B and C |  |  |  |  | 2550
|  | Labels | Alarm Labels | Neutral |  |  |  |  | 2551
|  | Labels | Alarm Labels | Earth |  |  |  |  | 2552
|  | Labels | Alarm Labels | Neutral-Earth |  |  |  |  | 2553
|  | Labels | Alarm Labels | Phase A-B |  |  |  |  | 2564
|  | Labels | Alarm Labels | Phase B-C |  |  |  |  | 2565
|  | Labels | Alarm Labels | Phase C-A |  |  |  |  | 2566
|  | Labels | Alarm Labels | Phases A-B and B-C |  |  |  |  | 2567
|  | Labels | Alarm Labels | Phases B-C and C-A |  |  |  |  | 2568
|  | Labels | Alarm Labels | Phases A-B and C-A |  |  |  |  | 2569
|  | Labels | Alarm Labels | Phases A-B, B-C and C-A |  |  |  |  | 2570
|  | Labels | Alarm Labels | Phase A-N |  |  |  |  | 2584
|  | Labels | Alarm Labels | Phase B-N |  |  |  |  | 2585
|  | Labels | Alarm Labels | Phase C-N |  |  |  |  | 2586
|  | Labels | Alarm Labels | Phases A-N and B-N |  |  |  |  | 2587
|  | Labels | Alarm Labels | Phases B-N and C-N |  |  |  |  | 2588
|  | Labels | Alarm Labels | Phases A-N and C-N |  |  |  |  | 2589
|  | Labels | Alarm Labels | Phases A-N, B-N and C-N |  |  |  |  | 2590
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Trigger |  |  |  |  | 165675011
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Period |  |  |  |  | 165675009
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Sync Mode |  |  |  |  | 165675010
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  |  |  |  | 166723585
|  | DataRecorder Modules | Data Rec 1 | RE1 Data Log |  |  |  |  | 167772161
|  | DataRecorder Modules | Data Rec 1 | RE1 Log State |  |  |  |  | 167772162
|  | DataRecorder Modules | Data Rec 1 | RE1 Records Left |  |  |  |  | 167772163
|  | DataRecorder Modules | Data Rec 1 | RE1 Record Complete |  |  |  |  | 167772164
|  | DataRecorder Modules | Data Rec 1 | RE1 Depth |  |  |  |  | 167772165
|  | DataRecorder Modules | Data Rec 1 | RE1 RecordMode |  |  |  |  | 167772166
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Threshold |  |  |  |  | 167772167
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Action |  |  |  |  | 167772168

## PM3255
PM3255 Translator Details
Data Recorder | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | ModbusAddr | Format | RequestType | IONHandle | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | 400090 | UINT16 | R | 4864
|  | Factory Information | Factory 1 | FAC1 Compliance |  |  |  |  | 4865
|  | Factory Information | Factory 1 | FAC1 Options |  |  |  |  | 4866
|  | Factory Information | Factory 1 | FAC1 Revision | FAC1 Revision | 401637 | UINT16 | R | 4867
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | 400130 | UINT32 | R | 4868
|  | Factory Information | Factory 1 | FAC1 ION Version |  |  |  |  | 30510
|  | Factory Information | Factory 1 | FAC1 Template |  |  |  |  | 4989
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | 400030 | ASCII | R | 22340 |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 Manuf Date Time | FAC1 Manuf Date Time | 400132 | DateTime3_IEC870_LOCAL | R | 30129
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | 401845 | DateTime3_IEC870_LOCAL | R | 65546
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | 401845 | DateTime3_IEC870_LOCAL | R | 23420
|  | Resets and Triggers | Digital Outputs | DO1 De-Energize |  |  |  |  | 156238339
|  | Resets and Triggers | Digital Outputs | DO2 De-Energize |  |  |  |  | 156238340
|  | Resets and Triggers | Digital Outputs | DO1 Energize |  |  |  |  | 156238337
|  | Resets and Triggers | Digital Outputs | DO2 Energize |  |  |  |  | 156238338
|  | Resets and Triggers | Resets | Energy Reset | Energy Reset | 405250 | U16-21-ARRAY | CW | 156237828
|  | Resets and Triggers | Resets | Input Metering Accum All Channels Reset | Input Metering Accum All Channels Reset | 405250 | U16-21-ARRAY | CW | 156237827
|  | Resets and Triggers | Resets | Min Max Reset | Min Max Reset | 405250 | U16-21-ARRAY | CW | 156237826
|  | Resets and Triggers | Resets | Peak Demand Reset | Peak Demand Reset | 405250 | U16-21-ARRAY | CW | 156237825
|  | Resets and Triggers | Time Of Use Rate Control | Time Of Use Rate Control | Time Of Use Rate Control | 404191 | UINT16 | RW | 156238081
|  | Alarms - Over Under | Alarms - Global Setup | Over Under Global Alarm Dropout Setpoint | Over Under Global Alarm Dropout Setpoint | 414009 | F32-4321 | RW | 160433665
|  | Alarms - Over Under | Alarms - Global Setup | Over Under Global Alarm Pickup Delay | Over Under Global Alarm Pickup Delay | 414007 | UINT32 | RW | 160433666
|  | Alarms - Over Under | Alarms - Global Setup | Over Under Global Alarm Output | Over Under Global Alarm Output | 414013 | UINT16 | RW | 160433667 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Active Energy | Over Active Energy Alarm | Over Active Energy Alarm | 411024 | MaskedBool | R | 160436737 | 0x0001
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Alarm Priority | Over Active Energy-Alarm Priority | 414940 | UINT32 | R | 160436739 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Pickup Delay | Over Active Energy-Pickup Delay | 414947 | UINT32 | R | 160436741
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Dropout Setpoint | Over Active Energy-Dropout Setpoint | 414949 | F32-4321 | R | 160436742
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Dropout Delay | Over Active Energy-Dropout Delay | 414951 | UINT32 | R | 160436743
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Alarm Output | Over Active Energy-Alarm Output | 414953 | UINT16 | R | 160436744 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Alarm Enabled | Over Active Energy-Alarm Enabled | 414940 | UINT32 | RW | 160436738 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Energy | Over Active Energy-Pickup Setpoint | Over Active Energy-Pickup Setpoint | 414945 | F32-4321 | RW | 160436740
|  | Alarms - Over Under | Over Active Power | Over Active Power Alarm | Over Active Power Alarm | 411021 | MaskedBool | R | 160432129 | 0x0100 | 256
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Output | Over Active Power-Alarm Output | 414173 | UINT16 | R | 160432136 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Priority | Over Active Power-Alarm Priority | 414160 | UINT32 | R | 160432131 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Delay | Over Active Power-Dropout Delay | 414171 | UINT32 | R | 160432135
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Setpoint | Over Active Power-Dropout Setpoint | 414169 | F32-4321 | R | 160432134
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Delay | Over Active Power-Pickup Delay | 414167 | UINT32 | R | 160432133
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Enabled | Over Active Power-Alarm Enabled | 414160 | UINT32 | RW | 160432130 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Setpoint | Over Active Power-Pickup Setpoint | 414165 | F32-4321 | RW | 160432132
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power Alarm | Over Apparent Power Alarm | 411021 | MaskedBool | R | 160433153 | 0x0400 | 1024
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Output | Over Apparent Power-Alarm Output | 414213 | UINT16 | R | 160433160 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Priority | Over Apparent Power-Alarm Priority | 414200 | UINT32 | R | 160433155 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Delay | Over Apparent Power-Dropout Delay | 414211 | UINT32 | R | 160433159
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Setpoint | Over Apparent Power-Dropout Setpoint | 414209 | F32-4321 | R | 160433158
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Delay | Over Apparent Power-Pickup Delay | 414207 | UINT32 | R | 160433157
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Enabled | Over Apparent Power-Alarm Enabled | 414200 | UINT32 | RW | 160433154 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Setpoint | Over Apparent Power-Pickup Setpoint | 414205 | F32-4321 | RW | 160433156
|  | Alarms - Over Under | Over Current Phase | Over Current Phase Alarm | Over Current Phase Alarm | 411021 | MaskedBool | R | 160432385 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Output | Over Current Phase-Alarm Output | 414013 | UINT16 | R | 160432392 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Priority | Over Current Phase-Alarm Priority | 414000 | UINT32 | R | 160432387 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Delay | Over Current Phase-Dropout Delay | 414011 | UINT32 | R | 160432391
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Setpoint | Over Current Phase-Dropout Setpoint | 414009 | F32-4321 | R | 160432390
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Delay | Over Current Phase-Pickup Delay | 414007 | UINT32 | R | 160432389
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Enabled | Over Current Phase-Alarm Enabled | 414000 | UINT32 | RW | 160432386 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Setpoint | Over Current Phase-Pickup Setpoint | 414005 | F32-4321 | RW | 160432388
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present Alarm | Over Demand Active Power Present Alarm | 411021 | MaskedBool | R | 160435457 | 0x8000 | 32768
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Output | Over Demand Active Power Present-Alarm Output | 414313 | UINT16 | R | 160435464 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Priority | Over Demand Active Power Present-Alarm Priority | 414300 | UINT32 | R | 160435459 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Delay | Over Demand Active Power Present-Dropout Delay | 414311 | UINT32 | R | 160435463
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Setpoint | Over Demand Active Power Present-Dropout Setpoint | 414309 | F32-4321 | R | 160435462
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Delay | Over Demand Active Power Present-Pickup Delay | 414307 | UINT32 | R | 160435461
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Enabled | Over Demand Active Power Present-Alarm Enabled | 414300 | UINT32 | RW | 160435458 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Setpoint | Over Demand Active Power Present-Pickup Setpoint | 414305 | F32-4321 | RW | 160435460
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present Alarm | Over Demand Apparent Power Present Alarm | 411022 | MaskedBool | R | 160435713 | 0x0020 | 32
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Output | Over Demand Apparent Power Present-Alarm Output | 414433 | UINT16 | R | 160435720 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Priority | Over Demand Apparent Power Present-Alarm Priority | 414420 | UINT32 | R | 160435715 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Delay | Over Demand Apparent Power Present-Dropout Delay | 414431 | UINT32 | R | 160435719
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Setpoint | Over Demand Apparent Power Present-Dropout Setpoint | 414429 | F32-4321 | R | 160435718
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Delay | Over Demand Apparent Power Present-Pickup Delay | 414427 | UINT32 | R | 160435717
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Enabled | Over Demand Apparent Power Present-Alarm Enabled | 414420 | UINT32 | RW | 160435714 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Setpoint | Over Demand Apparent Power Present-Pickup Setpoint | 414425 | F32-4321 | RW | 160435716
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor Alarm | Lagging Power Factor Alarm | 411021 | MaskedBool | R | 160435201 | 0x1000 | 4096
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Output | Lagging Power Factor-Alarm Output | 414253 | UINT16 | R | 160435208 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Priority | Lagging Power Factor-Alarm Priority | 414240 | UINT32 | R | 160435203 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Delay | Lagging Power Factor-Dropout Delay | 414251 | UINT32 | R | 160435207
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Setpoint | Lagging Power Factor-Dropout Setpoint | 414249 | F32-4321 | R | 160435206
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Delay | Lagging Power Factor-Pickup Delay | 414247 | UINT32 | R | 160435205
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Enabled | Lagging Power Factor-Alarm Enabled | 414240 | UINT32 | RW | 160435202 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Setpoint | Lagging Power Factor-Pickup Setpoint | 414245 | F32-4321 | RW | 160435204
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor Alarm | Leading Power Factor Alarm | 411021 | MaskedBool | R | 160434945 | 0x0800 | 2048
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Output | Leading Power Factor-Alarm Output | 414233 | UINT16 | R | 160434952 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Priority | Leading Power Factor-Alarm Priority | 414220 | UINT32 | R | 160434947 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Delay | Leading Power Factor-Dropout Delay | 414231 | UINT32 | R | 160434951
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Setpoint | Leading Power Factor-Dropout Setpoint | 414229 | F32-4321 | R | 160434950
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Delay | Leading Power Factor-Pickup Delay | 414227 | UINT32 | R | 160434949
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Enabled | Leading Power Factor-Alarm Enabled | 414220 | UINT32 | RW | 160434946 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Setpoint | Leading Power Factor-Pickup Setpoint | 414225 | F32-4321 | RW | 160434948
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power Alarm | Over Reactive Power Alarm | 411021 | MaskedBool | R | 160434689 | 0x0200 | 512
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Output | Over Reactive Power-Alarm Output | 414193 | UINT16 | R | 160434696 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Priority | Over Reactive Power-Alarm Priority | 414180 | UINT32 | R | 160434691 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Delay | Over Reactive Power-Dropout Delay | 414191 | UINT32 | R | 160434695
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Setpoint | Over Reactive Power-Dropout Setpoint | 414189 | F32-4321 | R | 160434694
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Delay | Over Reactive Power-Pickup Delay | 414187 | UINT32 | R | 160434693
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Enabled | Over Reactive Power-Alarm Enabled | 414180 | UINT32 | RW | 160434690 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Setpoint | Over Reactive Power-Pickup Setpoint | 414185 | F32-4321 | RW | 160434692
|  | Alarms - Over Under | Over THD Current | Over THD Current Alarm | Over THD Current Alarm | 411022 | MaskedBool | R | 160436225 | 0x4000 | 16384
|  | Alarms - Over Under | Over THD Current | Over THD Current-Alarm Output | Over THD Current-Alarm Output | 414873 | UINT16 | R | 160436232 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over THD Current | Over THD Current-Alarm Priority | Over THD Current-Alarm Priority | 414860 | UINT32 | R | 160436227 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over THD Current | Over THD Current-Dropout Delay | Over THD Current-Dropout Delay | 414871 | UINT32 | R | 160436231
|  | Alarms - Over Under | Over THD Current | Over THD Current-Dropout Setpoint | Over THD Current-Dropout Setpoint | 414869 | F32-4321 | R | 160436230
|  | Alarms - Over Under | Over THD Current | Over THD Current-Pickup Delay | Over THD Current-Pickup Delay | 414867 | UINT32 | R | 160436229
|  | Alarms - Over Under | Over THD Current | Over THD Current-Alarm Enabled | Over THD Current-Alarm Enabled | 414860 | UINT32 | RW | 160436226 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Current | Over THD Current-Pickup Setpoint | Over THD Current-Pickup Setpoint | 414865 | F32-4321 | RW | 160436228
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage Alarm | Over THD Voltage Alarm | 411022 | MaskedBool | R | 160435969 | 0x0800 | 2048
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Output | Over THD Voltage-Alarm Output | 414553 | UINT16 | R | 160435976 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Priority | Over THD Voltage-Alarm Priority | 414540 | UINT32 | R | 160435971 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Delay | Over THD Voltage-Dropout Delay | 414551 | UINT32 | R | 160435975
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Setpoint | Over THD Voltage-Dropout Setpoint | 414549 | F32-4321 | R | 160435974
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Delay | Over THD Voltage-Pickup Delay | 414547 | UINT32 | R | 160435973
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Enabled | Over THD Voltage-Alarm Enabled | 414540 | UINT32 | RW | 160435970 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Setpoint | Over THD Voltage-Pickup Setpoint | 414545 | F32-4321 | RW | 160435972
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N Alarm | Over THD Voltage L-N Alarm | 411022 | MaskedBool | R | 160436481 | 0x8000 | 32768
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Alarm Output | Over THD Voltage L-N-Alarm Output | 414913 | UINT16 | R | 160436488 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Alarm Priority | Over THD Voltage L-N-Alarm Priority | 414900 | UINT32 | R | 160436483 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Dropout Delay | Over THD Voltage L-N-Dropout Delay | 414911 | UINT32 | R | 160436487
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Dropout Setpoint | Over THD Voltage L-N-Dropout Setpoint | 414909 | F32-4321 | R | 160436486
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Pickup Delay | Over THD Voltage L-N-Pickup Delay | 414907 | UINT32 | R | 160436485
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Alarm Enabled | Over THD Voltage L-N-Alarm Enabled | 414900 | UINT32 | RW | 160436482 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Voltage L-N | Over THD Voltage L-N-Pickup Setpoint | Over THD Voltage L-N-Pickup Setpoint | 414905 | F32-4321 | RW | 160436484
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L Alarm | Over Voltage L-L Alarm | 411021 | MaskedBool | R | 160434177 | 0x0010 | 16
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Output | Over Voltage L-L-Alarm Output | 414093 | UINT16 | R | 160434184 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Priority | Over Voltage L-L-Alarm Priority | 414080 | UINT32 | R | 160434179 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Delay | Over Voltage L-L-Dropout Delay | 414091 | UINT32 | R | 160434183
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Setpoint | Over Voltage L-L-Dropout Setpoint | 414089 | F32-4321 | R | 160434182
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Delay | Over Voltage L-L-Pickup Delay | 414087 | UINT32 | R | 160434181
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Enabled | Over Voltage L-L-Alarm Enabled | 414080 | UINT32 | RW | 160434178 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Setpoint | Over Voltage L-L-Pickup Setpoint | 414085 | F32-4321 | RW | 160434180
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N Alarm | Over Voltage L-N Alarm | 411021 | MaskedBool | R | 160434433 | 0x0040 | 64
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Output | Over Voltage L-N-Alarm Output | 414133 | UINT16 | R | 160434440 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Priority | Over Voltage L-N-Alarm Priority | 414120 | UINT32 | R | 160434435 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Delay | Over Voltage L-N-Dropout Delay | 414131 | UINT32 | R | 160434439
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Setpoint | Over Voltage L-N-Dropout Setpoint | 414129 | F32-4321 | R | 160434438
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Delay | Over Voltage L-N-Pickup Delay | 414127 | UINT32 | R | 160434437
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Enabled | Over Voltage L-N-Alarm Enabled | 414120 | UINT32 | RW | 160434434 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Setpoint | Over Voltage L-N-Pickup Setpoint | 414125 | F32-4321 | RW | 160434436
|  | Alarms - Over Under | Under Active Power | Under Active Power Alarm | Under Active Power Alarm | 411022 | MaskedBool | R | 160433409 | 0x2000 | 8192
|  | Alarms - Over Under | Under Active Power | Under Active Power-Alarm Output | Under Active Power-Alarm Output | 414833 | UINT16 | R | 160433416 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Active Power | Under Active Power-Alarm Priority | Under Active Power-Alarm Priority | 414820 | UINT32 | R | 160433411 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Active Power | Under Active Power-Dropout Delay | Under Active Power-Dropout Delay | 414831 | UINT32 | R | 160433415
|  | Alarms - Over Under | Under Active Power | Under Active Power-Dropout Setpoint | Under Active Power-Dropout Setpoint | 414829 | F32-4321 | R | 160433414
|  | Alarms - Over Under | Under Active Power | Under Active Power-Pickup Delay | Under Active Power-Pickup Delay | 414827 | UINT32 | R | 160433413
|  | Alarms - Over Under | Under Active Power | Under Active Power-Alarm Enabled | Under Active Power-Alarm Enabled | 414820 | UINT32 | RW | 160433410 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Active Power | Under Active Power-Pickup Setpoint | Under Active Power-Pickup Setpoint | 414825 | F32-4321 | RW | 160433412
|  | Alarms - Over Under | Under Current Phase | Under Current Phase Alarm | Under Current Phase Alarm | 411021 | MaskedBool | R | 160433921 | 0x0002 | 2
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Output | Under Current Phase-Alarm Output | 414033 | UINT16 | R | 160433927 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Priority | Under Current Phase-Alarm Priority | 414020 | UINT32 | R | 160433923 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Delay | Under Current Phase-Dropout Delay | 414031 | UINT32 | R | 160433928
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Setpoint | Under Current Phase-Dropout Setpoint | 414029 | F32-4321 | R | 160433926
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Delay | Under Current Phase-Pickup Delay | 414027 | UINT32 | R | 160433925
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Enabled | Under Current Phase-Alarm Enabled | 414020 | UINT32 | RW | 160433922 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Setpoint | Under Current Phase-Pickup Setpoint | 414025 | F32-4321 | RW | 160433924
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L Alarm | Under Voltage L-L Alarm | 411021 | MaskedBool | R | 160432641 | 0x0020 | 32
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Output | Under Voltage L-L-Alarm Output | 414113 | UINT16 | R | 160432648 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Priority | Under Voltage L-L-Alarm Priority | 414100 | UINT32 | R | 160432643 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Delay | Under Voltage L-L Alarm Dropout Delay | 414111 | UINT32 | R | 160432647
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Setpoint | Under Voltage L-L-Dropout Setpoint | 414109 | F32-4321 | R | 160432646
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Delay | Under Voltage L-L-Pickup Delay | 414107 | UINT32 | R | 160432645
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Enabled | Under Voltage L-L-Alarm Enabled | 414100 | UINT32 | RW | 160432642 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Setpoint | Under Voltage L-L-Pickup Setpoint | 414105 | F32-4321 | RW | 160432644
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N Alarm | Under Voltage L-N Alarm | 411021 | MaskedBool | R | 160432897 | 0x0080 | 128
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Output | Under Voltage L-N-Alarm Output | 414153 | UINT16 | R | 160432904 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Priority | Under Voltage L-N-Alarm Priority | 414140 | UINT32 | R | 160432899 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Delay | Under Voltage L-N-Dropout Delay | 414151 | UINT32 | R | 160432903
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Setpoint | Under Voltage L-N-Dropout Setpoint | 414149 | F32-4321 | R | 160432902
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Delay | Under Voltage L-N-Pickup Delay | 414147 | UINT32 | R | 160432901
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Enabled | Under Voltage L-N-Alarm Enabled | 414140 | UINT32 | RW | 160432898 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Setpoint | Under Voltage L-N-Pickup Setpoint | 414145 | F32-4321 | RW | 160432900
DR1 | 900 | Currents | Current | Current Phase A | Current Phase A | 403000 | F32-4321 | R | 164626433
|  | Currents | Current | Current Phase Average | Current Phase Average | 403010 | F32-4321 | R | 164626439
DR1 | 900 | Currents | Current | Current Phase B | Current Phase B | 403002 | F32-4321 | R | 164626434
DR1 | 900 | Currents | Current | Current Phase C | Current Phase C | 403004 | F32-4321 | R | 164626435
|  | Currents | Current | Neutral Current | Neutral Current | 403006 | F32-4321 | R | 164626436
|  | Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | 403252 | DateTime3_IEC870_LOCAL | R | 169870337
|  | Energies | Energy | Active Energy Delivered | Active Energy Delivered | 403204 | S64-87-21 | R | 169869313 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase A | Active Energy Delivered Phase A | 403518 | S64-87-21 | R | 169869322 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase B | Active Energy Delivered Phase B | 403522 | S64-87-21 | R | 169869323 |  | 1000
|  | Energies | Energy | Active Energy Delivered Phase C | Active Energy Delivered Phase C | 403526 | S64-87-21 | R | 169869324 |  | 1000
|  | Energies | Energy | Active Energy Received | Active Energy Received | 403208 | S64-87-21 | R | 169869314 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered | Apparent Energy Delivered | 403236 | S64-87-21 | R | 169869315 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase A | Apparent Energy Delivered Phase A | 403542 | S64-87-21 | R | 169869325 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase B | Apparent Energy Delivered Phase B | 403546 | S64-87-21 | R | 169869326 |  | 1000
|  | Energies | Energy | Apparent Energy Delivered Phase C | Apparent Energy Delivered Phase C | 403550 | S64-87-21 | R | 169869327 |  | 1000
|  | Energies | Energy | Apparent Energy Received | Apparent Energy Received | 403240 | S64-87-21 | R | 169869318 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered | Reactive Energy Delivered | 403220 | S64-87-21 | R | 169869316 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase A | Reactive Energy Delivered Phase A | 403530 | S64-87-21 | R | 169869319 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase B | Reactive Energy Delivered Phase B | 403534 | S64-87-21 | R | 169869320 |  | 1000
|  | Energies | Energy | Reactive Energy Delivered Phase C | Reactive Energy Delivered Phase C | 403538 | S64-87-21 | R | 169869321 |  | 1000
|  | Energies | Energy | Reactive Energy Received | Reactive Energy Received | 403224 | S64-87-21 | R | 169869317 |  | 1000
|  | Energies | Energy Since Last Reset | Active Energy Delivered Since Last Reset | Active Energy Delivered Since Last Reset | 403256 | S64-87-21 | R | 169869825 |  | 1000
|  | Energies | Energy Since Last Reset | Apparent Energy Delivered Since Last Reset | Apparent Energy Delivered Since Last Reset | 403288 | S64-87-21 | R | 169869827 |  | 1000
|  | Energies | Energy Since Last Reset | Reactive Energy Delivered Since Last Reset | Reactive Energy Delivered Since Last Reset | 403272 | S64-87-21 | R | 169869826 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate A | Active Energy Delivered Rate A | 404196 | S64-87-21 | R | 169870084 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate B | Active Energy Delivered Rate B | 404200 | S64-87-21 | R | 169870085 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate C | Active Energy Delivered Rate C | 404204 | S64-87-21 | R | 169870086 |  | 1000
|  | Energies | Time of Use | Active Energy Delivered Rate D | Active Energy Delivered Rate D | 404208 | S64-87-21 | R | 169870087 |  | 1000
|  | Energies | Time of Use | Time of Use Active Rate | Time of Use Active Rate | 404191 | UINT16 | R | 169870082
|  | Energies | Interval Energy | Active Energy Delivered Interval | Active Energy Delivered Interval | 445605 | S64-87-21 | R | 169869569 |  | 1000
|  | Miscellaneous | DT Last Reset MinMax | DT Last Reset MinMax | DT Last Reset MinMax | 427214 | DateTime3_IEC870_LOCAL | R | 179307265
|  | Miscellaneous | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | 403716 | DateTime3_IEC870_LOCAL | R | 179307777
|  | Miscellaneous | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | 403706 | DateTime3_IEC870_LOCAL | R | 179307521
|  | Miscellaneous | Frequency | Frequency | Frequency | 403110 | F32-4321 | R | 179306497
|  | Miscellaneous | Reactive Factor Total | Reactive Factor Total | Reactive Factor Total | 403108 | F32-4321 | R | 179307009
|  | Miscellaneous | Temperature | Temperature Celsius | Temperature Celsius | 403132 | F32-4321 | R | 179306753
|  | Power Factors | Power Factor A | Power Factor A Load Direction | Power Factor A Load Direction | 403078 | F32-4321 | R | 186646786
|  | Power Factors | Power Factor A | Power Factor Signed Phase A | Power Factor Signed Phase A | 403078 | PF32 | R | 186646785 |  |  | 100
|  | Power Factors | Power Factor B | Power Factor B Load Direction | Power Factor B Load Direction | 403080 | F32-4321 | R | 186647042
|  | Power Factors | Power Factor B | Power Factor Signed Phase B | Power Factor Signed Phase B | 403080 | PF32 | R | 186647041 |  |  | 100
|  | Power Factors | Power Factor C | Power Factor C Load Direction | Power Factor C Load Direction | 403082 | F32-4321 | R | 186647298
|  | Power Factors | Power Factor C | Power Factor Signed Phase C | Power Factor Singed Phase C | 403082 | PF32 | R | 186647297 |  |  | 100
|  | Power Factors | Power Factor Total | Power Factor Signed | Power Factor Signed | 403084 | PF32 | R | 186646532 |  |  | 100
|  | Power Factors | Power Factor Total | Power Factor Total Load Direction | Power Factor Total Load Direction | 403084 | F32-4321 | R | 186646534
|  | Powers | Power | Apparent Power A | Apparent Power A | 403070 | F32-4321 | R | 190840841
|  | Powers | Power | Apparent Power B | Apparent Power B | 403072 | F32-4321 | R | 190840842
|  | Powers | Power | Apparent Power C | Apparent Power C | 403074 | F32-4321 | R | 190840843
DR1 | 900 | Powers | Power | Apparent Power Total | Apparent Power Total | 403076 | F32-4321 | R | 190840844
|  | Powers | Power | Reactive Power A | Reactive Power A | 403062 | F32-4321 | R | 190840837
|  | Powers | Power | Reactive Power B | Reactive Power B | 403064 | F32-4321 | R | 190840838
|  | Powers | Power | Reactive Power C | Reactive Power C | 403066 | F32-4321 | R | 190840839
|  | Powers | Power | Reactive Power Total | Reactive Power Total | 403068 | F32-4321 | R | 190840840
|  | Powers | Power | Real Power A | Real Power A | 403054 | F32-4321 | R | 190840833
|  | Powers | Power | Real Power B | Real Power B | 403056 | F32-4321 | R | 190840834
|  | Powers | Power | Real Power C | Real Power C | 403058 | F32-4321 | R | 190840835
DR1 | 900 | Powers | Power | Real Power Total | Real Power Total | 403060 | F32-4321 | R | 190840836
|  | Voltages | Voltage | Average Voltage Line-to-Line | Average Voltage Line-to-Line | 403026 | F32-4321 | R | 201326596
|  | Voltages | Voltage | Average Voltage Line-to-Neutral | Average Voltage Line-to-Neutral | 403036 | F32-4321 | R | 201326600
|  | Voltages | Voltage | Voltage Phases AB | Voltage Phases AB | 403020 | F32-4321 | R | 201326593
|  | Voltages | Voltage | Voltage Phases AN | Voltage Phases AN | 403028 | F32-4321 | R | 201326597
|  | Voltages | Voltage | Voltage Phases BC | Voltage Phases BC | 403022 | F32-4321 | R | 201326594
|  | Voltages | Voltage | Voltage Phases BN | Voltage Phases BN | 403030 | F32-4321 | R | 201326598
|  | Voltages | Voltage | Voltage Phases CA | Voltage Phases CA | 403024 | F32-4321 | R | 201326595
|  | Voltages | Voltage | Voltage Phases CN | Voltage Phases CN | 403032 | F32-4321 | R | 201326599
|  | Diagnostics | Meter | Calibration Error | Calibration Error | 445000 | MaskedBool | R | 205520898 | 0x0002 | 2
|  | Diagnostics | Meter | Current Reversed | Current Reversed | 445000 | MaskedBool | R | 205520904 | 0x0020 | 32
|  | Diagnostics | Meter | Energy Pulse Overrun | Energy Pulse Overrun | 445000 | MaskedBool | R | 205520899 | 0x0080 | 128
|  | Diagnostics | Meter | Frequency Setting Error | Frequency Setting Error | 445000 | MaskedBool | R | 205520900 | 0x0004 | 4
|  | Diagnostics | Meter | Meter ON Duration | Meter ON Duration | 402004 | UINT32 | R | 205520897 |  | 3600
|  | Diagnostics | Meter | NVRAM Error | NVRAM Error | 445000 | MaskedBool | R | 205520901 | 0x0001
|  | Diagnostics | Meter | Oscillator Error | Oscillator Error | 445000 | MaskedBool | R | 205520902 | 0x0100 | 256
|  | Diagnostics | Meter | Phase Sequence Reversed | Phase Sequence Reversed | 445000 | MaskedBool | R | 205520903 | 0x0010 | 16
|  | Diagnostics | Meter | RTC Error | RTC Error | 445000 | MaskedBool | R | 205520905 | 0x0040 | 64
|  | Diagnostics | Meter | Wiring Error | Wiring Error | 445000 | MaskedBool | R | 205520906 | 0x0008 | 8
|  | Power Meters | Power Meter | PM1 Nominal Frequency | PM1 Nominal Frequency | 402017 | UINT16 | R | 65547
|  | Power Meters | Power Meter | PM1 CT Primary | PM1 CT Primary | 402030 | UINT16 | R | 65550
|  | Power Meters | Power Meter | PM1 CT Secondary | PM1 CT Secondary | 402031 | UINT16 | R | 65551
|  | Power Meters | Power Meter | PM1 Nominal Phase Rotation | PM1 Nominal Phase Rotation | 402024 | UINT16 | R | 65537
|  | Power Meters | Power Meter | PM1 Volts Mode | PM1 Volts Mode | 402016 | UINT16 | R | 30720
|  | Power Meters | Power Meter | PM1 VT Primary | PM1 VT Primary | 402026 | F32-4321 | R | 65548
|  | Power Meters | Power Meter | PM1 VT Secondary | PM1 VT Secondary | 402028 | UINT16 | R | 65549
|  | Unbalances | Current Unbalance | Current Unbalance A | Current Unbalance A | 403012 | F32-4321 | R | 157286401
|  | Unbalances | Current Unbalance | Current Unbalance B | Current Unbalance B | 403014 | F32-4321 | R | 157286402
|  | Unbalances | Current Unbalance | Current Unbalance C | Current Unbalance C | 403016 | F32-4321 | R | 157286403
|  | Unbalances | Current Unbalance | Current Unbalance Worst | Current Unbalance Worst | 403018 | F32-4321 | R | 157286404
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-B | Voltage Unbalance A-B | 403038 | F32-4321 | R | 157286657
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-N | Voltage Unbalance A-N | 403046 | F32-4321 | R | 157286661
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-C | Voltage Unbalance B-C | 403040 | F32-4321 | R | 157286658
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-N | Voltage Unbalance B-N | 403048 | F32-4321 | R | 157286662
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-A | Voltage Unbalance C-A | 403042 | F32-4321 | R | 157286659
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-N | Voltage Unbalance C-N | 403050 | F32-4321 | R | 157286663
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-L Worst | Voltage Unbalance L-L Worst | 403044 | F32-4321 | R | 157286660
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-N Worst | Voltage Unbalance L-N Worst | 403052 | F32-4321 | R | 157286664
|  | Demand Readings and History | Demand Current | Block Demand Current N | Block Demand Current N | 403862 | F32-4321 | R | 159383816
|  | Demand Readings and History | Demand Current | Current Demand Interval | Current Demand Interval | 403712 | UINT16 | R | 159383815
|  | Demand Readings and History | Demand Current | Current Phase A Sliding Window Demand Delivered-Received | Current Phase A Sliding Window Demand Delivered-Received | 403814 | F32-4321 | R | 159383809
|  | Demand Readings and History | Demand Current | Current Phase Average Sliding Window Demand Delivered-Received | Current Phase Average Sliding Window Demand Delivered-Received | 403878 | F32-4321 | R | 159383813
|  | Demand Readings and History | Demand Current | Current Phase B Sliding Window Demand Delivered-Received | Current Phase B Sliding Window Demand Delivered-Received | 403830 | F32-4321 | R | 159383810
|  | Demand Readings and History | Demand Current | Current Phase C Sliding Window Demand Delivered-Received | Current Phase C Sliding Window Demand Delivered-Received | 403846 | F32-4321 | R | 159383811
|  | Demand Readings and History | Demand Current | Current Demand Calculation Method | Current Demand Calculation Method | 403711 | UINT16 | R | 159383814
|  | Demand Readings and History | Demand Power | Active Power Sliding Window Demand Delivered-Received | Active Power Sliding Window Demand Delivered-Received | 403766 | F32-4321 | R | 159384065
|  | Demand Readings and History | Demand Power | Apparent Power Sliding Window Demand Delivered-Received | Apparent Power Sliding Window Demand Delivered-Received | 403798 | F32-4321 | R | 159384067
|  | Demand Readings and History | Demand Power | Power Demand Interval | Power Demand Interval | 403702 | UINT16 | R | 159384069
|  | Demand Readings and History | Demand Power | Reactive Power Sliding Window Demand Delivered - Received | Reactive Power Sliding Window Demand Delivered - Received | 403782 | F32-4321 | R | 159384066
|  | Demand Readings and History | Demand Power | Power Demand Calculation Method | Power Demand Calculation Method | 403701 | UINT16 | R | 159384068
|  | Demand Readings and History | Peak Demand Apparent Power | Apparent Power Sliding Window Demand Delivered-Received Maximum | Apparent Power Sliding Window Demand Delivered-Received Maximum | 403802 | F32-4321 | R | 159385345
|  | Demand Readings and History | Peak Demand Apparent Power | DT Peak Demand Apparent Power | DT Peak Demand Apparent Power | 403804 | DateTime3_IEC870_LOCAL | R | 159385346
|  | Demand Readings and History | Peak Demand Current A | Current Phase A Sliding Window Demand Delivered-Received Maximum | Current Phase A Sliding Window Demand Delivered-Received Maximum | 403818 | F32-4321 | R | 159383553
|  | Demand Readings and History | Peak Demand Current A | DT Peak Demand Current A | DT Peak Demand Current A | 403820 | DateTime3_IEC870_LOCAL | R | 159383554
|  | Demand Readings and History | Peak Demand Current Avg | Current Phase Average Sliding Window Demand Delivered-Received Maximum | Current Phase Average Sliding Window Demand Delivered-Received Maximum | 403882 | F32-4321 | R | 159385857
|  | Demand Readings and History | Peak Demand Current Avg | DT Peak Demand Current Avg | DT Peak Demand Current Avg | 403884 | DateTime3_IEC870_LOCAL | R | 159385858
|  | Demand Readings and History | Peak Demand Current B | Current Phase B Sliding Window Demand Delivered-Received Maximum | Current Phase B Sliding Window Demand Delivered-Received Maximum | 403834 | F32-4321 | R | 159384321
|  | Demand Readings and History | Peak Demand Current B | DT Peak Demand Current B | DT Peak Demand Current B | 403836 | DateTime3_IEC870_LOCAL | R | 159384322
|  | Demand Readings and History | Peak Demand Current C | Current Phase C Sliding Window Demand Delivered-Received Maximum | Current Phase C Sliding Window Demand Delivered-Received Maximum | 403850 | F32-4321 | R | 159384577
|  | Demand Readings and History | Peak Demand Current C | DT Peak Demand Current C | DT Peak Demand Current C | 403852 | DateTime3_IEC870_LOCAL | R | 159384578
|  | Demand Readings and History | Peak Demand Current N | Current Phase N Sliding Window Demand Delivered-Received Maximum | Current Phase N Sliding Window Demand Delivered-Received Maximum | 403866 | F32-4321 | R | 159385601
|  | Demand Readings and History | Peak Demand Current N | DT Peak Demand Current N | DT Peak Demand Current N | 403868 | DateTime3_IEC870_LOCAL | R | 159385602
|  | Demand Readings and History | Peak Demand Reactive Power | DT Peak Demand Reactive Power | DT Peak Demand Reactive Power | 403788 | DateTime3_IEC870_LOCAL | R | 159385090
|  | Demand Readings and History | Peak Demand Reactive Power | Reactive Power Sliding Window Demand Delivered - Received Maximum | Reactive Power Sliding Window Demand Delivered - Received Maximum | 403786 | F32-4321 | R | 159385089
|  | Demand Readings and History | Peak Demand Real Power | Active Power Sliding Window Demand Delivered-Received Maximum | Active Power Sliding Window Demand Delivered-Received Maximum | 403770 | F32-4321 | R | 159384833
|  | Demand Readings and History | Peak Demand Real Power | DT Peak Demand Real Power | DT Peak Demand Real Power | 403772 | DateTime3_IEC870_LOCAL | R | 159384834
|  | Power Quality | THD Current | Current Total Harmonic Distortion Neutral | Current Total Harmonic Distortion Neutral | 421306 | F32-4321 | R | 161480708
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase A | Current Total Harmonic Distortion Phase A | 421300 | F32-4321 | R | 161480705
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase B | Current Total Harmonic Distortion Phase B | 421302 | F32-4321 | R | 161480706
|  | Power Quality | THD Current | Current Total Harmonic Distortion Phase C | Current Total Harmonic Distortion Phase C | 421304 | F32-4321 | R | 161480707
|  | Power Quality | THD Current | Current Total Harmonic Distortion Worst | Current Total Harmonic Distortion Worst | 445108 | F32-4321 | R | 161480709
|  | Power Quality | THD Voltage | THD Voltage A-B | THD Voltage A-B | 421322 | F32-4321 | R | 161480961
|  | Power Quality | THD Voltage | THD Voltage A-N | THD Voltage A-N | 421330 | F32-4321 | R | 161480965
|  | Power Quality | THD Voltage | THD Voltage B-C | THD Voltage B-C | 421324 | F32-4321 | R | 161480962
|  | Power Quality | THD Voltage | THD Voltage B-N | THD Voltage B-N | 421332 | F32-4321 | R | 161480966
|  | Power Quality | THD Voltage | THD Voltage C-A | THD Voltage C-A | 421326 | F32-4321 | R | 161480963
|  | Power Quality | THD Voltage | THD Voltage C-N | THD Voltage C-N | 421334 | F32-4321 | R | 161480967
|  | Power Quality | THD Voltage | THD Voltage L-L | THD Voltage L-L | 421328 | F32-4321 | R | 161480964
|  | Power Quality | THD Voltage | THD Voltage L-L Worst | THD Voltage L-L Worst | 445118 | F32-4321 | R | 161480969
|  | Power Quality | THD Voltage | THD Voltage L-N | THD Voltage L-N | 421338 | F32-4321 | R | 161480968
|  | Power Quality | THD Voltage | THD Voltage L-N Worst | THD Voltage L-N Worst | 445128 | F32-4321 | R | 161480970
|  | Minimum Readings | Min Current | Current Phase A Minimum | Current Phase A Minimum | 427218 | F32-4321 | R | 162529281
|  | Minimum Readings | Min Current | Current Phase Average Minimum | Current Phase Average Minimum | 427228 | F32-4321 | R | 162529285
|  | Minimum Readings | Min Current | Current Phase B Minimum | Current Phase B Minimum | 427220 | F32-4321 | R | 162529282
|  | Minimum Readings | Min Current | Current Phase C Minimum | Current Phase C Minimum | 427222 | F32-4321 | R | 162529283
|  | Minimum Readings | Min Current | Min Current | Min Current | 445134 | F32-4321 | R | 162529286
|  | Minimum Readings | Min Current | Neutral Current Minimum | Neutral Current Minimum | 427224 | F32-4321 | R | 162529284
|  | Minimum Readings | Min Frequency | Frequency Minimum | Frequency Minimum | 427616 | F32-4321 | R | 162531585
|  | Minimum Readings | Min Power | Active Power Minimum | Active Power Minimum | 427278 | F32-4321 | R | 162530052
|  | Minimum Readings | Min Power | Active Power Phase A Minimum | Active Power Phase A Minimum | 427272 | F32-4321 | R | 162530049
|  | Minimum Readings | Min Power | Active Power Phase B Minimum | Active Power Phase B Minimum | 427274 | F32-4321 | R | 162530050
|  | Minimum Readings | Min Power | Active Power Phase C Minimum | Active Power Phase C Minimum | 427276 | F32-4321 | R | 162530051
|  | Minimum Readings | Min Power | Apparent Power Minimum | Apparent Power Minimum | 427294 | F32-4321 | R | 162530060
|  | Minimum Readings | Min Power | Apparent Power Phase A Minimum | Apparent Power Phase A Minimum | 427288 | F32-4321 | R | 162530057
|  | Minimum Readings | Min Power | Apparent Power Phase B Minimum | Apparent Power Phase B Minimum | 427290 | F32-4321 | R | 162530058
|  | Minimum Readings | Min Power | Apparent Power Phase C Minimum | Apparent Power Phase C Minimum | 427292 | F32-4321 | R | 162530059
|  | Minimum Readings | Min Power | Reactive Power Minimum | Reactive Power Minimum | 427286 | F32-4321 | R | 162530056
|  | Minimum Readings | Min Power | Reactive Power Phase A Minimum | Reactive Power Phase A Minimum | 427280 | F32-4321 | R | 162530053
|  | Minimum Readings | Min Power | Reactive Power Phase B Minimum | Reactive Power Phase B Minimum | 427282 | F32-4321 | R | 162530054
|  | Minimum Readings | Min Power | Reactive Power Phase C Minimum | Reactive Power Phase C Minimum | 427284 | F32-4321 | R | 162530055
|  | Minimum Readings | Min Power Factor A | Min Power Factor A | Min Power Factor A | 427306 | PF32 | R | 162530305 |  |  | 100
|  | Minimum Readings | Min Power Factor A | Min Power Factor A Load Direction | Min Power Factor A Load Direction | 427306 | F32-4321 | R | 162530306
|  | Minimum Readings | Min Power Factor B | Min Power Factor B | Min Power Factor B | 427308 | PF32 | R | 162530561 |  |  | 100
|  | Minimum Readings | Min Power Factor B | Min Power Factor B Load Direction | Min Power Factor B Load Direction | 427308 | F32-4321 | R | 162530562
|  | Minimum Readings | Min Power Factor C | Min Power Factor C | Min Power Factor C | 427310 | PF32 | R | 162530817 |  |  | 100
|  | Minimum Readings | Min Power Factor C | Min Power Factor C Load Direction | Min Power Factor C Load Direction | 427310 | F32-4321 | R | 162530818
|  | Minimum Readings | Min Power Factor Total | Min Power Factor | Min Power Factor | 427312 | PF32 | R | 162531073 |  |  | 100
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total Load Direction | Min Power Factor Total Load Direction | 427312 | F32-4321 | R | 162531074
|  | Minimum Readings | Min Reactive Factor Total | Min Reactive Factor Total | Min Reactive Factor Total | 427336 | F32-4321 | R | 162531329
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase A Minimum | Current Total Harmonic Distortion Phase A Minimum | 427338 | F32-4321 | R | 162529537
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase B Minimum | Current Total Harmonic Distortion Phase B Minimum | 427340 | F32-4321 | R | 162529538
|  | Minimum Readings | Min THD Current | Current Total Harmonic Distortion Phase C Minimum | Current Total Harmonic Distortion Phase C Minimum | 427342 | F32-4321 | R | 162529539
|  | Minimum Readings | Min THD Current | Min THD Current N | Min THD Current N | 427344 | F32-4321 | R | 162529540
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-L | Min THD Voltage L-L | 427366 | F32-4321 | R | 162531847
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-N | Min THD Voltage L-N | 427376 | F32-4321 | R | 162531848
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Minimum | 427368 | F32-4321 | R | 162531844
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Minimum | 427370 | F32-4321 | R | 162531845
|  | Minimum Readings | Min THD Voltage | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Minimum | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Minimum | 427372 | F32-4321 | R | 162531846
|  | Minimum Readings | Min THD Voltage | Voltage Phases AB Total Harmonic Distortion Minimum | Voltage Phases AB Total Harmonic Distortion Minimum | 427360 | F32-4321 | R | 162531841
|  | Minimum Readings | Min THD Voltage | Voltage Phases BC Total Harmonic Distortion Minimum | Voltage Phases BC Total Harmonic Distortion Minimum | 427362 | F32-4321 | R | 162531842
|  | Minimum Readings | Min THD Voltage | Voltage Phases CA Total Harmonic Distortion Minimum | Voltage Phases CA Total Harmonic Distortion Minimum | 427364 | F32-4321 | R | 162531843
|  | Minimum Readings | Min Voltage | Average Voltage Line-to-Line Minimum | Average Voltage Line-to-Line Minimum | 427244 | F32-4321 | R | 162529799
|  | Minimum Readings | Min Voltage | Average Voltage Line-to-Neutral Minimum | Average Voltage Line-to-Neutral Minimum | 427254 | F32-4321 | R | 162529800
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase A Minimum | Voltage Line-to-Neutral Phase A Minimum | 427246 | F32-4321 | R | 162529796
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase B Minimum | Voltage Line-to-Neutral Phase B Minimum | 427248 | F32-4321 | R | 162529797
|  | Minimum Readings | Min Voltage | Voltage Line-to-Neutral Phase C Minimum | Voltage Line-to-Neutral Phase C Minimum | 427250 | F32-4321 | R | 162529798
|  | Minimum Readings | Min Voltage | Voltage Phases AB Minimum | Voltage Phases AB Minimum | 427238 | F32-4321 | R | 162529793
|  | Minimum Readings | Min Voltage | Voltage Phases BC Minimum | Voltage Phases BC Minimum | 427240 | F32-4321 | R | 162529794
|  | Minimum Readings | Min Voltage | Voltage Phases CA Minimum | Voltage Phases CA Minimum | 427242 | F32-4321 | R | 162529795
|  | Minimum Readings | Minimum Readings Date Time | Min Current Date Time | Min Current Date Time | 445130 | DateTime3_IEC870_LOCAL | R | 162532097
|  | Minimum Readings | Minimum Readings Date Time | Min Power Factor Date Time | Min Power Factor Date Time | 445136 | DateTime3_IEC870_LOCAL | R | 162532098
|  | Maximum Readings | Max Current | Average Current Maximum | Average Current Maximum | 427704 | F32-4321 | R | 163577861
|  | Maximum Readings | Max Current | Current Phase A Maximum | Current Phase A Maximum | 427694 | F32-4321 | R | 163577857
|  | Maximum Readings | Max Current | Current Phase B Maximum | Current Phase B Maximum | 427696 | F32-4321 | R | 163577858
|  | Maximum Readings | Max Current | Current Phase C Maximum | Current Phase C Maximum | 427698 | F32-4321 | R | 163577859
|  | Maximum Readings | Max Current | Max Current | Max Current | 445146 | F32-4321 | R | 163577862
|  | Maximum Readings | Max Current | Neutral Current Maximum | Neutral Current Maximum | 427700 | F32-4321 | R | 163577860
|  | Maximum Readings | Max Frequency | Frequency Maximum | Frequency Maximum | 428092 | F32-4321 | R | 163580161
|  | Maximum Readings | Max Power | Active Power Maximum | Active Power Maximum | 427754 | F32-4321 | R | 163578628
|  | Maximum Readings | Max Power | Active Power Phase A Maximum | Active Power Phase A Maximum | 427748 | F32-4321 | R | 163578625
|  | Maximum Readings | Max Power | Active Power Phase B Maximum | Active Power Phase B Maximum | 427750 | F32-4321 | R | 163578626
|  | Maximum Readings | Max Power | Active Power Phase C Maximum | Active Power Phase C Maximum | 427752 | F32-4321 | R | 163578627
|  | Maximum Readings | Max Power | Apparent Power Maximum | Apparent Power Maximum | 427770 | F32-4321 | R | 163578636
|  | Maximum Readings | Max Power | Apparent Power Phase A Maximum | Apparent Power Phase A Maximum | 427764 | F32-4321 | R | 163578633
|  | Maximum Readings | Max Power | Apparent Power Phase B Maximum | Apparent Power Phase B Maximum | 427766 | F32-4321 | R | 163578634
|  | Maximum Readings | Max Power | Apparent Power Phase C Maximum | Apparent Power Phase C Maximum | 427768 | F32-4321 | R | 163578635
|  | Maximum Readings | Max Power | Reactive Power Maximum | Reactive Power Maximum | 427762 | F32-4321 | R | 163578632
|  | Maximum Readings | Max Power | Reactive Power Phase A Maximum | Reactive Power Phase A Maximum | 427756 | F32-4321 | R | 163578629
|  | Maximum Readings | Max Power | Reactive Power Phase B Maximum | Reactive Power Phase B Maximum | 427758 | F32-4321 | R | 163578630
|  | Maximum Readings | Max Power | Reactive Power Phase C Maximum | Reactive Power Phase C Maximum | 427760 | F32-4321 | R | 163578631
|  | Maximum Readings | Max Power Factor A | Max Power Factor A | Max Power Factor A | 427782 | PF32 | R | 163578881 |  |  | 100
|  | Maximum Readings | Max Power Factor A | Max Power Factor A Load Direction | Max Power Factor A Load Direction | 427782 | F32-4321 | R | 163578882
|  | Maximum Readings | Max Power Factor B | Max Power Factor B | Max Power Factor B | 427784 | PF32 | R | 163579137 |  |  | 100
|  | Maximum Readings | Max Power Factor B | Max Power Factor B Load Direction | Max Power Factor B Load Direction | 427784 | F32-4321 | R | 163579138
|  | Maximum Readings | Max Power Factor C | Max Power Factor C | Max Power Factor C | 427786 | PF32 | R | 163579393 |  |  | 100
|  | Maximum Readings | Max Power Factor C | Max Power Factor C Load Direction | Max Power Factor C Load Direction | 427786 | F32-4321 | R | 163579394
|  | Maximum Readings | Max Power Factor Total | Max Power Factor | Max Power Factor | 427788 | PF32 | R | 163579649 |  |  | 100
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total Load Direction | Max Power Factor Total Load Direction | 427788 | F32-4321 | R | 163579650
|  | Maximum Readings | Max Reactive Factor Total | Max Reactive Factor Total | Max Reactive Factor Total | 427812 | F32-4321 | R | 163579905
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase A Maximum | Current Total Harmonic Distortion Phase A Maximum | 427814 | F32-4321 | R | 163578113
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase B Maximum | Current Total Harmonic Distortion Phase B Maximum | 427816 | F32-4321 | R | 163578114
|  | Maximum Readings | Max THD Current | Current Total Harmonic Distortion Phase C Maximum | Current Total Harmonic Distortion Phase C Maximum | 427818 | F32-4321 | R | 163578115
|  | Maximum Readings | Max THD Current | Max THD Current N | Max THD Current N | 427820 | F32-4321 | R | 163578116
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-L | Max THD Voltage L-L | 427842 | F32-4321 | R | 163580422
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-N | Max THD Voltage L-N | 427852 | F32-4321 | R | 163580423
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase A Total Harmonic Distortion Maximum | 427844 | F32-4321 | R | 163580420
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase B Total Harmonic Distortion Maximum | 427846 | F32-4321 | R | 163580421
|  | Maximum Readings | Max THD Voltage | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Maximum | Voltage Line-to-Neutral Phase C Total Harmonic Distortion Maximum | 427848 | F32-4321 | R | 163580424
|  | Maximum Readings | Max THD Voltage | Voltage Phases AB Total Harmonic Distortion Maximum | Voltage Phases AB Total Harmonic Distortion Maximum | 427836 | F32-4321 | R | 163580417
|  | Maximum Readings | Max THD Voltage | Voltage Phases BC Total Harmonic Distortion Maximum | Voltage Phases BC Total Harmonic Distortion Maximum | 427838 | F32-4321 | R | 163580418
|  | Maximum Readings | Max THD Voltage | Voltage Phases CA Total Harmonic Distortion Maximum | Voltage Phases CA Total Harmonic Distortion Maximum | 427840 | F32-4321 | R | 163580419
|  | Maximum Readings | Max Voltage | Average Voltage Line-to-Line Maximum | Average Voltage Line-to-Line Maximum | 427720 | F32-4321 | R | 163578375
|  | Maximum Readings | Max Voltage | Average Voltage Line-to-Neutral Maximum | Average Voltage Line-to-Neutral Maximum | 427730 | F32-4321 | R | 163578376
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase A Maximum | Voltage Line-to-Neutral Phase A Maximum | 427722 | F32-4321 | R | 163578372
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase B Maximum | Voltage Line-to-Neutral Phase B Maximum | 427724 | F32-4321 | R | 163578373
|  | Maximum Readings | Max Voltage | Voltage Line-to-Neutral Phase C Maximum | Voltage Line-to-Neutral Phase C Maximum | 427726 | F32-4321 | R | 163578374
|  | Maximum Readings | Max Voltage | Voltage Phases AB Maximum | Voltage Phases AB Maximum | 427714 | F32-4321 | R | 163578369
|  | Maximum Readings | Max Voltage | Voltage Phases BC Maximum | Voltage Phases BC Maximum | 427716 | F32-4321 | R | 163578370
|  | Maximum Readings | Max Voltage | Voltage Phases CA Maximum | Voltage Phases CA Maximum | 427718 | F32-4321 | R | 163578371
|  | Maximum Readings | Maximum Readings Date Time | Max Apparent Power Total Date Time | Max Apparent Power Total Date Time | 445154 | DateTime3_IEC870_LOCAL | R | 163580674
|  | Maximum Readings | Maximum Readings Date Time | Max Power Factor Date Time | Max Power Factor Date Time | 445160 | DateTime3_IEC870_LOCAL | R | 163580675
|  | Maximum Readings | Maximum Readings Date Time | Max Real Power Total Date Time | Max Real Power Total Date Time | 445148 | DateTime3_IEC870_LOCAL | R | 163580673
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Trigger |  |  |  |  | 165675011
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Period |  |  |  |  | 165675009
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Sync Mode |  |  |  |  | 165675010
|  | Labels | Alarm Labels | Over Current Alarm |  |  |  |  | 14000
|  | Labels | Alarm Labels | Under Current Alarm |  |  |  |  | 14020
|  | Labels | Alarm Labels | Over Voltage L-L Alarm |  |  |  |  | 14080
|  | Labels | Alarm Labels | Under Voltage L-L Alarm |  |  |  |  | 14100
|  | Labels | Alarm Labels | Over Voltage L-N Alarm |  |  |  |  | 14120
|  | Labels | Alarm Labels | Under Voltage L-N Alarm |  |  |  |  | 14140
|  | Labels | Alarm Labels | Over Active Power Alarm |  |  |  |  | 14160
|  | Labels | Alarm Labels | Over Reactive Power Alarm |  |  |  |  | 14180
|  | Labels | Alarm Labels | Over Apparent Power Alarm |  |  |  |  | 14200
|  | Labels | Alarm Labels | Leading Power Factor Alarm |  |  |  |  | 14220
|  | Labels | Alarm Labels | Lagging Power Factor Alarm |  |  |  |  | 14240
|  | Labels | Alarm Labels | Over Demand Active Power Present Alarm |  |  |  |  | 14300
|  | Labels | Alarm Labels | Over Demand Apparent Power Present Alarm |  |  |  |  | 14420
|  | Labels | Alarm Labels | Over THD Voltage Alarm |  |  |  |  | 14540
|  | Labels | Alarm Labels | Under Active Power Alarm |  |  |  |  | 14820
|  | Labels | Alarm Labels | Over THD Current Alarm |  |  |  |  | 14860
|  | Labels | Alarm Labels | Over THD Voltage L-N Alarm |  |  |  |  | 14900
|  | Labels | Alarm Labels | Over Active Energy Alarm |  |  |  |  | 14940
|  | Labels | Alarm Labels | [5 empty] | 2543
|  | Labels | Alarm Labels | Phase A |  |  |  |  | 2544
|  | Labels | Alarm Labels | Phase B |  |  |  |  | 2545
|  | Labels | Alarm Labels | Phase C |  |  |  |  | 2546
|  | Labels | Alarm Labels | Phases A and B |  |  |  |  | 2547
|  | Labels | Alarm Labels | Phases B and C |  |  |  |  | 2548
|  | Labels | Alarm Labels | Phases A and C |  |  |  |  | 2549
|  | Labels | Alarm Labels | Phases A, B and C |  |  |  |  | 2550
|  | Labels | Alarm Labels | Neutral |  |  |  |  | 2551
|  | Labels | Alarm Labels | Earth |  |  |  |  | 2552
|  | Labels | Alarm Labels | Neutral-Earth |  |  |  |  | 2553
|  | Labels | Alarm Labels | Phase A-B |  |  |  |  | 2564
|  | Labels | Alarm Labels | Phase B-C |  |  |  |  | 2565
|  | Labels | Alarm Labels | Phase C-A |  |  |  |  | 2566
|  | Labels | Alarm Labels | Phases A-B and B-C |  |  |  |  | 2567
|  | Labels | Alarm Labels | Phases B-C and C-A |  |  |  |  | 2568
|  | Labels | Alarm Labels | Phases A-B and C-A |  |  |  |  | 2569
|  | Labels | Alarm Labels | Phases A-B, B-C and C-A |  |  |  |  | 2570
|  | Labels | Alarm Labels | Phase A-N |  |  |  |  | 2584
|  | Labels | Alarm Labels | Phase B-N |  |  |  |  | 2585
|  | Labels | Alarm Labels | Phase C-N |  |  |  |  | 2586
|  | Labels | Alarm Labels | Phases A-N and B-N |  |  |  |  | 2587
|  | Labels | Alarm Labels | Phases B-N and C-N |  |  |  |  | 2588
|  | Labels | Alarm Labels | Phases A-N and C-N |  |  |  |  | 2589
|  | Labels | Alarm Labels | Phases A-N, B-N and C-N |  |  |  |  | 2590
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  |  |  |  | 166723585
|  | DataRecorder Modules | Data Rec 1 | RE1 Data Log |  |  |  |  | 167772161
|  | DataRecorder Modules | Data Rec 1 | RE1 Log State |  |  |  |  | 167772162
|  | DataRecorder Modules | Data Rec 1 | RE1 Records Left |  |  |  |  | 167772163
|  | DataRecorder Modules | Data Rec 1 | RE1 Record Complete |  |  |  |  | 167772164
|  | DataRecorder Modules | Data Rec 1 | RE1 Depth |  |  |  |  | 167772165
|  | DataRecorder Modules | Data Rec 1 | RE1 RecordMode |  |  |  |  | 167772166
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Threshold |  |  |  |  | 167772167
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Action |  |  |  |  | 167772168
|  | DataRecorder Modules | Data Rec 2 | RE2 Data Log |  |  |  |  | 167772417
|  | DataRecorder Modules | Data Rec 2 | RE2 Log State |  |  |  |  | 167772419
|  | DataRecorder Modules | Data Rec 2 | RE2 Record Complete |  |  |  |  | 167772420
|  | DataRecorder Modules | Data Rec 2 | RE2 Records Left |  |  |  |  | 167772422
|  | DataRecorder Modules | Data Rec 2 | RE2 Fully Uploaded |  |  |  |  | 167772423
|  | DataRecorder Modules | Data Rec 2 | RE2 Enabled | RE2 Enabled | 445402 | UINT16 | R | 167772424 |  |  |  | LogEnable
|  | DataRecorder Modules | Data Rec 2 | RE2 Depth |  |  |  |  | 167772418
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Threshold |  |  |  |  | 167772425
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Action |  |  |  |  | 167772426
|  | DataRecorder Modules | Data Rec 2 | RE2 RecordMode |  |  |  |  | 167772421
|  | DataRecorder Modules | Data Rec 2 | RE2 Jitter Rounding |  |  |  |  | 167772427
|  | DataRecorder Modules | Data Rec 3 | RE3 Data Log |  |  |  |  | 167772673
|  | DataRecorder Modules | Data Rec 3 | RE3 Record Complete |  |  |  |  | 167772676
|  | DataRecorder Modules | Data Rec 3 | RE3 Log State |  |  |  |  | 167772675
|  | DataRecorder Modules | Data Rec 3 | RE3 Records Left |  |  |  |  | 167772678
|  | DataRecorder Modules | Data Rec 3 | RE3 Fully Uploaded |  |  |  |  | 167772679
|  | DataRecorder Modules | Data Rec 3 | RE3 Enabled | RE3 Enabled | 445422 | UINT16 | R | 167772680 |  |  |  | LogEnable
|  | DataRecorder Modules | Data Rec 3 | RE3 Depth |  |  |  |  | 167772674
|  | DataRecorder Modules | Data Rec 3 | RE3 Staleness Threshold |  |  |  |  | 167772681
|  | DataRecorder Modules | Data Rec 3 | RE3 Staleness Action |  |  |  |  | 167772682
|  | DataRecorder Modules | Data Rec 3 | RE3 RecordMode |  |  |  |  | 167772677
|  | DataRecorder Modules | Data Rec 3 | RE3 Jitter Rounding |  |  |  |  | 167772683
|  | Digital Input Output | Digital Input 1 | DI1 Status | Digital Input 1 | 408905 | UINT32 | R | 168821505 | 0x00000001
|  | Digital Input Output | Digital Input 1 | DI1 Control Mode | DI1 Control Mode | 407274 | UINT16 | R | 168821506
|  | Digital Input Output | Digital Input 2 | DI2 Control Mode | DI2 Control Mode | 407298 | UINT16 | R | 168821761
|  | Digital Input Output | Digital Input 2 | DI2 Status | Digital Input 2 | 408905 | UINT32 | R | 168821762 | 0x00000002 | 2
|  | Digital Input Output | Digital Output 1 | DO1 Status | Digital Output 1 | 409667 | MaskedBool | R | 168822018 | 0x0001
|  | Digital Input Output | Digital Output 1 | DO1 Control Mode | DO1 Control Mode | 409673 | UINT16 | R | 168822017
|  | Digital Input Output | Digital Output 2 | DO2 Status | Digital Output 2 | 409667 | MaskedBool | R | 168822274 | 0x0002 | 2
|  | Digital Input Output | Digital Output 2 | DO2 Control Mode | DO2 Control Mode | 409681 | UINT16 | R | 168822273
|  | Digital Input Output | Energy Pulse Duration | Energy Pulse Duration | Energy Pulse Duration | 402129 | UINT16 | R | 168820737
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Digital Output Association | EPO1 Digital Output Association | 402131 | UINT16 | R | 168820993
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Pulse Weight | EPO1 Pulse Weight | 402132 | F32-4321 | R | 168820994
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Digital Output Association | EPO2 Digital Output Association | 402135 | UINT16 | R | 168821249
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Pulse Weight | EPO2 Pulse Weight | 402136 | F32-4321 | R | 168821250
|  | Input Metering | DT Last Reset Input Metering | DT Last Reset Input Metering | DT Last Reset Input Metering | 403554 | DateTime3_IEC870_LOCAL | R | 170917889
DR1 | 900 | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage | WAGES External Input 1 Cumulative Usage | 403558 | S64-87-21 | R | 170918145
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Digital Input Association | WAGES External Input 1 Digital Input Association | 407055 | UINT16 | R | 170918148
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Label | WAGES External Input 1 Label | 407032 | ASCII | R | 170918146 |  |  |  |  | 20
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Pulse Weight | WAGES External Input 1 Pulse Weight | 407052 | F32-4321 | R | 170918147
DR1 | 900 | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage | WAGES External Input 2 Cumulative Usage | 403562 | S64-87-21 | R | 170918401
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Digital Input Association | WAGES External Input 2 Digital Input Association | 407079 | UINT16 | R | 170918404
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Label | WAGES External Input 2 Label | 407056 | ASCII | R | 170918402 |  |  |  |  | 20
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Pulse Weight | WAGES External Input 2 Pulse Weight | 407076 | F32-4321 | R | 170918403