## Sheet1
Power Quality - Sag/Swell module configuration
Nominal voltage | 240
Swell limit % | 110
Sag limit % | 90
ChangeCrit | 10
Hysteresis % | 2
Your Meter will… | [in Volts] | [in percentages]
Record a sag when voltage falls below | 216 | 90
Record a swell when voltage is over | 264 | 110
Consider a new sub-disturbance when voltage falls below | 192 | 80
Consider a new sub-disturbance when voltage is over | 288 | 120
however it will…
Consider a sag over when voltage is over | 220.8 | 92
Consider a swell over when voltage falls below | 259.2 | 108