Answer:

How to configure the RM22UA33MR product to monitor overvoltage 300V and undervoltage 230V?

Vn

= [(Overvoltage – Undervoltage) / 2 ] + Undervoltage

= [(300V – 230V) / 2 ] + 230V

= 265V

To set U value (%)

= (Nominal Voltage / Full range Voltage) x 100%

= 265V / 300V x 100

= 88.33%

Next step, how to configure Overvoltage = 300V and Undervoltage = 230V?

Configure operating mode to >U>, No memory.

Note:

Please note that the RM22 product is not a precision measurement device.