
Exec Upgrade Procedure  (4/7/06)

	Step
	Action

	1.
	From an MS-DOS prompt, create a working directory (example: upgrade) on your computer to perform the upgrade.  For example:
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D:\>nkdir upgrade

D:\>cd upgrade
[D:\UPGRADE>_






	2.
	Copy the STBNIP2212exec2_1_3.zip file acquired from Schneider Electric into the directory just created.    There will be two files when it is unzipped.  

1. upgrade.exe

2. FBC000.bin



	3.
	Exec Upgrade

To perform the upgrade, you will need the IP address of your STB NIP 2212.  To install the new Executive, enter the following command at your DOS prompt:

Upgrade {IP Address}  –e FBC000.bin
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uarning: Active 1/0.
1f you choose to continue with this upgrade procedure, 1/0’s may be active.

[RECOMMENDATION: Set 1/0’s to their fallback or reset state.
[select one of the folloying options:
2. Using the Advantys Configuration Tool, set the 1/0’s to reset state or,

[>] Stop the Modbus Client (if any> that is weiting to the STB NIP 2212.
Wait until the output 1/0 modules are set to their fallback state.

[Press *y’ to continue or to abort this upgrade procedure=>.






	4.
	After hitting <enter> a ‘Warning: Active I/O’ will appear.  This warns the user that if a Modbus client is currently communicating to the I/O, the I/O will remain active and operational throughout the download of the Exec.  Entering ‘y’ continues this procedure, ‘n’ will abort it.  Upon successful completion of the Exec. download, the STB NIP 2212 will be automatically re-booted with the new executive and the I/O will go to its fallback state.  If there are no communications to the Island from a Modbus client, the Exec. can be downloaded.
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[D:\UPGRADE>_




Depending on the NIM configuration and switch settings, it may be necessary to re-assign the IP address after the NIM reboots.

	5.
	When the STB NIP 2212 has completed its reboot, go to the Ethernet NIMs “Properties” Web page and verify that the Exec. version is 2.1.3 or at the version that was installed.  
If so, the upgrade has been successfully completed.




