## Sheet1
Integral | TeSys U replacement | Description Integral | Description TeSys U
LA1LB001 | LUB12 or LUB32 Auxiliary contact (13,14) | Auxiliary 1 CONTACT | 1 NO contact Integrated in the LUB12 or LUB32 terminals ( 13 14 )
LA1LB015 | LUFN20 +LUA1C20 | 3 contacts poles status, 2 contact trips | LUFN20 : 2 NO contacts poles status, 1NO 1NC contact trips
LA1LB017 | LUFN20 +LUA1C20 | 2 contacts poles status, 1 contact trips | LUFN20 : 2 NO contacts poles status, 1NO 1NC contact trips
LA1LB019 | LUFN20 +LUA1C20 | 2 contacts poles status, 1 contact trips | LUFN20 : 2 NO contacts poles status, 1NO 1NC contact trips
LA1LB021 | LUFN20 +LUA1C20 or LUA1C11 | 3 contacts poles status, 2 NO contact trips | LUFN20 : 2 NO contacts poles status, contact trips
LA1LB0211 | LUFN20 +LUA1C20 or LUA1C12 | 3 contacts poles status, 1 NO + 1NC contacts trips | LUFN20 : 2 NO contacts poles status, contact trips
LA1LB031 | LUA1C20+LUA8E20 | 2 Auxiliary : handle position 2NO | 2 contacts handle trip position + 2 NO ON/OFF handle position
LA1LB0311 | LUA1C20 or LUA1C11 | 2 Auxiliary : handle position 1NO + 1NC | 2 contacts handle trip position
LA1LB034 | LUA1C20+LUA8E20 | 4 Auxiliary : handle position 2NO + Trip NC 1NO | 2 contacts handle trip position + 2 NO ON/OFF handle position
LA1LB0341 | LUA1C11+LUA8E20 | 4 Auxiliary : handle position NO 1 NC + Trip NC 1NO | 2 contacts handle trip position + 2 NO ON/OFF handle position
LB1LB03P02 | LUCAX6.. | protection module LB1LB 0.16 to 0.25 A 3P 3d Id = 3.75 A | Control Unit standard 0,16 … 0,6 (Control voltage to be added)
LB1LB03P03 | LUCAX6.. | protection module LB1LB 0.25 to 0.4 A 3P 3d Id = 6 A | Control Unit standard 0,16 … 0,6 (Control voltage to be added)
LB1LB03P04 | LUCA1X.. | protection module LB1LB 0.4 to 0.63 A 3P 3d Id = 9.45 A | Control Unit standard 0,35 … 1,4 (Control voltage to be added)
LB1LB03P05 | LUCA1X.. | protection module LB1LB 0.63 to 1 A 3P 3d Id = 15 A | Control Unit standard 0,35 … 1,4 (Control voltage to be added)
LB1LB03P06 | LUCA1X.. | protection module LB1LB 1 to 1.6 A 3P 3d Id = 24 A | Control Unit standard 0,35 … 1,4 (Control voltage to be added)
LB1LB03P07 | LUCA05.. | protection module LB1LB 1.6 to 2.5 A 3P 3d Id = 37.5 A | Control Unit standard 1,25…5 (Control voltage to be added)
LB1LB03P08 | LUCA05.. | protection module LB1LB 2.5 to 4 A 3P 3d Id = 60 A | Control Unit standard 1,25…5 (Control voltage to be added)
LB1LB03P10 | LUCA12.. | protection module LB1LB 4 to 6 A 3P 3d Id = 90 A | Control Unit standard 3…12 (Control voltage to be added)
LB1LB03P13 | LUCA12.. | protection module LB1LB 6 to 10 A 3P 3d Id = 150 A | Control Unit standard 3…12 (Control voltage to be added)
LB1LB03P17 | LUCA18.. | protection module LB1LB 10 to 16 A 3P 3d Id = 240 A | Control Unit standard 4,5…18 (Control voltage to be added)
LB1LB03P21 | LUCA18.. | protection module LB1LB 12 to 18 A 3P 3d Id = 270 A | Control Unit standard 4,5…18 (Control voltage to be added)
LB6LC03M03 | LUCL6X.. | INTGERAL 32 MAGNETIC MODULE 2,4 ...4,8 | TeSys U MAGNETIC MODULE 2,13 …7,8
LB6LC03M04 | LUCL6X.. | INTGERAL 32MAGNETIC MODULE 3,8...7,6 | TeSys U MAGNETIC MODULE 2,13 …7,8
LB6LC03M06 | LUCL1X.. | INTGERAL 32MAGNETIC MODULE 9,5...19 | TeSys U MAGNETIC MODULE 4,97...18,2
LB6LC03M07 | LUCL1X.. Or LUCL05.. | INTGERAL 32MAGNETIC MODULE 15...30 | TeSys U MAGNETIC MODULE 4,97...18,3 OR 17,75…65
LB6LC03M08 | LUCL05.. | INTGERAL 32MAGNETIC MODULE 24...48 | TeSys U MAGNETIC MODULE 17,75…65
LB6LC03M10 | LUCL12.. | INTGERAL 32MAGNETIC MODULE 38...76 | TeSys U MAGNETIC MODULE 42,6...156
LB6LC03M13 | LUCL12.. | INTGERAL 32MAGNETIC MODULE 60...120 | TeSys U MAGNETIC MODULE 42,6...156
LB6LC03M17 | LUCL18.. | INTGERAL 32MAGNETIC MODULE 95...190 | TeSys U MAGNETIC MODULE 63,9...234
LB6LC03M22 | LUCL32.. | INTGERAL 32MAGNETIC MODULE 150...300 | TeSys U MAGNETIC MODULE 113,6…416
LB6LC03M53 | LUCL32.. | INTGERAL 32MAGNETIC MODULE 190...380 | TeSys U MAGNETIC MODULE 113,6…416
LD1LB030B + LB1LB03P02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030B + LB1LB03P03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030B + LB1LB03P04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030B + LB1LB03P05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/50Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LB030B + LB1LB03P06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030B + LB1LB03P07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030B + LB1LB03P08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030B + LB1LB03P10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LB030B + LB1LB03P13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LB030B + LB1LB03P17 | LUB32 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/50Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LB030B + LB1LB03P21 | LUB32 + LUCB18B | DOL motor starter 18A-70kA(400V)-24/50Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/60Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P17 | LUB32 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/60Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LB030BC + LB1LB03P21 | LUB32 + LUCB18B | DOL motor starter 18A-70kA(400V)-24/60Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LB030BD + LB1LB03P02 | LUB12 + LUCBX6BL | DOL motor starter 0,25A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P03 | LUB12 + LUCBX6BL | DOL motor starter 0,4A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P04 | LUB12 + LUCBX6BL | DOL motor starter 0,6A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P05 | LUB12 + LUCB1XBL | DOL motor starter 1A-70kA(400V)-24DC | DOL motor starter 1,4A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P06 | LUB12 + LUCB05BL | DOL motor starter 1,6A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P07 | LUB12 + LUCB05BL | DOL motor starter 2,5A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P08 | LUB12 + LUCB05BL | DOL motor starter 4A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P10 | LUB12 + LUCB12BL | DOL motor starter 6A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P13 | LUB12 + LUCB12BL | DOL motor starter 10A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P17 | LUB32 + LUCB18BL | DOL motor starter 16A-70kA(400V)-24DC | DOL motor starter 18A-50kA(400V)-24DC
LD1LB030BD + LB1LB03P21 | LUB32 + LUCB18BL | DOL motor starter 18A-70kA(400V)-24DC | DOL motor starter 18A-50kA(400V)-24DC
LD1LB030D + LB1LB03P02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/60Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/60Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LB030D + LB1LB03P21 | LUB32 + LUCB18ES | DOL motor starter 18A-70kA(400V)-48/60Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/50Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/50Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LB030E + LB1LB03P21 | LUB32 + LUCB18ES | DOL motor starter 18A-70kA(400V)-48/50Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LB030F + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030F + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-110/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-120/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-120/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030FC + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-120/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-127/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-127/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-127/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-127/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030G + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-127/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-150/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-150/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-150/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-150/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-150/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-150/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-150/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-150/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-150/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)150/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030GF + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-150/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030K + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-110/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-180/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-180/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-180/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-180/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-180/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-180/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-180/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-180/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-180/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)180/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030L + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-180/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030LC + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-220/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030M + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-220/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030MC + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-230/240/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030P + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-230/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030PU7 + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-230/240/50/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-240/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-240/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LB030U + LB1LB03P21 | LUB32 + LUCB18FU | DOL motor starter 18A-70kA(400V)-240/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030B + LB1LC03M02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030B + LB1LC03M03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030B + LB1LC03M04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030B + LB1LC03M05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/50Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LC030B + LB1LC03M06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030B + LB1LC03M07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030B + LB1LC03M08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030B + LB1LC03M10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC030B + LB1LC03M13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC030B + LB1LC03M17 | LUB32 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/50Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LC030B + LB1LC03M22 | LUB32 + LUCB32B | DOL motor starter 25A-70kA(400V)-24/50Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC030B + LB1LC03M53 | LUB32 + LUCB32B | DOL motor starter 32A-70kA(400V)-24/50Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/60Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M17 | LUB12 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/60Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M22 | LUB32 + LUCB32B | DOL motor starter 25A-70kA(400V)-24/60Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC030BC + LB1LC03M53 | LUB32 + LUCB32B | DOL motor starter 32A-70kA(400V)-24/60Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC030BD + LB1LC03M02 | LUB12 + LUCBX6BL | DOL motor starter 0,25A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M03 | LUB12 + LUCBX6BL | DOL motor starter 0,4A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M04 | LUB12 + LUCBX6BL | DOL motor starter 0,6A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M05 | LUB12 + LUCB1XBL | DOL motor starter 1A-70kA(400V)-24DC | DOL motor starter 1,4A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M06 | LUB12 + LUCB05BL | DOL motor starter 1,6A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M07 | LUB12 + LUCB05BL | DOL motor starter 2,5A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M08 | LUB12 + LUCB05BL | DOL motor starter 4A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M10 | LUB12 + LUCB12BL | DOL motor starter 6A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M13 | LUB12 + LUCB12BL | DOL motor starter 10A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M17 | LUB12 + LUCB18BL | DOL motor starter 16A-70kA(400V)-24DC | DOL motor starter 18A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M22 | LUB32 + LUCB32BL | DOL motor starter 25A-70kA(400V)-24DC | DOL motor starter 32A-50kA(400V)-24DC
LD1LC030BD + LB1LC03M53 | LUB32 + LUCB32BL | DOL motor starter 32A-70kA(400V)-24DC | DOL motor starter 32A-50kA(400V)-24DC
LD1LC030D + LB1LC03M02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/60Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/60Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M22 | LUB32 + LUCB32ES | DOL motor starter 25A-70kA(400V)-48/60Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030D + LB1LC03M53 | LUB32 + LUCB32ES | DOL motor starter 32A-70kA(400V)-48/60Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/50Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/50Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M22 | LUB32 + LUCB32ES | DOL motor starter 25A-70kA(400V)-48/50Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030E + LB1LC03M53 | LUB32 + LUCB32ES | DOL motor starter 32A-70kA(400V)-48/50Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48V DC | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)--48V DC | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)--48V DC | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)--48V DC | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)--48V DC | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)--48V DC | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)--48V DC | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)--48V DC | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)--48V DC | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)--48V DC | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M22 | LUB32 + LUCB32ES | DOL motor starter 25A-70kA(400V)--48V DC | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030ED + LB1LC03M53 | LUB32 + LUCB32ES | DOL motor starter 32A-70kA(400V)--48V DC | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC030F + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-110/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030F + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-110/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-120/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-120/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-120/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030FC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-120/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110V DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110V DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110V DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110V DC | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110V DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110V DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110V DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110V DC | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110V DC | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110V DC | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-110V DC | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030FD + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-110V DC | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-127/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-127/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-127/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-127/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-127/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-127/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-127/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030G + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-127/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-125 DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-125 DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-125 DC | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-125 DC | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-125 DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-125 DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-125 DC | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-125 DC | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-125 DC | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-125 DC | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-125 DC | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030GD + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-125 DC | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-110/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030K + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-110/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-240/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-240/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030L + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030L+ LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030L+ LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030L+ LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030L+ LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-220/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030LC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-220/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-220/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030M + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-220/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030MC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030P + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/240/50/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030PU7 + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/240/50/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-240/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-240/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-240/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC030U + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-240/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130B + LB1LC03M02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130B + LB1LC03M03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130B + LB1LC03M04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/50Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130B + LB1LC03M05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/50Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LC130B + LB1LC03M06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130B + LB1LC03M07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130B + LB1LC03M08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/50Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130B + LB1LC03M10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC130B + LB1LC03M13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/50Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC130B + LB1LC03M17 | LUB32 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/50Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LC130B + LB1LC03M22 | LUB32 + LUCB32B | DOL motor starter 25A-70kA(400V)-24/50Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC130B + LB1LC03M53 | LUB32 + LUCB32B | DOL motor starter 32A-70kA(400V)-24/50Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M02 | LUB12 + LUCBX6B | DOL motor starter 0,25A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M03 | LUB12 + LUCBX6B | DOL motor starter 0,4A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M04 | LUB12 + LUCBX6B | DOL motor starter 0,6A-70kA(400V)-24/60Hz | DOL motor starter 0,6A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M05 | LUB12 + LUCB1XB | DOL motor starter 1A-70kA(400V)-24/60Hz | DOL motor starter 1,4A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M06 | LUB12 + LUCB05B | DOL motor starter 1,6A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M07 | LUB12 + LUCB05B | DOL motor starter 2,5A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M08 | LUB12 + LUCB05B | DOL motor starter 4A-70kA(400V)-24/60Hz | DOL motor starter 5A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M10 | LUB12 + LUCB12B | DOL motor starter 6A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M13 | LUB12 + LUCB12B | DOL motor starter 10A-70kA(400V)-24/60Hz | DOL motor starter 12A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M17 | LUB32 + LUCB18B | DOL motor starter 16A-70kA(400V)-24/60Hz | DOL motor starter 18A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M22 | LUB32 + LUCB32B | DOL motor starter 25A-70kA(400V)-24/60Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC130BC + LB1LC03M53 | LUB32 + LUCB32B | DOL motor starter 32A-70kA(400V)-24/60Hz | DOL motor starter 32A-50kA(400V)-24AC
LD1LC130BD + LB1LC03M02 | LUB12 + LUCBX6BL | DOL motor starter 0,25A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M03 | LUB12 + LUCBX6BL | DOL motor starter 0,4A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M04 | LUB12 + LUCBX6BL | DOL motor starter 0,6A-70kA(400V)-24DC | DOL motor starter 0,6A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M05 | LUB12 + LUCB1XBL | DOL motor starter 1A-70kA(400V)-24DC | DOL motor starter 1,4A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M06 | LUB12 + LUCB05BL | DOL motor starter 1,6A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M07 | LUB12 + LUCB05BL | DOL motor starter 2,5A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M08 | LUB12 + LUCB05BL | DOL motor starter 4A-70kA(400V)-24DC | DOL motor starter 5A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M10 | LUB12 + LUCB12BL | DOL motor starter 6A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M13 | LUB12 + LUCB12BL | DOL motor starter 10A-70kA(400V)-24DC | DOL motor starter 12A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M17 | LUB32 + LUCB18BL | DOL motor starter 16A-70kA(400V)-24DC | DOL motor starter 18A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M22 | LUB32 + LUCB32BL | DOL motor starter 25A-70kA(400V)-24DC | DOL motor starter 32A-50kA(400V)-24DC
LD1LC130BD + LB1LC03M53 | LUB32 + LUCB32BL | DOL motor starter 32A-70kA(400V)-24DC | DOL motor starter 32A-50kA(400V)-24DC
LD1LC130D + LB1LC03M02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/60Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/60Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/60Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/60Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/60Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M22 | LUB32 + LUCB32ES | DOL motor starter 25A-70kA(400V)-48/60Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC130D + LB1LC03M53 | LUB32 + LUCB32ES | DOL motor starter 32A-70kA(400V)-48/60Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M02 | LUB12 + LUCBX6ES | DOL motor starter 0,25A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M03 | LUB12 + LUCBX6ES | DOL motor starter 0,4A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M04 | LUB12 + LUCBX6ES | DOL motor starter 0,6A-70kA(400V)-48/50Hz | DOL motor starter 0,6A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M05 | LUB12 + LUCB1XES | DOL motor starter 1A-70kA(400V)-48/50Hz | DOL motor starter 1,4A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M06 | LUB12 + LUCB05ES | DOL motor starter 1,6A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M07 | LUB12 + LUCB05ES | DOL motor starter 2,5A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M08 | LUB12 + LUCB05ES | DOL motor starter 4A-70kA(400V)-48/50Hz | DOL motor starter 5A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M10 | LUB12 + LUCB12ES | DOL motor starter 6A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M13 | LUB12 + LUCB12ES | DOL motor starter 10A-70kA(400V)-48/50Hz | DOL motor starter 12A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M17 | LUB32 + LUCB18ES | DOL motor starter 16A-70kA(400V)-48/50Hz | DOL motor starter 18A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M22 | LUB32 + LUCB32ES | DOL motor starter 25A-70kA(400V)-48/50Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC130E + LB1LC03M53 | LUB32 + LUCB32ES | DOL motor starter 32A-70kA(400V)-48/50Hz | DOL motor starter 32A-50kA(400V)-48..72AC/DC
LD1LC130F + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-110/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130F + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-110/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-120/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-120/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-120/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-120/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-120/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-120/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130FC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-120/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-110/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-110/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-110/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-110/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M17 | LUB12 + LUCB18FU | DOL motor starter 16A-70kA(400V)-110/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-110/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130K + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-110/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-220/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130LC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-220/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-220/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-220/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-220/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-220/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-220/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-220/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130M + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-220/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130MC + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/240/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130P + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-230/240/50/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130PU7 + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-230/240/50/60Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M02 | LUB12 + LUCBX6FU | DOL motor starter 0,25A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M03 | LUB12 + LUCBX6FU | DOL motor starter 0,4A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M04 | LUB12 + LUCBX6FU | DOL motor starter 0,6A-70kA(400V)-240/50Hz | DOL motor starter 0,6A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M05 | LUB12 + LUCB1XFU | DOL motor starter 1A-70kA(400V)-240/50Hz | DOL motor starter 1,4A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M06 | LUB12 + LUCB05FU | DOL motor starter 1,6A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M07 | LUB12 + LUCB05FU | DOL motor starter 2,5A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M08 | LUB12 + LUCB05FU | DOL motor starter 4A-70kA(400V)-240/50Hz | DOL motor starter 5A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M10 | LUB12 + LUCB12FU | DOL motor starter 6A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M13 | LUB12 + LUCB12FU | DOL motor starter 10A-70kA(400V)-240/50Hz | DOL motor starter 12A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M17 | LUB32 + LUCB18FU | DOL motor starter 16A-70kA(400V)-240/50Hz | DOL motor starter 18A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M22 | LUB32 + LUCB32FU | DOL motor starter 25A-70kA(400V)-240/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD1LC130U + LB1LC03M53 | LUB32 + LUCB32FU | DOL motor starter 32A-70kA(400V)-240/50Hz | DOL motor starter 32A-50kA(400V)-110..240AC/DC
LD3LB130M05 | LUB12 + LUCA1XFU | DOL Integral 18 A 0.63 to 1 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 0.35 to 1.4 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M06 | LUB12 + LUCA1XFU | DOL Integral 18 A 1 to 1.6 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 0.35 to 1.4 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M07 | LUB12 + LUCA05FU | DOL Integral 18 A 1.6 to 2.5 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 1.25 to 5 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M08 | LUB12 + LUCA05FU | DOL Integral 18 A 2.5 to 4 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 1.25 to 5 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M10 | LUB12 + LUCA12FU | DOL Integral 18 A 4 to 6 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 3 to 12 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M13 | LUB12 + LUCA12FU | DOL Integral 18 A 6 to 10 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 3 to 12 Amps AC 110 V to 240 V 50/60 HZ
LD3LB130M17 | LUB32 + LUCA18FU | DOL Integral 18 A 10 to 16 A 220 V AC 50 Hz | DOL TeSys U power base 12 Amps + Control unit setting range 4.5 to 18 Amps AC 110 V to 240 V 50/60 HZ
LD5LB130B + LB1LB03P02 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P02 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P03 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P03 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P04 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P04 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P05 | LU2B12B + LUCB1XB | DOL motor starter For/Rev 1A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P05 | LUB12 + LUCB1XB + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P06 | LU2B12B + LUCB05B | DOL motor starter For/Rev 1,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P06 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P07 | LU2B12B + LUCB05B | DOL motor starter For/Rev 2,5A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P07 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P08 | LU2B12B + LUCB05B | DOL motor starter For/Rev 4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P08 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P10 | LU2B12B + LUCB12B | DOL motor starter For/Rev 6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P10 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P13 | LU2B12B + LUCB12B | DOL motor starter For/Rev 10A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P13 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P17 | LU2B32B + LUCB18B | DOL motor starter For/Rev 16A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P17 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LB130B + LB1LB03P21 | LU2B32B + LUCB18B | DOL motor starter For/Rev 18A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LB130B + LB1LB03P21 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P02 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P02 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P03 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P03 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P04 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P04 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P05 | LU2B12B + LUCB1XB | DOL motor starter For/Rev 1A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P05 | LUB12 + LUCB1XB + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P06 | LU2B12B + LUCB05B | DOL motor starter For/Rev 1,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P06 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P07 | LU2B12B + LUCB05B | DOL motor starter For/Rev 2,5A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P07 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P08 | LU2B12B + LUCB05B | DOL motor starter For/Rev 4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P08 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P10 | LU2B12B + LUCB12B | DOL motor starter For/Rev 6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P10 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P13 | LU2B12B + LUCB12B | DOL motor starter For/Rev 10A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P13 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P17 | LU2B32B + LUCB18B | DOL motor starter For/Rev 16A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P17 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LB130BC + LB1LB03P21 | LU2B32B2 + LUCB18B | DOL motor starter For/Rev 18A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LB130BC + LB1LB03P21 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LB130BD + LB1LB03P02 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,25A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P02 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P03 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,4A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P03 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P04 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,6A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P04 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P05 | LU2B12BL + LUCB1XBL | DOL motor starter For/Rev 1A-70kA(400V)-24DC | DOL motor starter For/Rev 1,4A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P05 | LUB12 + LUCB1XBL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24DC | DOL motor starter For/Rev 1,4A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P06 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 1,6A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P06 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P07 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 2,5A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P07 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P08 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 4A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P08 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P10 | LU2B12BL + LUCB12BL | DOL motor starter For/Rev 6A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P10 | LUB12 + LUCB12BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P13 | LU2B12BL + LUCB12BL | DOL motor starter For/Rev 10A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P13 | LUB12 + LUCB12BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P17 | LU2B32BL + LUCB18BL | DOL motor starter For/Rev 16A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P17 | LUB32 + LUCB18BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 90mm)
LD5LB130BD + LB1LB03P21 | LU2B32BL + LUCB18BL | DOL motor starter For/Rev 18A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 45mm)
LD5LB130BD + LB1LB03P21 | LUB32 + LUCB18BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 90mm)
LD5LB130D + LB1LB03P02 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P02 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P03 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P03 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P04 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P04 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P05 | LU2B12ES + LUCB1XES | DOL motor starter For/Rev 1A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P05 | LUB12 + LUCB1XES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P06 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 1,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P06 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P07 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 2,5A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P07 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P08 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P08 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P10 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P10 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P13 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 10A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P13 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P17 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 16A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P17 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130D + LB1LB03P21 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 18A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130D + LB1LB03P21 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P02 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P02 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P03 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P03 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P04 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P04 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P05 | LU2B12ES + LUCB1XES | DOL motor starter For/Rev 1A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P05 | LUB12 + LUCB1XES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P06 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 1,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P06 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P07 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 2,5A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P07 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P08 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P08 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P10 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P10 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P13 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 10A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P13 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P17 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 16A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P17 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130E + LB1LB03P21 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 18A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LB130E + LB1LB03P21 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LB130F + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130F + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130F + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FC + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FC + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-1110 DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110 DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD+ LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110 DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD+ LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110 DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110 DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD+ LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110 DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110 DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD+ LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110 DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110 DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130FD+ LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-110 DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130FD+ LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-110 DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G+ LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G+ LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130G+ LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130G+ LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130K + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130K + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130L + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130L + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-180/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130LC + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130LC + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P17 | LUB12 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130M + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130M + LB1LB03P21 | LUB12 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130MC + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130MC + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130P + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130P + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130PU7 + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130PU7 + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LB130U + LB1LB03P21 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 18A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LB130U + LB1LB03P21 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 18A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130B + LB1LC03M02 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M02 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M03 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M03 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M04 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M04 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M05 | LU2B12B + LUCB1XB | DOL motor starter For/Rev 1A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M05 | LUB12 + LUCB1XB + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M06 | LU2B12B + LUCB05B | DOL motor starter For/Rev 1,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M06 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M07 | LU2B12B + LUCB05B | DOL motor starter For/Rev 2,5A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M07 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M08 | LU2B12B + LUCB05B | DOL motor starter For/Rev 4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M08 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M10 | LU2B12B + LUCB12B | DOL motor starter For/Rev 6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M10 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M13 | LU2B12B + LUCB12B | DOL motor starter For/Rev 10A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M13 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M17 | LU2B32B + LUCB18B | DOL motor starter For/Rev 16A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M17 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M22 | LU2B32B + LUCB32B | DOL motor starter For/Rev 25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M22 | LUB32 + LUCB32B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 90mm)
LD5LC130B + LB1LC03M53 | LU2B32B + LUCB32B | DOL motor starter For/Rev 32A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 45mm)
LD5LC130B + LB1LC03M53 | LUB32 + LUCB32B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-24/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M02 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M02 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M03 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M03 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M04 | LU2B12B + LUCBX6B | DOL motor starter For/Rev 0,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M04 | LUB12 + LUCBX6B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M05 | LU2B12B + LUCB1XB | DOL motor starter For/Rev 1A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M05 | LUB12 + LUCB1XB + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M06 | LU2B12B + LUCB05B | DOL motor starter For/Rev 1,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M06 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M07 | LU2B12B + LUCB05B | DOL motor starter For/Rev 2,5A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M07 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M08 | LU2B12B + LUCB05B | DOL motor starter For/Rev 4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M08 | LUB12 + LUCB05B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M10 | LU2B12B + LUCB12B | DOL motor starter For/Rev 6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M10 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M13 | LU2B12B + LUCB12B | DOL motor starter For/Rev 10A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M13 | LUB12 + LUCB12B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M17 | LU2B32B + LUCB18B | DOL motor starter For/Rev 16A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M17 | LUB32 + LUCB18B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M22 | LU2B32B + LUCB32B | DOL motor starter For/Rev 25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M22 | LUB32 + LUCB32B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 90mm)
LD5LC130BC + LB1LC03M53 | LU2B322B + LUCB32B | DOL motor starter For/Rev 32A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 45mm)
LD5LC130BC + LB1LC03M53 | LUB32 + LUCB32B + LU6MB0B + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-24/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-24AC (width 90mm)
LD5LC130BD + LB1LC03M02 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,25A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M02 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M03 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,4A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M03 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M04 | LU2B12BL + LUCBX6BL | DOL motor starter For/Rev 0,6A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M04 | LUB12 + LUCBX6BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-24DC | DOL motor starter For/Rev 0,6A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M05 | LU2B12BL + LUCB1XBL | DOL motor starter For/Rev 1A-70kA(400V)-24DC | DOL motor starter For/Rev 1,4A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M05 | LUB12 + LUCB1XBL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-24DC | DOL motor starter For/Rev 1,4A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M06 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 1,6A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M06 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M07 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 2,5A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M07 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M08 | LU2B12BL + LUCB05BL | DOL motor starter For/Rev 4A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M08 | LUB12 + LUCB05BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-24DC | DOL motor starter For/Rev 5A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M10 | LU2B12BL + LUCB12BL | DOL motor starter For/Rev 6A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M10 | LUB12 + LUCB12BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M13 | LU2B12BL + LUCB12BL | DOL motor starter For/Rev 10A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M13 | LUB12 + LUCB12BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-24DC | DOL motor starter For/Rev 12A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M17 | LU2B32BL + LUCB18BL | DOL motor starter For/Rev 16A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M17 | LUB32 + LUCB18BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-24DC | DOL motor starter For/Rev 18A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M22 | LU2B32BL + LUCB32BL | DOL motor starter For/Rev 25A-70kA(400V)-24DC | DOL motor starter For/Rev 32A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M22 | LUB32 + LUCB32BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-24DC | DOL motor starter For/Rev 32A-50kA(400V)-24DC (width 90mm)
LD5LC130BD + LB1LC03M53 | LU2B32BL + LUCB32BL | DOL motor starter For/Rev 32A-70kA(400V)-24DC | DOL motor starter For/Rev 32A-50kA(400V)-24DC (width 45mm)
LD5LC130BD + LB1LC03M53 | LUB32 + LUCB32BL + LU6MB0BL + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-24DC | DOL motor starter For/Rev 32A-50kA(400V)-24DC (width 90mm)
LD5LC130D + LB1LC03M02 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M02 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M03 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M03 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M04 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M04 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M05 | LU2B12ES + LUCB1XES | DOL motor starter For/Rev 1A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M05 | LUB12 + LUCB1XES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M06 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 1,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M06 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M07 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 2,5A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M07 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M08 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M08 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M10 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M10 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M13 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 10A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M13 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M17 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 16A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M17 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M22 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M22 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130D + LB1LC03M53 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 32A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130D + LB1LC03M53 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-48/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M02 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M02 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M03 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M03 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M04 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M04 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M05 | LU2B12ES + LUCB1XES | DOL motor starter For/Rev 1A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M05 | LUB12 + LUCB1XES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M06 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 1,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M06 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M07 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 2,5A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M07 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M08 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M08 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M10 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M10 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M13 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 10A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M13 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M17 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 16A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M17 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M22 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M22 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130E + LB1LC03M53 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 32A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130E + LB1LC03M53 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-48/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M02 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,25A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M02 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M03 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,4A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M03 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M04 | LU2B12ES + LUCBX6ES | DOL motor starter For/Rev 0,6A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M04 | LUB12 + LUCBX6ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-48 DC | DOL motor starter For/Rev 0,6A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M05 | LU2B12ES + LUCB1XES | DOL motor starter For/Rev 1A-70kA(400V)-48 DC | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M05 | LUB12 + LUCB1XES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-48 DC | DOL motor starter For/Rev 1,4A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M06 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 1,6A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M06 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M07 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 2,5A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M07 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M08 | LU2B12ES + LUCB05ES | DOL motor starter For/Rev 4A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M08 | LUB12 + LUCB05ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-48 DC | DOL motor starter For/Rev 5A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M10 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 6A-70kA(400V)-48 DC | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M10 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-48 DC | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M13 | LU2B12ES + LUCB12ES | DOL motor starter For/Rev 10A-70kA(400V)-48 DC | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M13 | LUB12 + LUCB12ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-48 DC | DOL motor starter For/Rev 12A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M17 | LU2B32ES + LUCB18ES | DOL motor starter For/Rev 16A-70kA(400V)-48 DC | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M17 | LUB32 + LUCB18ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-48 DC | DOL motor starter For/Rev 18A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M22 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 25A-70kA(400V)-48 DC | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M22 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-48 DC | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130ED + LB1LC03M53 | LU2B32ES + LUCB32ES | DOL motor starter For/Rev 32A-70kA(400V)-48 DC | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 45mm)
LD5LC130ED + LB1LC03M53 | LUB32 + LUCB32ES + LU6MB0ES + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-48 DC | DOL motor starter For/Rev 32A-50kA(400V)-48..72AC/DC (width 90mm)
LD5LC130F + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130F + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130F + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-110/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FC + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FC + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-120/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-110V DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110V DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110V /DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110V DCz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110V DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110V DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-110V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-110V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130FD + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-110V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130FD + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-110V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130G + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130G+ LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-127/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-125V DC | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-125V DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-125V DC | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-125V DC | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-125V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-125V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-125V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-125V DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-125V DC | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-125V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-125V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-125V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130GD + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-125V DC | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130GD+ LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-125V DC | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130K + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130K + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-110/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130LC + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130LC + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-220/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130M + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130M + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-220/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130MC + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130MC + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-230/240/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130P + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130P + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-230/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130PU7 + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130PU7 + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-230/240/50/60Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M02 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M02 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M03 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M03 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M04 | LU2B12FU + LUCBX6FU | DOL motor starter For/Rev 0,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M04 | LUB12 + LUCBX6FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 0,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 0,6A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M05 | LU2B12FU + LUCB1XFU | DOL motor starter For/Rev 1A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M05 | LUB12 + LUCB1XFU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 1,4A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M06 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 1,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M06 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 1,6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M07 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 2,5A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M07 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 2,5A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M08 | LU2B12FU + LUCB05FU | DOL motor starter For/Rev 4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M08 | LUB12 + LUCB05FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 4A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 5A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M10 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M10 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 6A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M13 | LU2B12FU + LUCB12FU | DOL motor starter For/Rev 10A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M13 | LUB12 + LUCB12FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 10A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 12A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M17 | LU2B32FU + LUCB18FU | DOL motor starter For/Rev 16A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M17 | LUB32 + LUCB18FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 16A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 18A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M22 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M22 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 25A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)
LD5LC130U + LB1LC03M53 | LU2B32FU + LUCB32FU | DOL motor starter For/Rev 32A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 45mm)
LD5LC130U + LB1LC03M53 | LUB32 + LUCB32FU + LU6MB0FU + LU9M1 + LU9MR1 | DOL motor starter For/Rev 32A-70kA(400V)-240/50Hz | DOL motor starter For/Rev 32A-50kA(400V)-110..240AC/DC (width 90mm)