## Slide 1: Adding a Device while Process Running
V-TechSupport)

## Slide 2
M580 HSBY DTM device changes while Process is Running
Online Modification (MOL)
Connect PC to Primary PLC
Modify program
BUILD command to transfer
If Logic mismatch allowed, peered stays STBY
Transfer app from Primary to STBY

## Slide 3
Forcing the Peered CPU from WAIT to STBY after offline modification
Working Conditions:
Logic Mismatch must be set to 1 in both CPUs
Needs to be implemented in both CPUs
Not all the offline changes are accepted (Scope: program primarily)
Build changes only (not rebuild all)
HSBY_BUILD_OFFLINE Function Block
Availability:
By default, Unity V12 (Q1 2017) and all subsequent versions.
All Control Expert versions.
M580 V2.80 and greater

## Slide 4
Offline program modification
PC is disconnected from PLC
Modify program, then BUILD
Connect to PLC
Because PRG is different, complete download required. Download to the PLC (as PLC will stop it will be the STBY)
RUN the PLC > PLC Switches to WAIT
Set to 1 the input of the Block in both PLC
Do a SWAP, then transfer app from PRIM to STBY
Implement an Offline Change on M580 HSBY
Offline Program Modification Steps
Primarily step: Implement the EFB
Connect PC to Primary PLC
Modify program and add the HSBY_BUILD_OFFLINE
BUILD changes
Transfer app from Primary to STBY

## Slide 5
Implement the HSBY_BUILD_OFFLINE in each CPU
Adding a Device without Stopping the Process
Macro Steps
Connected
RUN_PRIMARY
RUN_STANBY

## Slide 6
Implement the HSBY_BUILD_OFFLINE in each CPU
Disconnect, implement the change, and BUILD CHANGES (do not REBUILD the application)
Adding a Device without Stopping the Process
Macro Steps
Not Connected
RUN_PRIMARY
RUN_STANBY

## Slide 7
Implement the HSBY_BUILD_OFFLINE in each CPU
Disconnect, implement the change, and BUILD CHANGES (do not REBUILD the application)
Connect, transfer and run the application in the Standby
  At this stage, the Standby will be in WAIT state, the system is not redundant but the Primary still control the process
Adding a Device without Stopping the Process
Macro Steps
RUN_PRIMARY
WAIT

## Slide 8
Implement the HSBY_BUILD_OFFLINE in each CPU
Disconnect, implement the change, and BUILD CHANGES (do not REBUILD the application)
Connect, transfer and run the application in the Standby
  At this stage, the Standby will be in WAIT state, the system is not redundant but the Primary still control the process
Using the HSBY_BUILD_OFFLINE, force from WAIT to RUN_STANDBY to make the process redundant again
Adding a Device without Stopping the Process
Macro Steps
RUN_PRIMARY
RUN_STANBY

## Slide 9
Implement the HSBY_BUILD_OFFLINE in each CPU
Disconnect, implement the change, and BUILD CHANGES (do not REBUILD the application)
Connect, transfer and run the application in the Standby
  At this stage, the Standby will be in WAIT state, the system is not redundant but the Primary still control the process
Using the HSBY_BUILD_OFFLINE, force from WAIT to RUN_STANDBY to make the process redundant again
SWAP the CPUs in order to transfer the application is the other CPU
Adding a Device without Stopping the Process
Macro Steps
RUN_STANDBY
RUN_PRIMARY

## Slide 10
Side (good) effects… tested items that can be done without stopping the Process (PRIM/STBY)
Ability to add / remove a device scanned on Modbus TCP
Change Local Slaves configuration
Change Cybersecurity configuration (ok only on eNOC, not on CPUs)
Do not mix the usage of this block with Online build on the Primary related to variable modification. Indeed, reallocation of the variables in the memory might have side effects such as variable not being exchanged.
Adding a Device on Ethernet while Keeping Process Running
The Block is not able to check most modifications done in the DTMs
NOTE: all customer use cases cannot be tested as we cannot imagine all the potential use cases.
Responsibility of the User to implement this as tested.