## index
History
Version | Comment | Autor | Date
1.0 | Creation | Mathieu Kapfer - OPEN | 2010-11-08
1.1 | Review with SE | Mathieu Kapfer - OPEN | 2010-11-08
1.2 | Change description of item 353 - New descrition : "PLC Modbus TCP Server Dest Addr" Old Description : "PLC Modbus TCP Server Size" | Mathieu Kapfer - OPEN | 2010-11-15
1.2_rev4 | Compilation of versions 1.2 and 1.2-rev3 | Idy Demba Thiam- SE | 2011-11-24
1.3-rev2 | fusion 1.2-rev4 et 1.3: Modifications / EP2 | Idy Demba Thiam- SE | 2011-11-24
1.3-rev4 | fusion 1.3-rev2 and table ccve: check table correspondance | Idy Demba Thiam- SE | 2011-11-25
1.4 | ajout des entrants SE dans la table (capteurs, update, versions, etc) | Idy Demba Thiam- SE | 2011-11-25
1.4-rev1 | retour OPEN sur les nouveaux ajouts | Mathieu Kapfer - OPEN | 2011-12-02
1.4-rev2 | compilation retours OPEN (buzzer, TI, etc) | Mathieu Kapfer - OPEN | 2011-12-12
1.4-rev3 | intégration besoin US | Paul Reid- SE (US)
1.4-rev4 | intégration table IHM détaillée + besoin STU | Thierry Masciave- SE
1.5 | fusion table evse+ changes table US | Idy Demba Thiam- SE | 2012-01-27
2.0 | add inputs from SE (config, HMI, IP, Update peripherals) | Idy Demba Thiam- SE | 2012-03-05
2.1 | Update Description tab and lastchargestatus | Idy Demba Thiam- SE | 2012-03-20
2.2 | Update HMI table | Thierry Masciave/Idy Demba Thiam- SE | 2012-04-15
2.4 | add maintenance screens | Thierry Masciave/Idy Demba Thiam | 2012-06-18
2.5 | new SE inputs ( last charge status pool) | Idy Demba Thiam- SE | 2012-08-05
2.6 | Update Description tab and lastchargestatus | Idy Demba Thiam- SE | 2012-09-22
2.7 | Add PLC command register to interface with PLC | Idy Demba Thiam- SE | 2012-10-12
2.8 | Update PLC command description | Idy Demba Thiam- SE | 2012-11-01
2.9 | Set autotest status read only | Idy Demba Thiam | 2012-11-13
2.10 | add autotest status PLC communication loss | Idy Demba Thiam | 2013-02-12
2.11 | update parameters presentation with persistent data infos | Idy Demba Thiam | 2013-02-20
2.12 | align firmware update status and make ImaxUser read only | Idy Demba Thiam | 2013-02-27
2.13 | modify EVSE_Status register | Idy Demba Thiam | 2013-03-27
2.14 | modify EVSE_Status to add postponed mode bit | Idy Demba Thiam | 2013-05-15
2.15 | add factory, NRG management, history and supervision registers | Idy Demba Thiam | 2013-05-17
2.16 | add ImaxStation - Charging Point Upstream Protection | Idy Demba Thiam | 2013-06-11
2.17 | add remote setPoint to change current given to EV | Idy Demba Thiam | 2013-06-26
2.18 | add upgrade configuration file register @148 | Idy Demba Thiam | 2013-07-24
2.19 | add UID of current session | Idy Demba Thiam | 2013-09-02
2.20 | update for HMI and error management | Idy Demba Thiam | 2013-10-07
2.21 | update for energy management and remote command | Idy Demba Thiam | 2013-12-19
3.0 | add standalone energy management registers | Idy Demba Thiam | 2014-09-19
3.1 | add evse status bit 10 for alternative energy suspend | Idy Demba Thiam | 2014-10-13
3.2 | fix charge UID address and add remote authent registers | Idy Demba Thiam | 2014-11-13
3.4 | Add Time Setting and Control tab adn RemoteCmd 40, 41, 42 | Thomas Genet | 2015-02-06
3.5 | Add reservation registers in Supervision Tab and RemoteCmd 67 and 68 | Thomas Genet | 2015-04-08
3.6 | Add ChargingTime register @30 | Thomas Genet | 2015-04-24
3.7 | Add command "Back to factory" in register @ 701 | Thomas Genet | 2015-06-02
3.8 | Modification Error State MSB Bit 13 et Error State LSB Bit 8 | Thierry Andreis | 2015-10-06
3.9 | Ajout registres ReadOnly FW version | Guillaume Schmuck | 2016-03-25 | see \GIT\ev_link_charger\code\evse\src\database\database_def.h
Légende
Reserved register but function not yet implemented
US DaughterBoard
New section of current version

## Modbus parameters description
Register | Description | Size | Permission | Reset Value | Unit | Non Volatile Memory | Notes |  | US DB Data? |  | US Daughter Board Register to be read or written by main board.
Board supervision
EventBit | This bit is set by EVSE to notify the PLC of register modification | word | Read | 1 | - | No |  |  | ?
Automatically cleared after read.
LifeBit | This bit is set by PLC and should be reset by EVSE in less than 500 ms | word | Read/Write | 0 | - | no |  |  | NO
UpTime | Uptime – activity counter in number of second since last start up ( 2^32) | 2 word | Read | 0 |  | no |  |  | NO
Remote_command | Command from a Remote controller (PLC for instance) | word | Read/Write | 0 | - | no |  |  | NO
0- OK (initial state)
1- Enter Maintenance Mode
2- Enter Booked Mode
3- Stop charge(Unlock Plug)
4- Suspend Charging(from EVlink Energy for exemple)
5- restart charging (from Evlink Energy for exemple)
6- Raise "Error Circuit-Breaker state"
7- Lock Plug / Unlock Shutter
8- Unlock Plug / Lock Shutter
10- Start Charge (if charge is postponed)
16- Switch to Clustered mode
17- UpdateDurationTable (Grrenpark Power/duration table)
32- Quit maintenance Mode
33- Quit Booked Mode
34- Remove "Error Circuit-Breaker state"
40- Set Available
41- Set Unavailable
42- Set Unavailable Scheduled
64- Remote START (with UID, connector ID and transaction ID)
65- Remote STOP (transaction ID)
66- Remote Authent(with UID and optional type)
67 - Make or modify a reservation
68 - Delete a reservation
80- Remove the station from the cluster
0xFE- ACK (acknowledge errors), switch off indicators
0xFF- RAZ (RAZ bootcount, lastchargestatus, error statuses, etc)
Reboot | Platform reboot | word | Read/Write | 0 | - | no |  |  | NO
Remote Command Status | Indicate the status of the last PLC command execution(Cmd) | 1 word | Read | 0 | - | no |  |  | NO
0 - Remote controller has acked last command status
Cmd - OK (Last command was well executed)
Cmd ¦ 0x8000 - ERROR (last command was not well executed)
0xFF - Undefined
USBoardGFTimeUntilReset | Number of seconds remaining until GF auto-reset. Zero means auto-reset is not active. | word | Read | ? | - | no |  |  | YES |  | REG_GF_TIME_UNTIL_RESET (@12)
USBoardAutoResetCount | Number of automatic GF reset attempted during a single charging cycle | word | Read | 0 | - | no |  |  | YES |  | REG_AUTO_RESET_COUNT (@30)
ResetLastChargeStatus | Moves the currentFaultType register contents to the LastFaultType register, clears CurrentFaultType register. | word | Read/Write | 0 | - | no |  |  | YES |  | REG_FAULT_RESET (@36)
USBoardGFAutoResetTimeSetting | Number of seconds before GF auto-reset is attempted | word | Read/Write | 0 | - | no |  |  | YES |  | REG_GF_AUTO_RESET_TIME_SETTING (@38)
USBoardContactErrorCount | Number of contact error readings | word | Read | 0 |  | no |  |  | YES |  | REG_CONTACT_ERROR_COUNT (@60)
USBoardSelfTestRequest | 0xA0A0 - Request self test sequence (only when contacts are open) | word | Read/Write | 0 | - | no |  |  | YES |  | REG_SELF_TEST_REQUEST (@34)
Board configuration
MicroSwitch Status | Status of the 10 micro-switch on board start up | word | Read |  | - | no | Main board |  | NO
USBoardDetection | Indicate if US board is plugged or not | word | Read | 1 (not plugged) | - | no | Indicated by hardware, not US register. |  | NO
FWVersion | Major and minor of FW | 1 word | Read | FW Version | - | no | Main board |  | NO
FWRevisionNumber | Revision Number of FW | 1 word | Read | Rev Number | - | no | Main board |  | NO
HWReference | Hardware Reference of the station (board, plug, etc) | 4 word | Read/Write | HW Version | - | no | Main board |  | NO
SerialNumber | Board Serial Number | 2 word | Read/Write | Serial Number | - | no | Main board |  | NO
RFIDFWVersion | Major and Minor Version of RFID Reader | 2 word | Read | RFID Version | - | no | Main board |  | NO
STUFWVersion | Major and Minor Version of Screen Display | 2 word | Read | Screen Version | - | no | Main board |  | NO
USBoardFWVersion | Major and minor of US Board FW | 2 word | Read | FW Version | - | no |  |  | YES |  | REG_FIRMWARE_VERSION (@1)
USBoardFWChecksum | US Board FW Checksum | 1 word | Read | FW Checksum | - | no |  |  | YES |  | REG_FIRMWARE_CHECKSUM (@3)
State Machine
MainState | · 0 – EV supervision (M340 managed) | word | Read | 0 | - | no | Main board |  | NO |  | REG_MAIN_STATE (@10)
· 1 - FW update
| · 2 - Standalone mode (Charging point without PLC) ==> State Machine to be Described | [5 empty] | Main board |  | NO
| · 3 - Debug mode (Future usage TBD) | [5 empty] | Main board |  | NO
· 4 - US Board FW update
CPWState | CPW1 State: | word | Read | 0 | - | no | US board data if US board is plugged in, Main board otherwise. |  | YES |  | REG_GLOBAL_STATE (@16)
| · 0 – EVSE not available - state F | [8 empty] | 0 | STATE_CPW_EVSE_NotAvailable_StateF
| · 1 - EVSE available - state A | [8 empty] | 1 | STATE_CPW_EVSE_Available_StateA
| · 2 - Plug detected - state A+ | [8 empty] | 2 | STATE_CPW_PlugDetected_StateA_Plus
| · 3 - reserved | [8 empty] | 3 | STATE_CPW_Reserved
| · 4 - EV connected – state B | [8 empty] | 4 | STATE_CPW_EV_Connected_StateB
| · 5 - EV connected – state C- | [8 empty] | 5 | STATE_CPW_EV_Connected_StateC_Minus
| · 6 - EV connected, ventilation required – state D- | [8 empty] | 6 | STATE_CPW_EV_Connected_StateD_Minus
| · 7 - EVSE ready - state B+ | [8 empty] | 7 | STATE_CPW_EVSE_Ready_StateB_Plus
| · 8 - EV ready - state C | [8 empty] | 8 | STATE_CPW_EVSE_Ready_StateC
| · 9 - Charging EV - state C+ | [8 empty] | 9 | STATE_CPW_Charge_EV_StateC_Plus
| · 10 - EV ready, ventilation required - state D | [8 empty] | 10 | STATE_CPW_EVSE_Ready_StateD
| · 11 - Charging EV, ventilation required - state D+ | [8 empty] | 11 | STATE_CPW_Charge_EV_StateD_Plus
| · 12 - Stop charging | [8 empty] | 12 | STATE_CPW_StopCharging
| · 13 - Alarm | [8 empty] | 13 | STATE_CPW_Alarm
| · 14 - Shortcut – state E | [8 empty] | 14 | STATE_CPW_Shortcut
| · 15 - Digital Com by EVSE state | [8 empty] | 15 | STATE_CPW_EVSE_DigitalCom
[10 empty] | 255 | STATE_CPW_Undefined
CableState | Cable capability: (get from CPW2) | word | Read | 0 | - | no | Main board to determine cable ampacity of perminantly connected cable. US cable ampacity is typically 30A. May be OK to indicate 3 for 32A. | Main purpose is to indicate stuck cable. | NO
· 0 – No cable
· 1 – 13 A
· 2 – 20 A
· 3 – 32 A
· 4 – 63 A
· 5 – communication error
EVState | EV (get from CPW1): | word | Read | 0 | - | no |  |  | NO
· 0 - State A Not Present 12V,
· 1 - State B Present 9V,
· 2 - State B Present Asked 9V M12V,
· 3 - State C Ready 6V ,
· 4 - State C Ready 6V M12V ,
· 5 - State D Ready VR 3V,
. 6 - State D Ready VR 3V_M12V,
. 7 - State E ShortCircuit,
. 8 - State F NotAvialable,
. 9 - State Not defined
LastChargeStatus | Status of the last charge : | word | Read | 255 | - | yes | Status of the last charge. |  | YES |  | REG_LAST_FAULT_TYPE (@62)
· 0 – circuit breaker enabled (emergency)
· 1 – OK (ended by EV in mode 3)
· 2 - ended by cluster manager loss (lifebit timeout 10s)
· 3 – end of charge in SM3 (low current)
· 4 – communication error (PWM lost)
· 5 – disconnection cable (EVSE plug off)
· 6 - disconnection EV (VE plug off)
· 7 – shortcut
· 8 – overload
· 9 – canceled by supervisor (external command)
· 0xA - ventillation not allowed
· 0xB - unexpected contactor open
· 0xC - simplified mode 3 not allowed
· 0xD - power supply internal error(contactor not able to close)
· 0xE - Unexpected plug unlock
· 0xF - default Nb Phases (triphase not allowed)
· 0x45 – DI default Surge arrestor
· 0x46 – DI default Anti Intrusion
· 0x49 – DI default Shutter Unlock
· 0x4A – DI default FLSI (Force Load Shedding Input)
· 0x4B – DI default Emergency Stop
· 0x4C – DI default Undervoltage
· 0x4D – DI default CI (Conditional Input)
· 0xFE - other
· 0xFF - undefined
US Board Last Fault Types (enumeration proposed)
· 100 - Not used. Use "0" to indicate OK, ended by EV.
· 101 - GF test failure (last charge)
· 102 - Internal microcontroller fault detected (last charge)
· 103 - Internal power supply fault detected (12V) (last charge)
· 104 - Contactor stuck closed (last charge)
· 105 - Contactor stuck open (last charge)
· 106 - EV requests ventilation (last charge)
· 107 - Control pilot out of range (last charge)
· 108 - Undefined (last charge)
· 109 - Auto-Resettable GF detected (last charge)
· 110 - Non-autoresettable GF detected (last charge)
· 111 - Undefined (last charge)
· 112 - Undefined (last charge)
· 113 - Undefined (last charge)
· 114 - Undefined (last charge)
· 115 - Undefined (last charge)
· 116 - Undefined (last charge)
· 117 - Undefined (last charge)
· 118 - Undefined (last charge)
· 119 - Undefined (last charge)
· 254 - other
· 255 – undefined
LastChargeStatus_1 | Status of the last charge : | word | Read | 255 | - | yes | Status of the last charge - 1. |  | YES |  | REG_LAST_FAULT_TYPE (@63)
· 0 – circuit breaker enabled (emergency)
· 1 – OK (ended by EV in mode 3)
· 2 - ended by PLC disconnection (lifebit timeout 10s)
· 3 – end of charge in SM3 (low current)
· 4 – communication error (PWM lost)
· 5 – disconnection cable (EVSE plug off)
· 6 - disconnection EV (VE plug off)
· 7 – shortcut
· 8 – overload
· 9 – canceled by supervisor (external command)
· 0xA - ventillation not allowed
· 0xB - unexpected contactor open
· 0xC - simplified mode 3 not allowed
· 0xD - power supply internal error(contactor not able to close)
· 0xE - Unexpected plug unlock
· 0xF - default Nb Phases (triphase not allowed)
· 0x45 – DI default Parafoudre
· 0x46 – DI default Anti Intrusion
· 0x49 – DI default Shutter Unlock
· 0x4A – DI default FLSI (Force Load Shedding Input)
· 0x4B – DI default Emergency Stop
· 0x4C – DI default Undervoltage
· 0x4D – DI default CI (Conditional Input)
· 0xFE - other
· 0xFF - undefined
· 102 - Internal microcontroller fault detected (last charge -1)
· 103 - Internal power supply fault detected (12V) (last charge -1)
· 104 - Contactor stuck closed (last charge -1)
· 105 - Contactor stuck open (last charge -1)
· 106 - EV requests ventilation (last charge -1)
· 107 - Control pilot out of range (last charge -1)
· 108 - Undefined (last charge -1)
· 109 - Auto-Resettable GF detected (last charge -1)
· 110 - Non-autoresettable GF detected (last charge -1)
· 111 - Undefined (last charge -1)
· 112 - Undefined (last charge -1)
· 113 - Undefined (last charge -1)
· 114 - Undefined (last charge -1)
· 115 - Undefined (last charge -1)
· 116 - Undefined (last charge -1)
· 117 - Undefined (last charge -1)
· 118 - Undefined (last charge -1)
· 119 - Undefined (last charge -1)
· 254 - other
· 255 – undefined
LastChargeStatus_2 | Status of the last charge : | word | Read | 255 | - | yes | Status of the last charge - 2. |  | YES |  | REG_LAST_FAULT_TYPE (@64)
· 0 – circuit breaker enabled (emergency)
· 1 – OK (ended by EV in mode 3)
· 2 - ended by PLC disconnection (lifebit timeout 10s)
· 3 – end of charge in SM3 (low current)
· 4 – communication error (PWM lost)
· 5 – disconnection cable (EVSE plug off)
· 6 - disconnection EV (VE plug off)
· 7 – shortcut
· 8 – overload
· 9 – canceled by supervisor (external command)
· 0xA - ventillation not allowed
· 0xB - unexpected contactor open
· 0xC - simplified mode 3 not allowed
· 0xD - power supply internal error(contactor not able to close)
· 0xE - Unexpected plug unlock
· 0xF - default Nb Phases (triphase not allowed)
· 0x45 – DI default Parafoudre
· 0x46 – DI default Anti Intrusion
· 0x49 – DI default Shutter Unlock
· 0x4A – DI default FLSI (Force Load Shedding Input)
· 0x4B – DI default Emergency Stop
· 0x4C – DI default Undervoltage
· 0x4D – DI default CI (Conditional Input)
· 0xFE - other
· 0xFF - undefined
· 102 - Internal microcontroller fault detected (last charge -2)
· 103 - Internal power supply fault detected (12V) (last charge -2)
· 104 - Contactor stuck closed (last charge -2)
· 105 - Contactor stuck open (last charge -2)
· 106 - EV requests ventilation (last charge -2)
· 107 - Control pilot out of range (last charge -2)
· 108 - Undefined (last charge -2)
· 109 - Auto-Resettable GF detected (last charge -2)
· 110 - Non-autoresettable GF detected (last charge -2)
· 111 - Undefined (last charge -2)
· 112 - Undefined (last charge -2)
· 113 - Undefined (last charge -2)
· 114 - Undefined (last charge -2)
· 115 - Undefined (last charge -2)
· 116 - Undefined (last charge -2)
· 117 - Undefined (last charge -2)
· 118 - Undefined (last charge -2)
· 119 - Undefined (last charge -2)
· 254 - other
· 255 – undefined
LastChargeStatus_3 | Status of the last charge : | word | Read | 255 | - | yes | Status of the last charge - 3. |  | YES |  | REG_LAST_FAULT_TYPE (@65)
· 0 – circuit breaker enabled (emergency)
· 1 – OK (ended by EV in mode 3)
· 2 - ended by PLC disconnection (lifebit timeout 10s)
· 3 – end of charge in SM3 (low current)
· 4 – communication error (PWM lost)
· 5 – disconnection cable (EVSE plug off)
· 6 - disconnection EV (VE plug off)
· 7 – shortcut
· 8 – overload
· 9 – canceled by supervisor (external command)
· 0xA - ventillation not allowed
· 0xB - unexpected contactor open
· 0xC - simplified mode 3 not allowed
· 0xD - power supply internal error(contactor not able to close)
· 0xE - Unexpected plug unlock
· 0xF - default Nb Phases (triphase not allowed)
· 0x45 – DI default Parafoudre
· 0x46 – DI default Anti Intrusion
· 0x49 – DI default Shutter Unlock
· 0x4A – DI default FLSI (Force Load Shedding Input)
· 0x4B – DI default Emergency Stop
· 0x4C – DI default Undervoltage
· 0x4D – DI default CI (Conditional Input)
· 0xFE - other
· 0xFF - undefined
· 102 - Internal microcontroller fault detected (last charge -3)
· 103 - Internal power supply fault detected (12V) (last charge -3)
· 104 - Contactor stuck closed (last charge -3)
· 105 - Contactor stuck open (last charge -3)
· 106 - EV requests ventilation (last charge -3)
· 107 - Control pilot out of range (last charge -3)
· 108 - Undefined (last charge -3)
· 109 - Auto-Resettable GF detected (last charge -3)
· 110 - Non-autoresettable GF detected (last charge -3)
· 111 - Undefined (last charge -3)
· 112 - Undefined (last charge -3)
· 113 - Undefined (last charge -3)
· 114 - Undefined (last charge -3)
· 115 - Undefined (last charge -3)
· 116 - Undefined (last charge -3)
· 117 - Undefined (last charge -3)
· 118 - Undefined (last charge -3)
· 119 - Undefined (last charge -3)
· 254 - other
· 255 – undefined
LastChargeStatus_4 | Status of the last charge : | word | Read | 255 | - | yes | Status of the last charge - 4. |  | YES |  | REG_LAST_FAULT_TYPE (@66)
· 0 – circuit breaker enabled (emergency)
· 1 – OK (ended by EV in mode 3)
· 2 - ended by PLC disconnection (lifebit timeout 10s)
· 3 – end of charge in SM3 (low current)
· 4 – communication error (PWM lost)
· 5 – disconnection cable (EVSE plug off)
· 6 - disconnection EV (VE plug off)
· 7 – shortcut
· 8 – overload
· 9 – canceled by supervisor (external command)
· 0xA - ventillation not allowed
· 0xB - unexpected contactor open
· 0xC - simplified mode 3 not allowed
· 0xD - power supply internal error(contactor not able to close)
· 0xE - Unexpected plug unlock
· 0xF - default Nb Phases (triphase not allowed)
· 0x45 – DI default Parafoudre
· 0x46 – DI default Anti Intrusion
· 0x49 – DI default Shutter Unlock
· 0x4A – DI default FLSI (Force Load Shedding Input)
· 0x4B – DI default Emergency Stop
· 0x4C – DI default Undervoltage
· 0x4D – DI default CI (Conditional Input)
· 0xFE - other
· 0xFF - undefined
· 102 - Internal microcontroller fault detected (last charge -4)
· 103 - Internal power supply fault detected (12V) (last charge -4)
· 104 - Contactor stuck closed (last charge -4)
· 105 - Contactor stuck open (last charge -4)
· 106 - EV requests ventilation (last charge -4)
· 107 - Control pilot out of range (last charge -4)
· 108 - Undefined (last charge -4)
· 109 - Auto-Resettable GF detected (last charge -4)
· 110 - Non-autoresettable GF detected (last charge -4)
· 111 - Undefined (last charge -4)
· 112 - Undefined (last charge -4)
· 113 - Undefined (last charge -4)
· 114 - Undefined (last charge -4)
· 115 - Undefined (last charge -4)
· 116 - Undefined (last charge -4)
· 117 - Undefined (last charge -4)
· 118 - Undefined (last charge -4)
· 119 - Undefined (last charge -4)
· 254 - other
· 255 – undefined
EVSE_Status | Status of current EVSE charging state machine | word | Read | 255 | - | no | Status of the current charging event. |  | YES |  | TBD by US TEAM
| SimplifiedMode3Detected (1: yes, 0 no) | bit 0 | [6 empty] | NO
| Ventilation Mode Detected (1: yes, 0 no) | bit 1
| Cluster mode ( 1 clustered mode, 0 standalone mode) | bit 2 | [6 empty] | NO
| Monophased/Triphased charge (0 mono; 1 tri) | bit 3 | [6 empty] | NO
| Shucko plug charging | bit 4 | [6 empty] | NO
|  | bit 5 | [6 empty] | NO
bit 6
bit 7
| User Type (1 :VIP User, 0 : normal User) | bit 8
bit 9
| alternative energy suspend (1: yes, 0 no) | bit 10
| Postpone charge ( 1: postpone enabled, 0: postpone disabled) | bit 11
| Maintenance Cmd 1 received (1: yes, 0 no) | bit 12
| Booked cmd 2 received (1: yes; 0: no) | bit 13
| Suspend Cmd 4 received (1:yes; 0:no) | bit 14
| Unavailable Cmd 6 received (1 : yes, 0 : no) | bit 15
Command for VE management
EVSE_Management | Command for VE management register | word | Read/Write | 0 | - | no
| EVSE_ Availability : | bit 0 | Read/Write | 0 | - | no |  |  | NO
Used by PLC to set the EVSE available (used in CPW 1 state machine for transition from state F to state A)
| EVSE_Ready : | bit 1 | Read/Write | 0 | - | no |  |  | YES |  | if US board, when this register is set to 1, a "1" shall also be written to REG_ALLOW_CHARGE register on US board.(@39)
| Used by PLC to set the EVSE ready for sending energy (used in CPW 1 state machine for transition from B to B’) | [8 empty] | 0 1 | Charging not authorized Charging authorized
| EVSE_DigitalComMode: | bit 2 | Read/Write | 0 | - | no | Always 0 when US board connected. |  | NO
0 – CPW1, Other (=> PWM = 5%)
| SimplifiedMode3Enabled: | bit 3 | Read/Write | 0 | - | no | Not applicable if US board is plugged in |  | NO
0 – disable, 1 - enable
| VentilationEnabled: | bit 4 | Read/Write | 0 | - | no | Not applicable if US board is plugged in |  | NO
0 – disable, 1 - enable
RAZ Count | Reset pulse counter | word | Read/Write | 0 | - | no |  |  | NO
Input for VE management
ImaxCard | Maximum intensity coded by micro-switches on board startup | word | Read | 0 | A | no |  |  | NO
ImaxCable | Cable maximum intensity | word | Read | 0 | A | no | Max US board allowed intensity (Amps?) |  | YES |  | REG_MAX_CHARGING_CURRENT(@32)
IMaxPLC | Maximum intensity set by PLC | word | Read/Write | 63 | A | yes | US board - PLC can modify up to max allowed intensity |  | YES |  | REG_CHARGING_CURRENT_LIMIT(@40)
IMaxUser | Maximum intensity according to user power choice | word | Read/Write | 0 | A | yes |  |  | NO
IMaxInstall | Maximum intensity allowed by installation contract | word | Read/Write | 0 | A | yes |  |  | NO
CurrentMonitoringMode | 0 = Local , 1 = Externe (see §6.2.2) | word | Read/Write | 0 | - | no |  |  | NO
InstantCurrentMeasPhaseA | Instant Current Measured in Phase A | word | Read | 0 | 10² A | no |  |  | NO
InstantCurrentMeasPhaseB | Instant Current Measured in Phase B | word | Read | 0 | 10² A | no |  |  | NO
InstantCurrentMeasPhaseC | Instant Current Measured in Phase C | word | Read | 0 | 10² A | no |  |  | NO
InstantCurrentGivenPhaseA | Instant Current Given for Phase A | word | Read/Write | 0 | 10² A | no |  |  | NO
InstantCurrentGivenPhaseB | Instant Current Given for Phase B | word | Read/Write | 0 | 10² A | no |  |  | NO
InstantCurrentGivenPhaseC | Instant Current Given for Phase C | word | Read/Write | 0 | 10² A | no |  |  | NO
Correction courant mesuré | activer ou non la correction de la mesure courant? | word | Read/Write | 0 | - | no |  |  | NO
Simplified mode 3: minimum current threshold | in SM3, the minimum current which is allowed before considering charge end | word | Read/Write | 0 | 10² A | yes |  |  | NO
SM3 : max current allowed | SM3 : max current threshold | word | Read/Write | 0 |  | yes |  |  | NO
Simplified mode 3: minimum time threshold | in SM3, the delay before considering charge end if no more current is given | word | Read/Write | 0 | s | yes |  |  | NO
Time for mean current calculation (0x1005) | Time for mean current calculation (0x1005) | word | Read/Write | 0 | s | no |  |  | NO
EVSE_Status | EVSE_Status | word | Read/Write | 0 | - | no |  |  | NO
CurrentAdjustmentSlope | Slope of linear adjustment function | word | Read/Write | 0 | - | yes |  |  | NO
CurrentAdjustmentOffset | Offset Current for adjustment purpose (y=ax+b) | word | Read/Write | 0 | - | yes |  |  | NO
RawCurrentPhaseA | Phase A Current ADC output value | word | Read | 0 | - | no |  |  | NO
RawCurrentPhaseB | Phase B Current ADC output value | word | Read | 0 | - | no |  |  | NO
RawCurrentPhaseC | Phase C Current ADC output value | word | Read | 0 | - | no |  |  | NO
ChargingTime | How long the contactor have been closed (seconds) during the charging session | 2 words | Read | 0 | s | no |  |  | YES |  | REG_CHARGING_TIME(@13)
DefaultPower | Default on the 24V Power Supply | word | Read/Write | 0 | - | no |  |  | NO
Error Status Word-MSB | Result of internal or communication error check done by EVSE | word | Read/Write | 0x0000 | - | no |  |  | NO
| 0x0000 = OK-NO ERROR-MSW | -
| . Default RFID not found (cannot connect) | bit 0 |  | 0
| . Default Display not found (life bit error) | bit1 |  | 0
| . Default cannot connect to master board | bit2 |  | 0
| . Default incorrect plug un-lock state | bit 3 |  | 0
| . Default incorrect contactor state | bit 4 |  | 0
| . Default incorrect surge arrestor state | bit 5 |  | 0
| . Default incorrect Anti-intrusion state | bit 6 |  | 0
| . Default US DB not found (cannot connect) | bit 7 |  | 0
| . Default configuration error (file or internal eeprom) | bit8 |  | 0
| . Default incorrect shutter un-lock | bit9 |  | 0
| . Default incorrect circuit break state | bit10 |  | 0
| . Default PowerMeter communication lost | bit11 |  | 0
| . Default Under Voltage | bit12 |  | 0
| . Incorrect socket state | bit13 |  | 0
| . Default incorrect Nb phase charging | bit14 |  | 0
| . Default cluster manager communication lost (life bit) | bit15 |  | 0
| 0xFFFF = Unknown Error/Factory error- MSW | -
Error Status Word-LSB | Result of internal or communication error check done by EVSE | word | Read/Write | 0x0000 | - | no |  |  | NO
| 0x0000 = OK-NO ERROR-MSW | -
| . Default Mode3 error (control pilot out of range)- CP error | bit 0 |  | 0
| . Default cable state error (PP error or unplugged after charge) | bit1 |  | 0
| . Default EV disconnected during charge (earth cut) | bit2 |  | 0
| . Default shortcut control pilot (FP1) | bit 3 |  | 0
| . Default overcurrent during charge | bit 4 |  | 0
| . Default no energy available for charge (read from powermeter) | bit 5 |  | 0
| . Default high temperature | bit 6 |  | 0
| . Default weak signal (wireless communication error) | bit 7 |  | 0
| . Energy Reserve Error (Hermes) | bit8 |  | 0
| . Default tilt sensor- cannot read tilt sensor | bit9 |  | 0
| . Default shock- enclosure was shocked | bit10 |  | 0
| . Default shock sensor- cannot read shock sensor | bit11 |  | 0
| . Default service door- cannot read service door sensor | bit12 |  | 0
| . Default Supervision Error- configuration or communication | bit13 |  | 0
| . Reserved | bit14 |  | 0
| . Default system monitor- internal storage or cpu usage error | bit15 |  | 0
| 0xFFFF = Unknown Error/Factory error- LSW | -
RFID Status | Result of authentication request to the PLC or Supervision | word | Read/Write | 0 | - | no |  |  | NO
0- Not Initialized (default value at boot)
1- User Authorized
2- Validate Booking
3- Blacklisted
4- Unknown
5- VIP Authorized
6- Admin Authorized
64- User Added
65- VIP Added
66- Reserved
69- Add Failure: Already known
70- Add Failure: Database is Full
96- User Removed
97- VIP Removed
98- Reserved
99- Removal failure: badge doesn't exit in DB
0xFE- Add/Remove Failure
0xFF- Undefined
IPAddressBase | Base register for network IP distribution | 2 word | Read/Write | 0 | - | yes |  |  | NO
master: set next 0 bit if a new slave board is up corresponding bit only
slave: set own IP corresponding bit from master
ResetSettings | return to factory settings (IP, current, config, etc) | word | Read/Write | 0 | - | no |  |  | NO
StateFDelayPwmOff | delay in state F before starting PWM | word | Read/Write | 0 | s | no |  |  | NO
OperatingMode | Global charging Mode | word | Read/Write | 1 | - | no |  |  | NO
0- slave mode (charge controlled by PLC)
1- autonomous mode (no RFID, no Screen)
2- autonomous mode (RFID, no Screen)
3- autonomous mode (no RFID, Screen)
4- autonomous mode (RFID, Screen)
0xFE- disabled (US daughter board charging)
Output for VE management
ImaxEV | Maximum current available for the EV. | word | Read | 0 | A | no |  |  | NO
(min of ImaxCard, ImaxCable, IMaxPLC or active mode3 simplified 6A limitation)
CyclicRateCPW1 | PWM CPW1 cyclic rate in percent. | word | Read | 0 | - | no |  |  | YES |  | REG_PWM_STATUS(@31)
Count | Wh pulse counter | word | Read | 0 | - | no |  |  | NO
BootCounter | system boot counter notification (increment at each boot) | word | Read | 0 | - | yes |  |  | NO
Other Input / Output state
DI1-16 | Digital Input States | word | Read | 0 | - | no |  |  | NO
| · DI1 state | bit 0 |  | 0 |  |  | BP n° 1 | 1
| · DI2 state | bit1 |  | 0 |  |  | BP n° 2 | 2
| · DI3 state | bit2 |  | 0 |  |  | BP n° 3 | 3
| · DI4 state | bit 3 |  | 0 |  |  | Retour dé-verrouillage Prise | 4
| · DI5 state | bit 4 |  | 0 |  |  | retour contacteur | 5
| · DI6 state | bit 5 |  | 0 |  |  | Etat parafoudre | 6
| · DI7 state | bit 6 |  | 0 |  |  | Anti-intrusion | 7
| · DI8 state | bit 7 |  | 0 |  |  | Detection VE | 8
| · DI9-state | bit 8 |  | 0 |  |  | Retour cde acces / Postion haute Plot | 9 | NO
| · DI10 state | bit9 |  | 0 |  |  | Retour verrouillage Shutter | 10
| · DI11 state | bit 10 |  | 0 |  |  | Retour disj./ diff | 11
| · DI12 state | bit 11 |  | 0 |  |  | retour arrêt d'urgence | 12
| · DI13 state | bit 12 |  | 0 |  |  | under voltage | 13
| · DI14 state | bit 13 |  | 0 |  |  | Pulse count / charge delayed | 14
| · DI15 state | bit 14 |  | 0 |  |  | Not used | 15
| · DI16 state | bit 15 |  | 0 |  |  | Not used | 16
Digital Input States
DO1-16 | Digital Output States |  |  |  | -
DO1 | DO1 Command : Voyant prise enclenchée | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO2 | DO2 Command : Voyant BP charge normale | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO3 | DO3 Command : Voyant BP charge rapide | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO4 | DO4 Command : Voyant affichage vert | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO5 | DO5 Command : Voyant affichage orange | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO6 | DO6 Command : Voyant affichage rouge | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO7 | DO7 Command : Voyant BP arrêt de charge | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO8 | DO8 Command : VT autorisé | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO9 | DO9 Command : Plots place parking | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO10 | DO10 Command : command beep | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO11 | DO11 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO12 | DO12 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO13 | DO13 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO14 | DO14 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO15 | DO15 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
DO16 | DO16 Command : | word | Read/Write | 0 |  | no |  |  | NO
0 -> OFF
1 -> ON
2 -> 1 Hz blink
3 -> 2 Hz blink
Relay1 | Relay1 NO: Contactor Command | word | Read/Write | 0 | - | no |  |  | NO
0-> relay not activated
1-> relay actived
Relay2 | Relay 2 NC: Disjoncteur Command (MNX) | word | Read/Write | 0 | - | no |  |  | NO
0-> relay not activated
1-> relay actived
Relay3 | Relay 3 NO: Initial activation socket outlet coil | word | Read/Write | 0 | - | no |  |  | NO
0-> relay not activated
1-> relay actived
Relay4 | Relay 4 NO: Hold activation socket outlet coil | word | Read/Write | 0 | - | no |  |  | NO
0-> relay not activated
1-> relay actived
PwmLed Period | PwmLed period in ms. | word | Read/Write | 500 | ms | no |  |  | NO
Should be a multiple of 500 ms.
500 <= PwmLedPeriod <= 6000
Only effective in ramp mode (PwmLedRiseTime != 0 or PwmLedFallTime != 0)
PwmLed RiseTime | PwmLed rise time in ms. | word | Read/Write | 0 | ms | no |  |  | NO
Should be a multiple of 50 ms.
0 <= PwmLedRiseTime <= 2000
If PwmLedRiseTime == 0 and PwmLedFallTime ==0, PwmLed is continue mode.
Otherwise, PwmLed is in ramp mode.
PwmLed FallTime | PwmLed fall time in ms. | word | Read/Write | 0 | ms | no |  |  | NO
Should be a multiple of 50 ms.
0 <= PwmLedFallTime <= 2000
If PwmLedRiseTime == 0 and PwmLedFallTime ==0, PwmLed is continue mode.
Otherwise, PwmLed is in ramp mode.
PwmLed | Time at maximum of intensity of PwmLed in ms. | word | Read/Write | 0 | ms | no |  |  | NO
MaxTime | Should be a multiple of 50 ms.
0 <= PwmLedMaxTime <= 6000
Only effective in ramp mode (PwmLedRiseTime != 0 or PwmLedFallTime != 0)
PwmLed | Cyclic rate of PWM | word | Read/Write | 0 | - | no |  |  | NO
MaxIntensity | 0 <= PwmLedMaxIntensity <= 100
Only effective in continue mode (PwmLedRiseTime == 0 and PwmLedFallTime == 0)
Buzzer duration 1 | duration of 1st sound of the buzzer | word | Read/Write | 0 | ms | no |  |  | NO
Buzzer silence 1 | duration of silence for 1st sound | word | Read/Write | 0 | ms | no
Buzzer repetition 1 | times 1st sound is played | word | Read/Write | 0 | ms | no
Buzzer frequency 1 | frequency of 1st sound | word | Read/Write | 0 | ms | no
Buzzer duration 2 | duration of 2nd sound of the buzzer | word | Read/Write | 0 | ms | no
Buzzer silence 2 | duration of silence for 1st sound | word | Read/Write | 0 | ms | no
Buzzer repetition 2 | times 1st sound is played | word | Read/Write | 0 | ms | no
Buzzer frequency 2 | frequency of 1st sound | word | Read/Write | 0 | ms | no
Buzzer refesh | set to 1 to start buzzer sound | word | Read/Write | 0 | - | no
USBoardFaultLightState | State of the fault light controlled by the US board | word | Read/Write | 0 | - | no | Can be written only if USBoardFaultLightStatus register = 0. |  | YES |  | REG_FAULT_LIGHT_STATE(@33)
· 0 - Off
· 1 - Steady ON
· 2 - Flashing
USBoardFaultLightStatus | Status of the controllability of the US board fault light | word | Read | 0 | - | no | Not Controllable if US board is experiencing a non-resettable fault. |  | YES |  | REG_FAULT_LIGHT_STATUS(@15)
· 0 - Controllable
· 1 - Not Controllable
FW upgrade commands
FwUpIp | TFTP server ip address. | 2 words | Read/Write | FE00A8C0 | - | yes |  |  | NO
Server | IP addr is always coded with lower byte first, it means that default value192.168.0.254 is the 32-bit double word 0xFE00A8C0. | [7 empty] | NO
| Higher word is in the first word and lower word in second word. So Ip addr is coded : | [7 empty] | NO
| FwUpIpServer register = 0xFE00 | [7 empty] | NO
| FwUpIpServer register +1 = 0xA8C0 | [7 empty] | NO
FwUpCmd | Firmware Update Command : | word | Read/Write | 0 | - | no |  |  | NO
| 0 -> nothing | [7 empty] | NO
| 1 -> download file | [7 empty] | NO
| 2 -> update FW | [7 empty] | NO
| 3 -> update RFID reader | [7 empty] | NO
4 -> updload file
5 -> Update US Daughter Board FW
6-> update STU Display
| 7-> update UID Database | [7 empty] | NO
FwUpStatus | Firmware Update Status : | word | Read | 0 | - | no |  |  | NO
| 0 -> nothing | [7 empty] | NO
| 1-> transfer error – fw file not found | [7 empty] | NO
| 2 -> OK - download SUCCESS | [7 empty] | NO
| 3 -> Fw updating | [7 empty] | NO
| 4-> OK – FW Update SUCCESS | [7 empty] | NO
| 5 -> ERROR - FW Update failed | [7 empty] | NO
| 6 -> RFID reader FW updating | [7 empty] | NO
| 7 -> RFID reader FW update success | [7 empty] | NO
| 8 -> RFID reader FW update failed | [7 empty] | NO
| 9 | [7 empty] | NO
| 10 | [7 empty] | NO
| 11 | [7 empty] | NO
| 12 | [7 empty] | NO
FwUpFile | File to download name. | 16 words | Read/Write | 0 | - | yes |  |  | NO
Name | [8 empty] | NO
Scrutation rapide / polling parameters
RFIDReader Polling SourceAddr | Source Address of first word for RFID reader polling | word | Read/Write | 0x8000 | - | yes |  |  | NO
RFIDReader Polling Length | Length in nb Modbus word (16 bits) for RFID reader polling. NOTE: The valid length should be part of range [1-125]. Out of this range the polling is disable | word | Read/Write | 0 | - | yes |  |  | NO
RFIDReader PollingPeriod | Period in ms for RFID reader polling | word | Read/Write | 100 | ms | yes |  |  | NO
Scrutation rapide / PLC TCP Server parameters
PLC Modbus TCP Server IP Addr | (PLC Modbus TCP server is used by EVSE to notify PLC of change in RFID Reader) - IP address of PLC Modbus TCP server. | 2 words | Read/Write |  | - | yes |  |  | NO
PLC Modbus TCP Server Dest Addr | Destination Address of first word to write RFID reader polling information in PLC modbus table | word | Read/Write |  | - | yes |  |  | NO
PLC Modbus TCP Server Port | Port for PLC modbus communication | word | Read/Write |  | - | yes |  |  | NO
Autonomous mode
Degraded mode configuration | If PLC is disconnected (LifeBit not set during 10 seconds) 0 : open the contactor 1 : keep contactor closed | word | Read/Write | 0 | - | yes |  |  | NO
EVSE parameters (this board!)
EVSE IP address - persistent | Board IP address NOTE : If this register = 0, then board IP address is define by microswitch | 2 words | Read/Write | 0 | - | yes |  |  | NO
EVSE IP Mask - persistent | Board IP Mask NOTE : If "EVSE IP address" register = 0, then board Mask address is define by microswitch | 2 words | Read/Write | 0 | - | yes |  |  | NO
EVSE IP gateway - persistent | Board Gateway address NOTE : If "EVSE IP address" register = 0, then board gateway address is define by microswitch | 2 words | Read/Write | 0 | - | yes |  |  | NO
HMI Memory Exchange | Memory exchange buffer (typically used for PLC <-> HMI communication) | 50 words | Read/Write | 0 | - | no |  |  | NO
Error management
ResetErrorStatusWord | Error Acknowledge. Set ErrorStatusWord to zero when writing in this register | 1 word | Write | 0 | - | no |  |  | NO
Plug management
Plug type | 1 - Type 1 2 - Type 2 - Schuko 3 - Type 3 - Schneider (Default value) 4 - Mennekes | 1 word | Read/Write | 3 | - | no |  |  | NO
StateMachine | · 0 – No active CPW StateMachine | 1 word | Read | 1 | - | no |  |  | NO
| · 1 – Mode 3 CPW StateMachine | [7 empty] | NO
| · 2 – Mode 1/2 CPW StateMachine | [5 empty] | Mode 1/2 : définition ? |  | NO
Time management
Time | Time setting for STU | 4 Words | Read/Write | Version date | - | no |  |  | NO
Note on B690: M. Debarnot: Autres options: - Remettre à zero automatiquement ErrorStatusWord après sa lecture? - Ecrire 0 dans ErrorStatusWord

## ReadOnly Register addr
Format
register | Addr | Parameter | Type | Size | Read/Write
1 | 0 | EventBit | word | 1 | Read
2 | 1 | UpTime - MSB | word | 1 | Read
3 | 2 | UpTime - LSB | word | 1 | Read
4 | 3 | MicroSwitchStatus | word | 1 | Read
5 | 4 | FWVersion Major | word | 1 | Read
6 | 5 | MainState | word | 1 | Read
7 | 6 | CPWState | word | 1 | Read
8 | 7 | CableState | word | 1 | Read
9 | 8 | EVState | word | 1 | Read
10 | 9 | LastChargeStatus | word | 1 | Read
11 | 10 | EVSE_Status | word | 1 | Read
12 | 11 | ImaxCard | word | 1 | Read
13 | 12 | ImaxCable | word | 1 | Read
14 | 13 | InstantCurrentMeasPhaseA | word | 1 | Read
15 | 14 | InstantCurrentMeasPhaseB | word | 1 | Read
16 | 15 | InstantCurrentMeasPhaseC | word | 1 | Read
17 | 16 | ImaxEV | word | 1 | Read
18 | 17 | CyclicRateCPW1 | word | 1 | Read
19 | 18 | DI | word | 1 | Read
20 | 19 | FwUpStatus (RFID) | word | 1 | Read
21 | 20 | Remote Command Status | word | 1 | Read
22 | 21 | CountMSB | word | 1 | Read
23 | 22 | CountLSB | word | 1 | Read
24 | 23 | Error Status MSB | word | 1 | Read
25 | 24 | Error Status LSB | word | 1 | Read
26 | 25 | Commissionning tool Major version | word | 1 | Read
27 | 26 | RawCurrentPhaseA | word | 1 | Read
28 | 27 | RawCurrentPhaseB | word | 1 | Read
29 | 28 | RawCurrentPhaseC | word | 1 | Read
30 | 29 | StateMachine | word | 1 | Read
31 | 30 | ChargingTime | word | 2 | Read
33 | 32 | RFIDFWVersion | word | 2 | Read
35 | 34 | LastChargeStatus-1 | word | 1 | Read
36 | 35 | LastChargeStatus-2 | word | 1 | Read
37 | 36 | LastChargeStatus-3 | word | 1 | Read
38 | 37 | LastChargeStatus-4 | word | 1 | Read
39 | 38 | USBoardGFTimeUntilReset | word | 1 | Read
40 | 39 | USBoardAutoResetCount | word | 1 | Read
41 | 40 | USBoardContactErrorCount | word | 1 | Read
42 | 41 | USBoardFaultLightStatus | word | 1 | Read
43 | 42 | USBoardFWVersion | word | 2 | Read
45 | 44 | USBoardFWChecksum | word | 1 | Read
46 | 45 | BootCounter | word | 1 | Read
47 | 46 | ImaxUser | word | 1 | Read
48 | 47 | UnexpectedContactorOpenCount | word | 1 | Read
49 | 48 | CyclicRateCPW1Progressive | word | 1 | Read
50 | 49 | EVSE FW Minor version | word | 1 | Read
51 | 50 | Commissionning tool Minor version | word | 1 | Read
52 | 51 | ChargeStatus | word | 1 | Read
53 | 52 | ChargeStatusLastError | word | 1 | Read
54 | 53 | SelectedChargePower | word | 1 | Read
55 | 54 | SelectedChargeDuration | word | 1 | Read
56 | 55 | Component FW Major version | word | 1 | Read
57 | 56 | Component FW Minor version | word | 1 | Read

## ReadWrite Register addr
|  |  | Format |  |  | Remarque
register | Addr | Parameter | Type | Size | Read/Write
65 | 64 | LifeBit | word | 1 | Read/Write
66 | 65 | Reboot | word | 1 | Read/Write
67 | 66 | EVSE_Management | word | 1 | Read/Write
68 | 67 | IMaxPLC | word | 1 | Read/Write
69 | 68 | CurrentMonitoringMode | word | 1 | Read/Write
70 | 69 | InstantCurrentGivenPhaseA | word | 1 | Read/Write
71 | 70 | InstantCurrentGivenPhaseB | word | 1 | Read/Write
72 | 71 | InstantCurrentGivenPhaseC | word | 1 | Read/Write
73 | 72 | DO1-Voyant prise enclenché | word | 1 | Read/Write
74 | 73 | DO2-Voyants BP charge normale | word | 1 | Read/Write
75 | 74 | DO3-Voyants BP charge rapide | word | 1 | Read/Write
76 | 75 | DO4-Voyant affichage vert | word | 1 | Read/Write
77 | 76 | DO5-Voyant affichage orange | word | 1 | Read/Write
78 | 77 | DO6-Voyant affichage rouge | word | 1 | Read/Write
79 | 78 | DO7-VE autorisé | word | 1 | Read/Write
80 | 79 | DO8-VT autorisé | word | 1 | Read/Write
81 | 80 | DO9- Command plots place parking | word | 1 | Read/Write
82 | 81 | DO10-Commande beep | word | 1 | Read/Write
83 | 82 | DO11- Not used | word | 1 | Read/Write
84 | 83 | DO12- Not used | word | 1 | Read/Write
85 | 84 | DO13- Not used | word | 1 | Read/Write
86 | 85 | DO14- Not used | word | 1 | Read/Write
87 | 86 | DO15- Not used | word | 1 | Read/Write
88 | 87 | DO16 - Not used | word | 1 | Read/Write
89 | 88 | Relay1 | word | 1 | Read/Write
90 | 89 | Reserved | word | 1 | Read/Write
91 | 90 | Relay3 | word | 1 | Read/Write
92 | 91 | Relay4 | word | 1 | Read/Write
93 | 92 | PwmLedPeriod | word | 1 | Read/Write
94 | 93 | PwmLedRiseTime | word | 1 | Read/Write
95 | 94 | PwmLedFallTime | word | 1 | Read/Write
96 | 95 | PwmLedMaxTime | word | 1 | Read/Write
97 | 96 | PwmLedMaxIntensity | word | 1 | Read/Write
98 | 97 | PwmLedRefresh | word | 1 | Read/Write
99 | 98 | Reserved | word | 4 | Read/Write
103 | 102 | FwUpIpServer - LSB | word | 1 | Read/Write
104 | 103 | FwUpIpServer - MSB | word | 1 | Read/Write
105 | 104 | FwUpCmd | word | 1 | Read/Write
106 | 105 | FwUpFileName | word | 16 | Read/Write
122 | 121 | HWReference-MSW | word | 2 | Read/Write
124 | 123 | HWReference-LSW | word | 2 | Read/Write
126 | 125 | CurrentAdjustementScale | word | 1 | Read/Write
127 | 126 | CurrentAdjustmentSlope | word | 1 | Read/Write
128 | 127 | CurrentAdjustmentOffset | word | 1 | Read/Write
129 | 128 | Time | word | 4 | Read/Write
133 | 132 | Buzzer sound 1 | word | 1 | Read/Write
134 | 133 | Buzzer silence 1 | word | 1 | Read/Write
135 | 134 | Buzzer repetition 1 | word | 1 | Read/Write
136 | 135 | Buzzer frequency 1 | word | 1 | Read/Write
137 | 136 | Buzzer sound 2 | word | 1 | Read/Write
138 | 137 | Buzzer silence 2 | word | 1 | Read/Write
139 | 138 | Buzzer repetition 2 | word | 1 | Read/Write
140 | 139 | Buzzer frequency 2 | word | 1 | Read/Write
141 | 140 | Buzzer refesh | word | 1 | Read/Write
142 | 141 | Serial Conf | word | 1 | Read/Write
143 | 142 | StateFDelayPWMOFF | word | 1 | Read/Write
144 | 143 | EVSE IP Refresh | word | 1 | Read/Write
145 | 144 | RFID Status | word | 1 | Read/Write
146 | 145 | EVChargeTimeout | word | 1 | Read/Write
147 | 146 | StateFDelayPWMON | word | 1 | Read/Write
148 | 147 | Simplified mode 3: maximum current threshold | word | 1 | Read/Write
149 | 148 | Update configuration file | word | 1 | Read/Write
150 | 149 | Reserved | word | 1 | Read/Write
151 | 150 | Remote_command | word | 1 | Read/Write
152 | 151 | PLC ChargingStationBaseAddress | word | 1 | Read/Write
153 | 152 | PLC ChargingPointBaseAddress | word | 1 | Read/Write
154 | 153 | DisplayFWVersion | word | 1 | Read/Write
155 | 154 | PLCFWVersion | word | 1 | Read/Write
156 | 155 | Reserved | word | 5 | Read/Write
161 | 160 | IPServerBase | word | 2 | Read/Write
163 | 162 | ResetSettings | word | 1 | Read/Write
164 | 163 | Reserved | word | 1 | Read/Write
165 | 164 | Operating Mode | word | 1 | Read/Write
166 | 165 | ResetLastChargeStatus | word | 1 | Read/Write
167 | 166 | USBoardGFAutoResetTimeSetting | word | 1 | Read/Write
168 | 167 | USBoardSelfTestRequest | word | 1 | Read/Write
169 | 168 | USBoardFaultLightState | word | 1 | Read/Write
170 | 169 | RFIDReader Polling SourceAddr | word | 1 | Read/Write
171 | 170 | RFIDReader Polling Length | word | 1 | Read/Write
172 | 171 | RFIDReader Polling Period | word | 1 | Read/Write
173 | 172 | PLC Modbus TCP Server IP | word | 2 | Read/Write
175 | 174 | PLC Modbus TCP Server DestAddr | word | 1 | Read/Write
176 | 175 | Degraded mode configuration | word | 1 | Read/Write
177 | 176 | EVSE IP address | word | 2 | Read/Write
179 | 178 | EVSE IP Mask | word | 2 | Read/Write
181 | 180 | EVSE IP gateway | word | 2 | Read/Write
183 | 182 | EVSE IP DNS | word | 2 | Read/Write
185 | 184 | RAZ count | word | 1 | Read/Write
186 | 185 | Time for mean current calculation | word | 1 | Read/Write
187 | 186 | Simplified mode 3: minimum current threshold | word | 1 | Read/Write
188 | 187 | Simplified mode 3: minimum time threshold | word | 1 | Read/Write
189 | 188 | Time for mean current calculation (0x1005) | word | 1 | Read/Write
190 | 189 | CCVE_EVSE_Status | word | 1 | Read/Write
191 | 190 | PortPLC | word | 1 | Read/Write
192 | 191 | Reserved | word | 13 | Read/Write
205 | 204 | Stop_carte | word | 1 | Read/Write
206 | 205 | Terminal_version | word | 1 | Read/Write
207 | 206 | HMI exchange memory start | word | 50 | Read/Write
255

## Factory
Addr | Register | Type | Size | Access
121 | HWReference-MSW | word | 2 | Read
123 | HWReference-LSW | word | 2 | Read
512 | Serial Number | word | 26 | Read
600 | Product Reference | word | 50 | Read

## Energy Management
Addr | Register | Type | Size | Access
300 | Energy Management Setting | word | 1 | Read/Write
301 | SocketRemoteSetPoint | word | 1 | Read/Write
302 | Home Upstream Protection(ImaxInstall) | word | 1 | Read/Write
303 | CP Upstream Protection | word | 1 | Read/Write
304 | Monophased load shedding floor value | word | 1 | Read/Write
305 | Triphased load shedding floor value | word | 1 | Read/Write
306 | Monophased maximum power | word | 1 | Read/Write
307 | Tri phased maximum power | word | 1 | Read/Write
308 | Maximum charge duration | word | 1 | Read/Write
309 | Maximum authorized energy | word | 1 | Read/Write
310 | StationRemoteSetPoint | word | 1 | Read/Write
311 | Reserved | word | 9 | Read
320 | HeadMeter Phase1Current_I1 | word | 2 | Read
322 | HeadMeter Phase2Current_I2 | word | 2 | Read
324 | HeadMeter Phase3Current_I3 | word | 2 | Read
326 | HeadMeter ActiveEnergy | word | 2 | Read
328 | HeadMeter ActivePowerTotal | word | 2 | Read
330 | HeadMeter L1_L2 Voltage | word | 2 | Read
332 | HeadMeter L2_L3 Voltage | word | 2 | Read
334 | HeadMeter L3_L1 Voltage | word | 2 | Read
336 | HeadMeter L1_N Voltage | word | 2 | Read
338 | HeadMeter L2_N Voltage | word | 2 | Read
340 | HeadMeter L3_N Voltage | word | 2 | Read
342 | Reserved | word | 8 | Read
350 | StationMeter Phase1Current_I1 | word | 2 | Read
352 | StationMeter Phase2Current_I2 | word | 2 | Read
354 | StationMeter Phase3Current_I3 | word | 2 | Read
356 | StationMeter ActiveEnergy | word | 2 | Read
358 | StationMeter ActivePowerTotal | word | 2 | Read
360 | StationMeter L1_L2 Voltage | word | 2 | Read
362 | StationMeter L2_L3 Voltage | word | 2 | Read
364 | StationMeter L3_L1 Voltage | word | 2 | Read
366 | StationMeter L1_N Voltage | word | 2 | Read
368 | StationMeter L2_N Voltage | word | 2 | Read
370 | StationMeter L3_N Voltage | word | 2 | Read
372 | Reserved | word | 8 | Read
380 | AlternativeMeter Phase1Current_I1 | word | 2 | Read
382 | AlternativeMeter Phase2Current_I2 | word | 2 | Read
384 | AlternativeMeter Phase3Current_I3 | word | 2 | Read
386 | AlternativeMeter ActiveEnergy | word | 2 | Read
388 | AlternativeMeter ActivePowerTotal | word | 2 | Read
390 | AlternativeMeter L1_L2 Voltage | word | 2 | Read
392 | AlternativeMeter L2_L3 Voltage | word | 2 | Read
394 | AlternativeMeter L3_L1 Voltage | word | 2 | Read
396 | AlternativeMeter L1_N Voltage | word | 2 | Read
398 | AlternativeMeter L2_N Voltage | word | 2 | Read
400 | AlternativeMeter L3_N Voltage | word | 2 | Read
402 | Reserved | word | 98 | Read

## GreenPark
Format
register | Addr | Parameter | Type | Size | Read/Write
1551 | 1550 | Contract ID | word | 2 | RW
1553 | 1552 | MaxDuration2kW | word | 1 | RW
1554 | 1553 | MaxDuration3kW | word | 1 | RW
1555 | 1554 | MaxDuration7kW | word | 1 | RW
1556 | 1555 | MaxDuration11kW | word | 1 | RW
1557 | 1556 | MaxDuration22kW | word | 1 | RW
1558 | 1557 | MaxDuration43kW | word | 1 | RW
1559 | 1558 | MaxDuration50W | word | 1 | RW
1560 | 1559 | Reserved | word | 41 | RW

## Supervision
Addr | Register | Type | Size | Access
932 | Remote Manager lifebit | word | 1 | RW
933 | RemoteManager status | word | 1 | RW
934 | Remote authent manager lifebit | word | 1 | RW
935 | Remote authent manager status | word | 1 | R
936 | Reserved | word | 64 | RW
1000 | Time SERVER URL /IP Address | word | 50 | RW
1050 | Timezone | word | 50 | RW
1100 | Reserved | word | 100 | RW
1200 | Supervision URL /IP Address | word | 50 | RW
1250 | Authentication SERVER URL /IP Address | word | 50 | RW
1300 | HTTP Proxy URL/IP Address | word | 50 | RW
1350 |  | word | 170 | RW
1520 | Remote Authent UID | word | 8 | RW
1528 | Remote user type | word | 1 | RW
1529 | Reservation Connector ID | word | 1 | RW
1530 | Reservation ID | word | 2 | RW
1532 | Reservation duration | word | 1 | RW
1533 | Reservation status | word | 1 | R
1534 | Reserved |  | 16

## History
Addr | Register | Description | Type | Size | Acces | Min value | Max value | Default Value | Unit | Non Volatile Memory | Notes
1600 | PreviousError0 start time (s) |  | word | 2 | Read
1602 | PreviousError0 end time (s) |  | word | 2 | Read
1604 | PreviousError0 code |  | word | 1 | Read | 0 | 32 | 0 | - | yes
1605 | Reserved |  | word | 10 | Read
1615 | PreviousError1 start time (s) |  | word | 2 | Read
1617 | PreviousError1 end time (s) |  | word | 2 | Read
1619 | PreviousError1 code |  | word | 1 | Read | 0 | 32 | 0 | - | yes
1620 | Reserved |  | word | 10 | Read
1630 | PreviousError2 start time (s) |  | word | 2 | Read
1632 | PreviousError2 end time (s) |  | word | 2 | Read
1634 | PreviousError2 code |  | word | 1 | Read | 0 | 32 | 0 | - | yes
1635 | Reserved |  | word | 10 | Read
1645 | PreviousError3 start time (s) |  | word | 2 | Read
1647 | PreviousError3 end time (s) |  | word | 2 | Read
1649 | PreviousError3 code |  | word | 1 | Read | 0 | 32 | 0 | - | yes
1650 | Reserved |  | word | 10 | Read
1660 | PreviousError4 start time (s) |  | word | 2 | Read
1662 | PreviousError4 end time (s) |  | word | 2 | Read
1664 | PreviousError4 code |  | word | 1 | Read | 0 | 32 | 0 | - | yes
1665 | Reserved |  | word | 335 | Read
2000 | CurrentCharge start time |  | word | 2 | Read
2002 | CurrentCharge end time |  | word | 2 | Read
2004 | CurrentCharge duration |  | word | 2 | Read
2006 | CurrentCharge station energy table |  | word | 60 | Read
2066 | CurrentCharge alt energy table |  | word | 60 | Read
2126 | CurrentCharge station total energy |  | word | 2 | Read
2128 | CurrentCharge alt total energy |  | word | 2 | Read
2130 | CurrentCharge ID | ID of the current charge session | word | 8 | Read
2138 | CurrentCharge Nominal Power | Nominal Power of the current charge | word | 2 | Read
2140 | Reserved |  | word | 60 | Read
2200 | LastCharge start time |  | word | 2 | Read
2202 | LastCharge end time |  | word | 2 | Read
2204 | LastCharge duration |  | word | 2 | Read
2206 | LastCharge station energy table |  | word | 60 | Read
2266 | LastCharge alt energy table |  | word | 60 | Read
2326 | LastCharge station total energy |  | word | 2 | Read
2328 | LastCharge alt total energy |  | word | 2 | Read
2330 | LastCharge ID | ID of the previous charge session | word | 8 | Read
2338 | LastCharge Nominal Power | Nominal Power of the current charge | word | 2 | Read
2340 | Reserved |  | word | 60 | Read
2400 | History start time |  | word | 2 | Read
2402 | History end time |  | word | 2 | Read
2404 | History duration |  | word | 2 | Read
2406 | History station energy table |  | word | 60 | Read
2466 | History alt energy table |  | word | 60 | Read
2526 | History station total energy |  | word | 2 | Read
2528 | History alt total energy |  | word | 2 | Read
2530 | History ID | ID of the owner of history data | word | 8 | Read
2538 | History Nominal Power | Nominal Power of the history data | word | 2 | Read

## Time Setting
address | Register | Description | Type | Size | Acces | Min value | Max value | Default Value | Unit | Non Volatile Memory | Notes
Update date and time
900 | new year | year to set | word | 1 | RW | 2013 | 2099 | 0 | - | yes | ADDR_EDIT_YEAR
901 | new month | month to set | word | 1 | RW | 1 | 12 | 0 | - | yes | ADDR_EDIT_MONTH
902 | new month day | month day to set | word | 1 | RW | 1 | 31 | 0 | - | yes | ADDR_EDIT_MONTHDAY
903 | new week day | week day to set | word | 1 | RW | 1 | 7 | 0 | - | yes | ADDR_EDIT_WEEKDAY
904 | new hour | hour to set | word | 1 | RW | 0 | 24 | 0 | - | yes | ADDR_EDIT_HOUR
905 | new minute | minute to set | word | 1 | RW | 0 | 59 | 0 | - | yes | ADDR_EDIT_MINUTE
906 | new second | seconds to set | word | 1 | RW | 0 | 59 | 0 | - | yes | ADDR_EDIT_SECOND
907 | year | current year | word | 1 | R | 2013 | 2099 | 0 | - | no | ADDR_CURRENT_YEAR
908 | month | current month | word | 1 | R | 1 | 12 | 0 | - | no | ADDR_CURRENT_MONTH
909 | month day | current month day | word | 1 | R | 1 | 31 | 0 | - | no | ADDR_CURRENT_MONTHDAY
910 | week day | current week day | word | 1 | R | 1 | 7 | 0 | - | no | ADDR_CURRENT_WEEKDAY
911 | hour | current hour | word | 1 | R | 0 | 24 | 0 | - | no | ADDR_CURRENT_HOUR
912 | minute | current minute | word | 1 | R | 0 | 59 | 0 | - | no | ADDR_CURRENT_MINUTE
913 | second | current second | word | 1 | R | 0 | 59 | 0 | - | no | ADDR_CURRENT_SECOND
914 | time settings mode | 0: manual | word | 1 | RW | 0 | 1 | 0 | - | yes | ADDR_TIME_MODE
1: auto (timeserver)
915 | reserved | reserved | reserved | 1 | reserved | reserved | reserved | reserved | reserved | reserved | reserved
Time Server
1000 | Time server addr | URL/IP of time server | word | 100 | RW | - | - | - | - | yes | ADDR_TIME_SERVER
1050 | Timezone | new timezone to apply | String | 40 | RW | - | - | - | - | yes | ADDR_TIMEZONE

## Control
address | Register | Description | Type | Size | Acces | Min value | Max value | Default Value | Unit | Non Volatile Memory | Notes
701 | validate | 0:NONE_ACK | word | 1 | RW | 0 | 15 | 0 | - | no | ADDR_VALIDATE
[7 empty] | 1 |  | - | no
[7 empty] | 1 |  | - | no
7:validate time settings (OK_TIME_CHANGE)
|  | 15: back to factory (OK_RESTORE_FACTORY) |  |  |  |  | 1 |  | - | no
0 | validate return code | status of config or user changes by HMI | word | 1 | RW | 0 | 65535 | 0 | - | no | ADDR_RETURN_CODE
0:OK- no error
bit0: login error (incorrect password)
bit1: edit error - database is full
bit2: edit error - database is empty
bit3: edit error - incorrect user type
bit4: edit error - invalid password or mismatch
bit5: edit error - invalid email address?
bit6: edit error - internal db error
bit7-12: reserved
bit13: recover error (recover password failed)
bit14: restore error (reset settings or users failed)
bit15: configuration error (commissionning failed)