## Feuil1
Coordination Type 1 with Fuse according to IEC 60947-4-1 and IEC 60947-4-2
|  | 230 Vac Power supply, In line (1) | [7 empty] | 380 / 400 / 415 Vac Power supply | [7 empty] | 440 Vac Power supply | [7 empty] | 500 Vac Power supply | [7 empty] | 690 Vac Power supply
|  | In line | [7 empty] | In line | [7 empty] | In line | [7 empty] | In line | [7 empty] | In line
Soft Starter |  | Motor | Combination Iq | Type switch fuse disconnector (bare unit) | aM fuses |  |  | Line Contactor | Bypass contactor | Motor | Combination Iq | Type switch fuse disconnector (bare unit) | aM fuses |  |  | Line Contactor | Bypass contactor | Motor | Combination Iq | Type switch fuse disconnector (bare unit) | aM fuses |  |  | Line Contactor | Bypass contactor | Motor | Combination Iq | Type switch fuse disconnector (bare unit) | aM fuses |  |  | Line Contactor | Bypass contactor | Motor | Combination Iq | Type switch fuse disconnector (bare unit) | aM fuses |  |  | Line Contactor | Bypass contactor
Normal duty | Heavy duty |  |  |  | Unit reference (2) | [7 empty] | Unit reference (2) | [7 empty] | Unit reference (2) | [7 empty] | Unit reference (2) | [7 empty] | Unit reference (2)
[5 empty] | without stricker | with stricker | (w x l) | [5 empty] | without stricker | with stricker | (w x l) | [5 empty] | without stricker | with stricker | (w x l) | [5 empty] | without stricker | with stricker | (w x l) | [5 empty] | without stricker | with stricker | (w x l)
Class 10 | Class 20 | kW | kA | Reference | Reference | Reference | Size | Reference | Reference | kW | kA | Reference | Reference | Reference | Size | Reference | Reference | kW | kA | Reference | Reference | Reference | Size | Reference | Reference | kW | kA | Reference | Reference | Reference | Size | Reference | Reference | kW | kA | Reference | Reference | Reference | Size | Reference | Reference
NA | ATS480D17Y | 3 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D18 | LC1D18 | 5.5 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D18 | LC1D18 | 5.5 | 100 | LS1D32 | DF2CA16 | - | 10 x 38 | LC1D12 | LC1D12 | 7.5 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D40A | LC1D40A | 11 | 100 | GS1K | DF2EA16 | DF3EA16 | 22 x 58 | LC1D40A | LC1D40A
ATS480D17Y | ATS480D22Y | 4 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D18 | LC1D18 | 7.5 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D18 | LC1D18 | 7.5 | 100 | LS1D32 | DF2CA16 | - | 10 x 38 | LC1D18 | LC1D18 | 9 | 100 | LS1D32 | DF2CA16 | - | 10x38 | LC1D40A | LC1D40A | 15 | 100 | GS1K | DF2EA20 | DF3EA20 | 22 x 58 | LC1D40A | LC1D40A
ATS480D22Y | ATS480D32Y | 5.5 | 100 | LS1D32 | DF2CA25 | - | 10x38 | LC1D25 | LC1D25 | 11 | 100 | LS1D32 | DF2CA25 | - | 10x38 | LC1D25 | LC1D25 | 11 | 100 | GK1EK | DF2EA25 | DF3EA25 | 14 x 51 | LC1D25 | LC1D25 | 11 | 100 | GK1EK | DF2EA25 | DF3EA25 | 14x51 | LC1D40A | LC1D40A | 18.5 | 100 | GS1K | DF2EA25 | DF3EA25 | 22 x 58 | LC1D40A | LC1D40A
ATS480D32Y | ATS480D38Y | 7.5 | 100 | GK1EK | DF2EA32 | DF3EA32 | 14x51 | LC1D32 | LC1D32 | 15 | 100 | GK1EK | DF2EA32 | DF3EA32 | 14x51 | LC1D32 | LC1D32 | 15 | 100 | GK1EK | DF2EA32 | DF3EA32 | 14 x 51 | LC1D40A | LC1D40A | 18.5 | 100 | GK1EK | DF2EA32 | DF3EA32 | 14x51 | LC1D40A | LC1D40A | 22 | 100 | GS1K | DF2EA32 | DF3EA32 | 22 x 58 | LC1D40A | LC1D40A
ATS480D38Y | ATS480D47Y | 9 | 100 | GK1EK | DF2EA40 | DF3EA40 | 14x51 | LC1D38 | LC1D38 | 18.5 | 100 | GK1EK | DF2EA40 | DF3EA40 | 14x51 | LC1D40A | LC1D40A | 18.5 | 100 | GK1EK | DF2EA40 | DF3EA40 | 14 x 51 | LC1D40A | LC1D40A | 22 | 100 | GK1EK | DF2EA40 | DF3EA40 | 14x51 | LC1D50A | LC1D50A | 30 | 100 | GS1K | DF2EA40 | DF3EA40 | 22 x 58 | LC1D40A | LC1D40A
ATS480D47Y | ATS480D62Y | 11 | 100 | GS1K | DF2FA50 | DF3FA50 | 22X58 | LC1D50A | LC1D50A | 22 | 100 | GS1K | DF2FA50 | DF3FA50 | 22X58 | LC1D50A | LC1D50A | 22 | 100 | GS1K | DF2FA50 | DF3FA50 | 22 x 58 | LC1D40A | LC1D40A | 30 | 100 | GS1K | DF2FA50 | DF3FA50 | 22X58 | LC1D50A | LC1D50A | 37 | 100 | GS1K | DF2FA50 | DF3FA50 | 22 x 58 | LC1D65A | LC1D65A
ATS480D62Y | ATS480D75Y | 15 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D65A | LC1D65A | 30 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D65A | LC1D65A | 30 | 100 | GS1K | DF2FA80 | DF3FA80 | 22 x 58 | LC1D65A | LC1D65A | 37 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D65A | LC1D65A | 45 | - | - | - | - | - | - | -
ATS480D75Y | ATS480D88Y | 18.5 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D80 | LC1D80 | 37 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D80 | LC1D80 | 37 | 100 | GS1K | DF2FA80 | DF3FA80 | 22 x 58 | LC1D65A | LC1D65A | 45 | 100 | GS1K | DF2FA80 | DF3FA80 | 22X58 | LC1D80 | LC1D80 | 55 | - | - | - | - | - | - | -
ATS480D88Y | ATS480C11Y | 22 | 100 | GS1K | DF2FA100 | DF3FA100 | 22X58 | LC1D115 | LC1D115 | 45 | 100 | GS1K | DF2FA100 | DF3FA100 | 22X58 | LC1D115 | LC1D115 | 45 | 100 | GS1K | DF2FA100 | DF3FA100 | 22 x 58 | LC1D80 | LC1D80 | 55 | 100 | GS1K | DF2FA100 | DF3FA100 | 22X58 | LC1D80 | LC1D80 | 75 | - | - | - | - | - | - | -
ATS480C11Y | ATS480C14Y | 30 | 100 | GS1K | DF2FA125 | DF3FA125 | 22X58 | LC1D115 | LC1D115 | 55 | 100 | GS1K | DF2FA125 | DF3FA125 | 22X58 | LC1D115 | LC1D115 | 55 | 100 | GS1L | DF2GA125 | DF4GA125 | 0 | LC1D115 | LC1D115 | 75 | 100 | GS1L | DF2GA1121 | DF4GA121 | 0 | LC1D150 | LC1D150 | 90 | - | - | - | - | - | - | -
ATS480C14Y | ATS480C17Y | 37 | 100 | GS1L | DF2GA1161 | DF4GA1161 | 0 | LC1D150 | LC1D150 | 75 | 100 | GS1L | DF2GA1161 | DF4GA1161 | 0 | LC1D150 | LC1D150 | 75 | 100 | GS1L | DF2GA1161 | DF4GA1161 | 1 | LC1D150 | LC1D150 | 90 | 100 | GS1L | DF2GA1161 | DF4GA1161 | 0 | LC1D150 | LC1D150 | 110 | - | - | - | - | - | - | -
ATS480C17Y | ATS480C21Y | 45 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G185 | LC1G185 | 90 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G185 | LC1G185 | 90 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G150 | LC1G150 | 110 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G185 | LC1G185 | 160 | - | - | - | - | - | - | -
ATS480C21Y | ATS480C25Y | 55 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G225 | LC1G225 | 110 | 100 | GS1N | DF2HA1201 | DF4HA1201 | 1 | LC1G225 | LC1G225 | 110 | 100 | GS1N | DF2JA1251 | DF4JA1251 | 1 | LC1G185 | LC1G185 | 132 | 100 | GS1N | DF2HA1251 | DF4HA1251 | 1 | LC1G225 | LC1G225 | 200 | - | - | - | - | - | - | -
ATS480C25Y | ATS480C32Y | 75 | 100 | GS1QQ | DF2JA1251 | DF4JA1251 | 2 | LC1G265 | LC1G265 | 132 | 100 | GS1QQ | DF2JA1251 | DF4JA1251 | 2 | LC1G265 | LC1G265 | 132 | 100 | GS1QQ | DF2JA1311 | DF4JA1311 | 2 | LC1G225 | LC1G225 | 160 | 100 | GS1QQ | DF2JA1311 | DF4JA1311 | 2 | LC1G265 | LC1G265 | 250 | - | - | - | - | - | - | -
ATS480C32Y | ATS480C41Y | 90 | 100 | GS1QQ | DF2JA1311 | DF4JA1311 | 2 | LC1G330 | LC1G330 | 160 | 100 | GS1QQ | DF2JA1311 | DF4JA1311 | 2 | LC1G330 | LC1G330 | 160 | 100 | GS1QQ | DF2JA1311 | DF4JA1311 | 2 | LC1G265 | LC1G265 | 220 | 100 | GS1QQ | DF2JA1401 | DF4JA1401 | 2 | LC1G400 | LC1G400 | 315 | - | - | - | - | - | - | -
ATS480C41Y | ATS480C48Y | 110 | 100 | GS1S | DF2KA1401 | DF4KA1401 | 3 | LC1G400 | LC1G400 | 220 | 100 | GS1S | DF2KA1401 | DF4KA1401 | 3 | LC1G400 | LC1G400 | 220 | 100 | GS1S | DF2KA1501 | DF4KA1501 | 3 | LC1G400 | LC1G400 | 250 | 100 | GS1S | DF2KA1501 | DF4KA1501 | 3 | LC1G400 | LC1G400 | 400 | - | - | - | - | - | - | -
ATS480C48Y | ATS480C59Y | 132 | 100 | GS1S | DF2KA1501 | DF4KA1501 | 3 | LC1G500 | LC1G500 | 250 | 100 | GS1S | DF2KA1501 | DF4KA1501 | 3 | LC1G500 | LC1G500 | 250 | 100 | GS1S | DF2KA1501 | DF4KA1501 | 3 | LC1G400 | LC1G400 | 315 | 100 | GS1S | DF2KA1631 | DF4KA1631 | 3 | LC1G500 | LC1G500 | 500 | - | - | - | - | - | - | -
ATS480C59Y | ATS480C66Y | 160 | 100 | GS1S | DF2KA1631 | DF4KA1631 | 3 | LC1G630 | LC1G630 | 315 | 100 | GS1S | DF2KA1631 | DF4KA1631 | 3 | LC1G630 | LC1G630 | 355 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G630 | LC1G630 | 400 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G800 | LC1G800 | 560 | - | - | - | - | - | - | -
ATS480C66Y | ATS480C79Y | 200 | 100 | GS1S | DF2KA1631 | DF4KA1631 | 3 | LC1G630 | LC1G630 | 355 | 100 | GS1V | DF2LlA1631 | DF4LA1631 | 4 | LC1G630 | LC1G630 | 400 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G630 | LC1G630 | 450 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G800 | LC1G800 | 630 | - | - | - | - | - | - | -
ATS480C79Y | ATS480M10Y | 220 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G800 | LC1G800 | 400 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G800 | LC1G800 | 500 | 100 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1G800 | LC1G800 | 500 | 42 | GS1V | DF2LA1801 | DF4LA1801 | 4 | LC1F2600 | LC1F2600 | 710 | - | - | - | - | - | - | -
ATS480M10Y | ATS480M12Y | 250 | 100 | GS1V | DF2LA1101 | DF4LA1101 | 4 | LC1F1000 | LC1F1000 | 500 | 100 | GS1V | DF2LA1101 | DF4LA1101 | 4 | LC1F1000 | LC1F1000 | 630 | 100 | GS1V | DF2LA1101 | DF4LA1101 | 4 | LC1F1000 | LC1F1000 | 630 | 42 | GS1V | DF2LA1101 | DF4LA1101 | 4 | LC1F2600 | LC1F2600 | 900 | - | - | - | - | - | - | -
ATS480M12Y | NA | 355 | 42 | - | DF2LA1251 | DF4LA1251 | 4 | LC1F2600 | LC1F2600 | 630 | 42 | - | DF2LA1251 | DF4LA1251 | 4 | LC1F2600 | LC1F2600 | 710 | 42 | - | DF2LA1251 | - | 4 | LC1F2600 | LC1F2600 | 800 | 42 | - | DF2LA1251 | - | 4 | LC1F2600 | LC1F2600 | 950 | - | - | - | - | - | - | -