## Sheet1
Device type: VAMP 265 |  |  | Transformer mode
Program version: V10.108
Note: Data lists are customizable.
Possible data items for each category of data is listed below the default mappings.
DNP3
Binary Inputs
Idx | Class | UR | Item
0 | 1 | 0 | VI1
1 | 1 | 0 | DI2
2 | 1 | 0 | DI3
3 | 1 | 0 | DI4
4 | 1 | 0 | DI5
5 | 1 | 0 | DI6
6 | 1 | 0 | ARena
7 | 1 | 0 | ARLck
8 | 1 | 0 | ARReq1
9 | 1 | 0 | ARReq2
10 | 1 | 0 | ARReq3
11 | 1 | 0 | ARReq4
12 | 1 | 0 | ARReq5
13 | 1 | 0 | ARShot1
14 | 1 | 0 | ARShot2
15 | 1 | 0 | ARShot3
16 | 1 | 0 | ARShot4
17 | 1 | 0 | ARShot5
18 | 1 | 0 | ARCr
19 | 1 | 0 | I>s
20 | 1 | 0 | I>>s
21 | 1 | 0 | I>>>s
22 | 1 | 0 | I>t
23 | 1 | 0 | I>>t
24 | 1 | 0 | I>>>t
25 | 1 | 0 | I2>s
26 | 1 | 0 | I2>t
27 | 1 | 0 | T>s
28 | 1 | 0 | T>t
29 | 1 | 0 | IoInt>s
30 | 1 | 0 | IoInt>t
31 | 1 | 0 | Io>s
32 | 1 | 0 | Io>>s
33 | 1 | 0 | Io>t
34 | 1 | 0 | Io>>t
35 | 1 | 0 | Io>>>s
36 | 1 | 0 | Io>>>>s
37 | 1 | 0 | Io>>>t
38 | 1 | 0 | Io>>>>t
39 | 1 | 0 | Uo>s
40 | 1 | 0 | Uo>>s
41 | 1 | 0 | Uo>t
42 | 1 | 0 | Uo>>t
43 | 1 | 0 | IoD>s
44 | 1 | 0 | IoD>>s
45 | 1 | 0 | IoD>t
46 | 1 | 0 | IoD>>t
47 | 1 | 0 | CBFPs
48 | 1 | 0 | CBFPt
49 | 1 | 0 | FltL1
50 | 1 | 0 | FltL2
51 | 1 | 0 | FltL3
52 | 1 | 0 | P<s
53 | 1 | 0 | P<<s
54 | 1 | 0 | P<t
55 | 1 | 0 | P<<t
56 | 1 | 0 | df/dt_s
57 | 1 | 0 | df/dt_t
58 | 1 | 0 | U1<s
59 | 1 | 0 | U1<<s
60 | 1 | 0 | U1<t
61 | 1 | 0 | U1<<t
62 | 1 | 0 | Z<s
63 | 1 | 0 | Z<<s
Possible data items:
DI1
DI2
DI3
DI4
DI5
DI6
DI7
DI8
DI9
DI10
DI11
DI12
DI13
DI14
DI15
DI16
DI17
DI18
ARena
ARLck
ARReq1
ARReq2
ARReq3
ARReq4
ARReq5
ARShot1
ARShot2
ARShot3
ARShot4
ARShot5
ARCr
I>s
I>>s
I>>>s
I>t
I>>t
I>>>t
I2>s
I2>t
T>s
T>t
If2>s
If2>t
Io>s
Io>>s
Io>t
Io>>t
Io>>>s
Io>>>>s
Io>>>t
Io>>>>t
Uo>s
Uo>>s
Uo>t
Uo>>t
Iφ>s
Iφ>>s
Iφ>>>s
Iφ>>>>s
Iφ>t
Iφ>>t
Iφ>>>t
Iφ>>>>t
IoD>s
IoD>>s
IoD>t
IoD>>t
U>s
U>>s
U>>>s
U>t
U>>t
U>>>t
U<s
U<<s
U<<<s
U<t
U<<t
U<<<t
fXs
fXXs
fXt
fXXt
f<s
f<<s
f<t
f<<t
CBFPs
CBFPt
FltL1
FltL2
FltL3
P<s
P<<s
P<t
P<<t
df/dt_s
df/dt_t
U1<s
U1<<s
U1<t
U1<<t
Z<s
Z<<s
Z<t
Z<<t
X<s
X<<s
X<t
X<<t
Uof3<s
Uof3<t
Uf>s
Uf>t
Q<s
Q<t
dI>t
dI>>t
I'>s
I'>>s
I'>t
I'>>t
I'2>s
I'2>t
Ist>s
Ist>t
I<s
I<t
I2>>s
I2>>t
DI19
DI20
DI21
DI22
DI23
DI24
DI25
DI26
DI27
DI28
DI29
DI30
DI31
DI32
Z1<s
Z1<t
Z2<s
Z2<t
Z3<s
Z3<t
Z4<s
Z4<t
Z5<s
Z5<t
Z1e<s
Z1e<t
Z2e<s
Z2e<t
Z3e<s
Z3e<t
Z4e<s
Z4e<t
Z5e<s
Z5e<t
IoInt>s
IoInt>t
ExtDI1
ExtDI2
ExtDI3
ExtDI4
ExtDI5
ExtDI6
ExtDI7
ExtDI8
ExtDI9
ExtDI10
ExtDI11
ExtDI12
ExtDI13
ExtDI14
ExtDI15
ExtDI16
ExtDI17
ExtDI18
Logic1
Logic2
Logic3
Logic4
Logic5
Logic6
Logic7
Logic8
Logic9
Logic10
Logic11
Logic12
Logic13
Logic14
Logic15
Logic16
Logic17
Logic18
Logic19
Logic20
SGrp1
SGrp2
CTSV_alarm
VTSV_alarm
R/L
VI1
VI2
VI3
VI4
Prg1s
Prg1t
Prg2s
Prg2t
Prg3s
Prg3t
Prg4s
Prg4t
Prg5s
Prg5t
Prg6s
Prg6t
Prg7s
Prg7t
Prg8s
Prg8t
87Ls
87Lt
ArcStg1
ArcStg2
ArcStg3
ArcStg4
ArcStg5
ArcStg6
ArcStg7
ArcStg8
Double-Bit Inputs
Idx | Class | UR | Item
0 | 1 | 0 | Obj1
1 | 1 | 0 | Obj2
2 | 1 | 0 | Obj3
3 | 1 | 0 | Obj4
4 | 1 | 0 | Obj5
5 | 1 | 0 | Obj6
6 | 1 | 0 | Obj7
7 | 1 | 0 | Obj8
Possible data items:
Obj1
Obj2
Obj3
Obj4
Obj5
Obj6
Obj7
Obj8
Analog Inputs
Idx | Class | UR | Item
0 | 2 | 0 | IL1
1 | 2 | 0 | IL2
2 | 2 | 0 | IL3
3 | 2 | 0 | UL1
4 | 2 | 0 | UL2
5 | 2 | 0 | UL3
6 | 2 | 0 | U12
7 | 2 | 0 | U23
8 | 2 | 0 | U31
9 | 2 | 0 | Io1
10 | 2 | 0 | Io2
11 | 2 | 0 | IoCalc
12 | 2 | 0 | Uo
13 | 2 | 0 | P
14 | 2 | 0 | Q
15 | 2 | 0 | S
16 | 2 | 0 | P.F.
17 | 2 | 0 | CosPhi
18 | 2 | 0 | f
Possible data items:
IL1
IL2
IL3
UL1
UL2
UL3
U12
U23
U31
Io1
Io2
IoCalc
Uo
P
Q
S
P.F.
CosPhi
f
IL1RMS
IL2RMS
IL3RMS
Prms
Qrms
Srms
IL1da
IL2da
IL3da
Pda
Qda
Sda
PFda
CosPhida
fda
Prmsda
Qrmsda
Srmsda
THDIL
THDIL1
THDIL2
THDIL3
THDU
THDUa
THDUb
THDUc
I'L1
I'L2
I'L3
I'oCalc
dIL1
dIL2
dIL3
I'L1RMS
I'L2RMS
I'L3RMS
I'L1da
I'L2da
I'L3da
THDI'L
THDI'L1
THDI'L2
THDI'L3
AI1
AI2
AI3
AI4
AI5
AI6
AI7
AI8
AI9
AI10
AI11
AI12
AI13
AI14
AI15
AI16
Z12primary
Z23primary
Z31primary
Z12sec.
Z23sec.
Z31sec.
Z12angle
Z23angle
Z31angle
I>Value
I>>Value
I>>>Value
I_HV_Side
TRTD
Z1Gprimary
Z2Gprimary
Z3Gprimary
Z1Gsec.
Z2Gsec.
Z3Gsec.
Z1Gangle
Z2Gangle
Z3Gangle
PS1Value
PS2Value
PS3Value
PS4Value
PS5Value
PS6Value
PS7Value
PS8Value
PL1
PL2
PL3
QL1
QL2
QL3
SL1
SL2
SL3
cosL1
cosL2
cosL3
I1
I2
I2/I1
Iseq
U1
U2
U2/U1
Useq
U1SagSwell
U2SagSwell
U3SagSwell
Io1rms
Io2rms
IoRMSpeak
IoRMSfund
IoRMSrms
IoRMS/fund
Counters
Idx | Class | UR | Item
Possible data items:
DI1
DI2
DI3
DI4
DI5
DI6
DI7
DI8
DI9
DI10
DI11
DI12
DI13
DI14
DI15
DI16
DI17
DI18
DI19
DI20
DI21
DI22
DI23
DI24
DI25
DI26
DI27
DI28
DI29
DI30
DI31
DI32
E+
E-
Eq+
Eq-
Starts
Fail
Shot1
Shot2
Shot3
Shot4
Shot5
Binary Outputs
Idx | Item
0 | Obj1OC
1 | Obj1Un
2 | Obj2OC
3 | Obj2Un
4 | Obj3OC
5 | Obj3Un
6 | Obj4OC
7 | Obj4Un
8 | Obj5OC
9 | Obj5Un
10 | Obj6OC
11 | Obj6Un
12 | Obj7OC
13 | Obj7Un
14 | Obj8OC
15 | Obj8Un
16 | VI1
Possible data items:
None
Obj1OC
Obj1Un
Obj2OC
Obj2Un
Obj3OC
Obj3Un
Obj4OC
Obj4Un
Obj5OC
Obj5Un
Obj6OC
Obj6Un
Obj7OC
Obj7Un
Obj8OC
Obj8Un
VI1
VI2
VI3
VI4
SGrp1
SGrp2
Latch
ARena
R/L