## Sheet1
Device type: VAMP 230 |  |  | Motor mode
Program version: V10.108
IEC-103 |  | Note: The Digital and Analog sections are editable.
Digital |  | Other available data items are listed in the "Possible data item" list.
Idx | FUN | INF | GI | Event | Control | Item
0 | 55 | 161 | 1 | 1 | 1 | Virtual input 1
1 | 55 | 162 | 1 | 1 | 0 | Digital input 2
2 | 55 | 163 | 1 | 1 | 0 | Digital input 3
3 | 55 | 164 | 1 | 1 | 0 | Digital input 4
4 | 55 | 165 | 1 | 1 | 0 | Digital input 5
5 | 55 | 166 | 1 | 1 | 0 | Digital input 6
6 | 55 | 181 | 1 | 1 | 0 | Obj1 state
7 | 55 | 182 | 1 | 1 | 0 | Obj2 state
8 | 55 | 183 | 1 | 1 | 0 | Obj3 state
9 | 55 | 184 | 1 | 1 | 0 | Obj4 state
10 | 55 | 185 | 1 | 1 | 0 | Obj5 state
11 | 55 | 186 | 1 | 1 | 0 | Obj6 state
12 | 160 | 16 | 1 | 1 | 0
13 | 160 | 130 | 1 | 1 | 0
14 | 160 | 131 | 0 | 1 | 0
15 | 160 | 132 | 0 | 1 | 0
16 | 160 | 133 | 0 | 1 | 0
17 | 160 | 134 | 0 | 1 | 0
18 | 160 | 135 | 0 | 1 | 0
19 | 160 | 136 | 0 | 1 | 0
20 | 160 | 137 | 0 | 1 | 0
21 | 160 | 138 | 0 | 1 | 0
22 | 160 | 139 | 0 | 1 | 0
23 | 160 | 140 | 0 | 1 | 0
24 | 160 | 141 | 0 | 1 | 0
25 | 55 | 23 | 0 | 1 | 1 | Setting group 1
26 | 55 | 24 | 0 | 1 | 1 | Setting group 2
27 | 160 | 84 | 1 | 1 | 0 | I> start
28 | 160 | 94 | 1 | 1 | 0 | I>> start
29 | 160 | 95 | 1 | 1 | 0 | I>>> start
30 | 160 | 90 | 0 | 1 | 0 | I> trip
31 | 160 | 91 | 0 | 1 | 0 | I>> trip
32 | 160 | 96 | 0 | 1 | 0 | I>>> trip
33 | 160 | 106 | 1 | 1 | 0 | I2> start
34 | 160 | 107 | 0 | 1 | 0 | I2> trip
35 | 160 | 108 | 1 | 1 | 0 | T> start
36 | 160 | 109 | 0 | 1 | 0 | T> trip
37 | 160 | 67 | 1 | 1 | 0 | Io> start
38 | 160 | 97 | 1 | 1 | 0 | Io>> start
39 | 160 | 92 | 0 | 1 | 0 | Io> trip
40 | 160 | 93 | 0 | 1 | 0 | Io>> trip
41 | 160 | 123 | 1 | 1 | 0 | Io>>> start
42 | 160 | 125 | 1 | 1 | 0 | Io>>>> start
43 | 160 | 124 | 0 | 1 | 0 | Io>>> trip
44 | 160 | 126 | 0 | 1 | 0 | Io>>>> trip
45 | 160 | 102 | 1 | 1 | 0 | Uo> start
46 | 160 | 104 | 1 | 1 | 0 | Uo>> start
47 | 160 | 103 | 0 | 1 | 0 | Uo> trip
48 | 160 | 105 | 0 | 1 | 0 | Uo>> trip
49 | 160 | 98 | 1 | 1 | 0 | IoDir> start
50 | 160 | 100 | 1 | 1 | 0 | IoDir>> start
51 | 160 | 99 | 0 | 1 | 0 | IoDir> trip
52 | 160 | 101 | 0 | 1 | 0 | IoDir>> trip
53 | 160 | 180 | 1 | 1 | 0 | CBFP start
54 | 160 | 181 | 0 | 1 | 0 | CBFP trip
55 | 160 | 69 | 1 | 1 | 0 | Line 1 fault
56 | 160 | 70 | 1 | 1 | 0 | Line 2 fault
57 | 160 | 71 | 1 | 1 | 0 | Line 3 fault
58 | 160 | 19 | 0 | 0 | 1 | Release latches
59 | 160 | 16 | 0 | 0 | 1
60 | 55 | 181 | 0 | 0 | 1 | Obj1 state
61 | 55 | 182 | 0 | 0 | 1 | Obj2 state
62 | 55 | 163 | 0 | 0 | 1 | Control of A1
63 | 55 | 164 | 0 | 0 | 1 | Control of A2
64 | 55 | 165 | 0 | 0 | 1 | Control of A3
65 | 55 | 166 | 0 | 0 | 1 | Control of A4
66 | 55 | 167 | 0 | 0 | 1 | Control of A5
Analog
Idx | FUN | INF | ASDU | Items
67 | 160 | 162 | 3.1 | Io1
68 | 160 | 163 | 3.1 | Io2
69 | 160 | 177 | 3.1 | IoCalc
70 | 160 | 170 | 3.1
71 | 160 | 147 | 3.4 | Io1
72 | 160 | 148 | 9 | IL1 | IL2 | IL3 | f
73 | 160 | 190 | 4 | Fault current of I>
74 | 160 | 191 | 4 | Fault current of I>>
75 | 160 | 192 | 4 | Fault current of I>>>
76 | 160 | 73 | 4 | Fault reactance
Possible data items:
IL1
IL2
IL3
Io1
Io2
IoCalc
f
IL1RMS
IL2RMS
IL3RMS
IL1da
IL2da
IL3da
fda
DI1 counter
DI2 counter
DI3 counter
DI4 counter
DI5 counter
DI6 counter
THDIL
THDIL1
THDIL2
THDIL3
THDU
THDUa
THDUb
THDUc
DI21 counter
DI22 counter
DI23 counter
DI24 counter
DI25 counter
DI26 counter
DI27 counter
DI28 counter
DI29 counter
DI30 counter
DI31 counter
DI32 counter
IL1d31max
IL2d31max
IL3d31max
Io1d31max
Io2d31max
Faulty phase (EF)
Number of EFs
Digital input 1
Digital input 2
Digital input 3
Digital input 4
Digital input 5
Digital input 6
Obj1 state
Obj2 state
Obj3 state
Obj4 state
Obj5 state
Obj6 state
Release latches
Control of A1
Control of A2
Control of A3
Control of A4
Control of A5
Obj1 extended state
Obj1 extended state
Obj2 extended state
Obj2 extended state
Obj3 extended state
Obj3 extended state
Obj4 extended state
Obj4 extended state
Obj5 extended state
Obj5 extended state
Obj6 extended state
Obj6 extended state
U> start
U>> start
U>>> start
U> trip
U>> trip
U>>> trip
U< start
U<< start
U<<< start
U< trip
U<< trip
U<<< trip
fX start
fXX start
fX trip
fXX trip
f< start
f<< start
f< trip
f<< trip
Virtual input 1
Virtual input 2
Virtual input 3
Virtual input 4
I> start
I>> start
I>>> start
I> trip
I>> trip
I>>> trip
I2> start
I2> trip
T> start
T> trip
CBFP start
CBFP trip
2. Harm start
2. Harm trip
I< start
I< trip
I2>> start
I2>> trip
Ist> start
Ist> trip
N> alarm
Motor start disabled
Motor starting
Motor running
LdI>>> Start On
LdI>>> Trip On
Fault current of I>
Fault current of I>>
Fault current of I>>>
Fault reactance
Frequency
External AI1
External AI2
External AI3
External AI4
External AI5
External AI6
External AI7
External AI8
External AI9
External AI10
External AI11
External AI12
External AI13
External AI14
External AI15
External AI16
Last fault current
Distance to fault
EF reactance
Distance to EF
IDir> start
IDir>> start
IDir>>> start
IDir>>>> start
IDir> trip
IDir>> trip
IDir>>> trip
IDir>>>> trip
IoDir> start
IoDir>> start
IoDir> trip
IoDir>> trip
Prg1 start
Prg1 trip
Prg2 start
Prg2 trip
Prg3 start
Prg3 trip
Prg4 start
Prg4 trip
Prg5 start
Prg5 trip
Prg6 start
Prg6 trip
Prg7 start
Prg7 trip
Prg8 start
Prg8 trip
df/dt start
df/dt trip
P< start
P< trip
P<< start
P<< trip
Q< start
Q< trip
U1< start
U1< trip
U1<< start
U1<< trip
U/f> start
U/f> trip
Iv> start
Iv> trip
Uof3< start
Uof3< trip
Z< start
Z< trip
Z<< start
Z<< trip
X< start
X< trip
X<< start
X<< trip
I'> start
I'> trip
I'>> start
I'>> trip
I'2> start
I'2> trip
dI> trip
dI>> trip
Z1< start
Z1< trip
Z2< start
Z2< trip
Z3< start
Z3< trip
Z4< start
Z4< trip
Z5< start
Z5< trip
Z1e< start
Z1e< trip
Z2e< start
Z2e< trip
Z3e< start
Z3e< trip
Z4e< start
Z4e< trip
Z5e< start
Z5e< trip
IoInt> start
IoInt> trip
Io> start
Io>> start
Io> trip
Io>> trip
Uo> start
Uo>> start
Uo> trip
Uo>> trip
Io>>> start
Io>>>> start
Io>>> trip
Io>>>> trip
Trip relay 1
Trip relay 2
Signal relay 1
Signal relay 2
Signal relay 3
Signal relay 4
Signal relay 5
Binary output BO for light
Virtual output 1
Virtual output 2
External DI1
External DI2
External DI3
External DI4
External DI5
External DI6
External DI7
External DI8
External DI9
External DI10
External DI11
External DI12
External DI13
External DI14
External DI15
External DI16
External DI17
External DI18
Trip relay 5
Trip relay 6
Trip relay 7
Trip relay 8
Line 1 alarm
Line 2 alarm
Line 3 alarm
Digital input 21
Digital input 22
Digital input 23
Digital input 24
Digital input 25
Digital input 26
Digital input 27
Digital input 28
Digital input 29
Digital input 30
Digital input 31
Digital input 32
Virtual output 3
Virtual output 4
Virtual output 5
Virtual output 6