## Revisions
E3x Series Modbus Pointmap and BACnet Objects
Rev History
Rev. A | 2014-04-16 | Initial

## General
LEGEND
R/W: | R = Read-Only
R/W = Read from float or integer format, Write to integer format only
W = Write-Only
NV: | NV = Value is stored in non-volatile memory
V = Value is volatile
SQD ID 1517x: | Y = Parameter is valid for this ID
N = Parameter is invalid for this ID
Scale Reg: | V = Voltage
W = Power
E = Energy
I = Current
<val> = scale is fixed at value shown. If no value shown, it is assumed to be 0.
Modbus Addresses
There are 2 Modbus addresses associated with the E3x - one address for each set of 2 CT strips and set of 4 AUX inputs.
The primary Modbus address is set with the main PCB DIPswitches; The secondary address is always the primary addess + 1.
The Modbus Map detailed here is repeated in it's entirety for both addresses.
Supported Commands
Read Holding Register (03h)
Preset Single Register (06h)
Preset Multiple Registers (10h)
Report Slave ID (11h)
This will include the following info in the "Additional Data" area:
"Veris Model Exxx Branch Circuit Monitor, S/N=0x12345678, Location="<location string>""
Integer vs. Floating Point Registers
Integer format registers represent the data as 16 bit signed integer values. Float format registers represent the same data as 32-bit floating point values.
Floats
All floating point variables are read-only.
Floating point registers are packed as follows:
Float | MSB | BYTE3 | BYTE2 | LSB
Modbus MSW | MSB | LSB
Modbus LSW |  |  | MSB | LSB
Example:
For a floating point value of 3.14159, the encoded 32-bit float value is 0x40490FD0.
Modbus MSW = 0x4049
Modbus LSW = 0x0FD0
Integers
Integer format registers must be used in conjunction with their associated Scale registers.
The Scale Registers represent the exponent of the associated values and are used in conjunction with the integer registers to create the
final floating-point results.
Example:
integer register = 27
scale register = -2
final result = 27 * 10^(-2) = 0.27
Note: If a Scale register is not listed for a parameter, it is assumed to be 0.
32-bit integer values, such as KWH, are packed as follows:
32-bit integer | MSB | BYTE3 | BYTE2 | LSB
Modbus MSW | MSB | LSB
Modbus LSW |  |  | MSB | LSB
Example:
For a 32-bit value of 0x12345678.
Modbus MSW = 0x1234
Modbus LSW = 0x5678
Note that the Scale register for Energy (E) is applied only to the final 32-bit result.
For the Current Scales (I), Power Scales (W) and Energy Scales (E) for 1 phase, 2 phase and/or 3 phase Modbus Point Maps,
make sure you are using the correct Scale value
Example:
integer register #1336 (Current Meter 1) = 10
scale register #1000 = -1
final result = 10 * 10^(-1) = 1.0
Model Differences
The Device ID register (register #5) indicates which registers in the map are valid and invalid
Invalid channels report the following values:
Integer registers: 0x8000 (32768)
Float registers: 0x7FC00000 (NaN)
| Section | #Registers
| Common | 1040
| 1PH | 1806
| Logical Map by Group | 482
| Logical Map by Value | 2070 |  | Note: This map replaces the 2PH & 3PH Map
| 2PH | 1491
| 3PH | 1288
| TOTAL | 8177
Below maps the Device ID to Model Series:
15170 = Model C, current only on all channels, no voltage
15171 = Model B, current only on branch channels, power on AUX channels plus voltage
15172 = Model A, current and power on all channels plus voltage

## Common
[8 empty] | Modbus |  |  |  |  | BACnet
Channel | Model (A,B,C) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Description | Object Name | Object ID | Units | COV Increment | BACnet Description | Range | Default
Manufacturer Info
| A,B,C | R | NV | 1 |  |  |  | Serial Number MSW | Serial Number MSW | AI51 | No-Units | 1 | Serial Number MSW
| A,B,C | R | NV | 2 |  |  |  | Serial Number LSW | Serial Number LSW | AI52 | No-Units | 1 | Serial Number LSW
| A,B,C | R | NV | 3 |  |  |  | Firmware Revision RS | Firmware Revision RS | AI53 | No-Units | 1 | Firmware Revision RS
| A,B,C | R | NV | 4 |  |  |  | Firmware Revision OS | Firmware Revision OS | AI54 | No-Units | 1 | Firmware Revision OS
| A,B,C | R | NV | 5 |  |  |  | Device ID: | Device ID: | AI55 | No-Units | 1 | 15170=C; 15171=B; 15172=A
15170 = Model C, current only on all channels, no voltage
15171 = Model B, current only on branch channels, power on AUX
channels plus voltage
15172 = Model A, current and power on all channels plus voltage
General User Setup
E30 Series Only <start>
Logical Circuit Assignment will be cleared if Configuration Register is Changed, set Configuration first
| A,B,C | R/W | NV | 6 |  |  |  | Configuration (bit 0 is LSB): | Configuration (bit 0 is LSB): | AV1 | No-Units | 1 | Configuration (bit 0 is LSB): |  | 0
Bit 0: 0 = normal / sequential, 1 = rotated / odd-even
Bit 1: 0 = double-row, 1 = single-row
Bit 2-15: future use
Examples:
Value 0 = Top Feed
Value 1 = Bottom Feed
Value 2 = Single Row: Sequential
Value 3 = Single Row: Odd / Even
see install guide for diagrams
E30 Series Only <end>
E31 Series Only <start>
Logical Circuit Assignment will be cleared if Configuration Register is Changed, set Configuration first
| A,B,C | R/W | NV | 6 |  |  |  | Configuration (bit 0 is LSB): | Configuration (bit 0 is LSB): | AV1 | No-Units | 1 | Configuration (bit 0 is LSB): |  | 0
Bit 0: 0 = normal / sequential, 1 = rotated / odd-even
Bit 1: 0 = double-row, 1 = single-row
Bit 2-15: future use
Examples:
Value 0 = Odd/Even
Value 1 = Reserved for Solid-Core
Value 2 = Sequential
Value 3 = Reserved for Solid-Core
see install guide for diagrams
E31 Series Only <end>
| A,B,C | R/W | NV | 7 |  |  |  | Location String | [6 empty] | "Panel #<NUM>"
|  |  |  | through |  |  |  | These 64 registers provide for up to 128 packed ASCII text
|  |  |  | 70 |  |  |  | characters (with terminator)
It is also used in the Report_ID response
Lowest numbered register holds the 1st 2 characters of the string
Encoding is 2nd character in MSB, 1st in LSB
Example for "PDU#3":
Reg 7: 0x4450 (DP)
Reg 8: 0x2355 (#U)
Reg 9: 0x0033 (<term>3)
All other Regs: N/A
Demand Setup
Setup for Present KW Demand, Max KW Demand, Present Current Demand, Max Current Demand
All | A,B,C | R/W | NV | 71 |  |  |  | Number of Sub-Intervals per Demand Interval | # of Sub-Intervals per Demand Int. | AV2 | No-Units | 1 | Number of Sub-Intervals per Interval | 1-6 | 1
Sets the number of sub-intervals that make a single demand interval.
For block demand, set this to 1.
All | A,B,C | R/W | NV | 72 |  |  |  | Sub-Interval Length in seconds. For sync-to-comms, set this to 0. | Sub-Interval Length in seconds. | AV3 | No-Units | 1 | Sub-Interval Length in seconds. | 0, 10-32767 | 900 (15minutes)
CT Sizes (Amps)
E30 Series Only <start>
1 | A,B,C | R | NV | 73 |  |  |  | Branch CT Size | Branch 1 CT Size | AV4 | Amperes | 5 | Branch 1 CT Size | 0-32767 | 100
2 | A,B,C | R | NV | 74 |  |  |  | Branch CT Size | Branch 2 CT Size | AV5 | Amperes | 5 | Branch 2 CT Size | 0-32767 | 100
3 | A,B,C | R | NV | 75 |  |  |  | Branch CT Size | Branch 3 CT Size | AV6 | Amperes | 5 | Branch 3 CT Size | 0-32767 | 100
4 | A,B,C | R | NV | 76 |  |  |  | Branch CT Size | Branch 4 CT Size | AV7 | Amperes | 5 | Branch 4 CT Size | 0-32767 | 100
5 | A,B,C | R | NV | 77 |  |  |  | Branch CT Size | Branch 5 CT Size | AV8 | Amperes | 5 | Branch 5 CT Size | 0-32767 | 100
6 | A,B,C | R | NV | 78 |  |  |  | Branch CT Size | Branch 6 CT Size | AV9 | Amperes | 5 | Branch 6 CT Size | 0-32767 | 100
7 | A,B,C | R | NV | 79 |  |  |  | Branch CT Size | Branch 7 CT Size | AV10 | Amperes | 5 | Branch 7 CT Size | 0-32767 | 100
8 | A,B,C | R | NV | 80 |  |  |  | Branch CT Size | Branch 8 CT Size | AV11 | Amperes | 5 | Branch 8 CT Size | 0-32767 | 100
9 | A,B,C | R | NV | 81 |  |  |  | Branch CT Size | Branch 9 CT Size | AV12 | Amperes | 5 | Branch 9 CT Size | 0-32767 | 100
10 | A,B,C | R | NV | 82 |  |  |  | Branch CT Size | Branch 10 CT Size | AV13 | Amperes | 5 | Branch 10 CT Size | 0-32767 | 100
11 | A,B,C | R | NV | 83 |  |  |  | Branch CT Size | Branch 11 CT Size | AV14 | Amperes | 5 | Branch 11 CT Size | 0-32767 | 100
12 | A,B,C | R | NV | 84 |  |  |  | Branch CT Size | Branch 12 CT Size | AV15 | Amperes | 5 | Branch 12 CT Size | 0-32767 | 100
13 | A,B,C | R | NV | 85 |  |  |  | Branch CT Size | Branch 13 CT Size | AV16 | Amperes | 5 | Branch 13 CT Size | 0-32767 | 100
14 | A,B,C | R | NV | 86 |  |  |  | Branch CT Size | Branch 14 CT Size | AV17 | Amperes | 5 | Branch 14 CT Size | 0-32767 | 100
15 | A,B,C | R | NV | 87 |  |  |  | Branch CT Size | Branch 15 CT Size | AV18 | Amperes | 5 | Branch 15 CT Size | 0-32767 | 100
16 | A,B,C | R | NV | 88 |  |  |  | Branch CT Size | Branch 16 CT Size | AV19 | Amperes | 5 | Branch 16 CT Size | 0-32767 | 100
17 | A,B,C | R | NV | 89 |  |  |  | Branch CT Size | Branch 17 CT Size | AV20 | Amperes | 5 | Branch 17 CT Size | 0-32767 | 100
18 | A,B,C | R | NV | 90 |  |  |  | Branch CT Size | Branch 18 CT Size | AV21 | Amperes | 5 | Branch 18 CT Size | 0-32767 | 100
19 | A,B,C | R | NV | 91 |  |  |  | Branch CT Size | Branch 19 CT Size | AV22 | Amperes | 5 | Branch 19 CT Size | 0-32767 | 100
20 | A,B,C | R | NV | 92 |  |  |  | Branch CT Size | Branch 20 CT Size | AV23 | Amperes | 5 | Branch 20 CT Size | 0-32767 | 100
21 | A,B,C | R | NV | 93 |  |  |  | Branch CT Size | Branch 21 CT Size | AV24 | Amperes | 5 | Branch 21 CT Size | 0-32767 | 100
22 | A,B,C | R | NV | 94 |  |  |  | Branch CT Size | Branch 22 CT Size | AV25 | Amperes | 5 | Branch 22 CT Size | 0-32767 | 100
23 | A,B,C | R | NV | 95 |  |  |  | Branch CT Size | Branch 23 CT Size | AV26 | Amperes | 5 | Branch 23 CT Size | 0-32767 | 100
24 | A,B,C | R | NV | 96 |  |  |  | Branch CT Size | Branch 24 CT Size | AV27 | Amperes | 5 | Branch 24 CT Size | 0-32767 | 100
25 | A,B,C | R | NV | 97 |  |  |  | Branch CT Size | Branch 25 CT Size | AV28 | Amperes | 5 | Branch 25 CT Size | 0-32767 | 100
26 | A,B,C | R | NV | 98 |  |  |  | Branch CT Size | Branch 26 CT Size | AV29 | Amperes | 5 | Branch 26 CT Size | 0-32767 | 100
27 | A,B,C | R | NV | 99 |  |  |  | Branch CT Size | Branch 27 CT Size | AV30 | Amperes | 5 | Branch 27 CT Size | 0-32767 | 100
28 | A,B,C | R | NV | 100 |  |  |  | Branch CT Size | Branch 28 CT Size | AV31 | Amperes | 5 | Branch 28 CT Size | 0-32767 | 100
29 | A,B,C | R | NV | 101 |  |  |  | Branch CT Size | Branch 29 CT Size | AV32 | Amperes | 5 | Branch 29 CT Size | 0-32767 | 100
30 | A,B,C | R | NV | 102 |  |  |  | Branch CT Size | Branch 30 CT Size | AV33 | Amperes | 5 | Branch 30 CT Size | 0-32767 | 100
31 | A,B,C | R | NV | 103 |  |  |  | Branch CT Size | Branch 31 CT Size | AV34 | Amperes | 5 | Branch 31 CT Size | 0-32767 | 100
32 | A,B,C | R | NV | 104 |  |  |  | Branch CT Size | Branch 32 CT Size | AV35 | Amperes | 5 | Branch 32 CT Size | 0-32767 | 100
33 | A,B,C | R | NV | 105 |  |  |  | Branch CT Size | Branch 33 CT Size | AV36 | Amperes | 5 | Branch 33 CT Size | 0-32767 | 100
34 | A,B,C | R | NV | 106 |  |  |  | Branch CT Size | Branch 34 CT Size | AV37 | Amperes | 5 | Branch 34 CT Size | 0-32767 | 100
35 | A,B,C | R | NV | 107 |  |  |  | Branch CT Size | Branch 35 CT Size | AV38 | Amperes | 5 | Branch 35 CT Size | 0-32767 | 100
36 | A,B,C | R | NV | 108 |  |  |  | Branch CT Size | Branch 36 CT Size | AV39 | Amperes | 5 | Branch 36 CT Size | 0-32767 | 100
37 | A,B,C | R | NV | 109 |  |  |  | Branch CT Size | Branch 37 CT Size | AV40 | Amperes | 5 | Branch 37 CT Size | 0-32767 | 100
38 | A,B,C | R | NV | 110 |  |  |  | Branch CT Size | Branch 38 CT Size | AV41 | Amperes | 5 | Branch 38 CT Size | 0-32767 | 100
39 | A,B,C | R | NV | 111 |  |  |  | Branch CT Size | Branch 39 CT Size | AV42 | Amperes | 5 | Branch 39 CT Size | 0-32767 | 100
40 | A,B,C | R | NV | 112 |  |  |  | Branch CT Size | Branch 40 CT Size | AV43 | Amperes | 5 | Branch 40 CT Size | 0-32767 | 100
41 | A,B,C | R | NV | 113 |  |  |  | Branch CT Size | Branch 41 CT Size | AV44 | Amperes | 5 | Branch 41 CT Size | 0-32767 | 100
42 | A,B,C | R | NV | 114 |  |  |  | Branch CT Size | Branch 42 CT Size | AV45 | Amperes | 5 | Branch 42 CT Size | 0-32767 | 100
43 | A,B,C | R/W | NV | 115 |  |  |  | AUX CT Size | AUX Channel (phase 1) CT Size | AV46 | Amperes | 5 | AUX Channel (phase 1) CT Size | 0-32767 | 200
44 | A,B,C | R/W | NV | 116 |  |  |  | AUX CT Size | AUX Channel (phase 2) CT Size | AV47 | Amperes | 5 | AUX Channel (phase 2) CT Size | 0-32767 | 200
45 | A,B,C | R/W | NV | 117 |  |  |  | AUX CT Size | AUX Channel (phase 3) CT Size | AV48 | Amperes | 5 | AUX Channel (phase 3) CT Size | 0-32767 | 200
46 | A,B,C | R/W | NV | 118 |  |  |  | AUX CT Size | AUX Channel (Neutral) CT Size | AV49 | Amperes | 5 | AUX Channel (Neutral) CT Size | 0-32767 | 200
E30 Series Only <end>
E31 Series Only <start>
CT Sizes (Amps)
1 | A,B,C | R/W | NV | 73 |  |  |  | Branch CT Size | Branch 1 CT Size | AV4 | Amperes | 5 | Branch 1 CT Size | 0-32767 | 50
2 | A,B,C | R/W | NV | 74 |  |  |  | Branch CT Size | Branch 2 CT Size | AV5 | Amperes | 5 | Branch 2 CT Size | 0-32767 | 50
3 | A,B,C | R/W | NV | 75 |  |  |  | Branch CT Size | Branch 3 CT Size | AV6 | Amperes | 5 | Branch 3 CT Size | 0-32767 | 50
4 | A,B,C | R/W | NV | 76 |  |  |  | Branch CT Size | Branch 4 CT Size | AV7 | Amperes | 5 | Branch 4 CT Size | 0-32767 | 50
5 | A,B,C | R/W | NV | 77 |  |  |  | Branch CT Size | Branch 5 CT Size | AV8 | Amperes | 5 | Branch 5 CT Size | 0-32767 | 50
6 | A,B,C | R/W | NV | 78 |  |  |  | Branch CT Size | Branch 6 CT Size | AV9 | Amperes | 5 | Branch 6 CT Size | 0-32767 | 50
7 | A,B,C | R/W | NV | 79 |  |  |  | Branch CT Size | Branch 7 CT Size | AV10 | Amperes | 5 | Branch 7 CT Size | 0-32767 | 50
8 | A,B,C | R/W | NV | 80 |  |  |  | Branch CT Size | Branch 8 CT Size | AV11 | Amperes | 5 | Branch 8 CT Size | 0-32767 | 50
9 | A,B,C | R/W | NV | 81 |  |  |  | Branch CT Size | Branch 9 CT Size | AV12 | Amperes | 5 | Branch 9 CT Size | 0-32767 | 50
10 | A,B,C | R/W | NV | 82 |  |  |  | Branch CT Size | Branch 10 CT Size | AV13 | Amperes | 5 | Branch 10 CT Size | 0-32767 | 50
11 | A,B,C | R/W | NV | 83 |  |  |  | Branch CT Size | Branch 11 CT Size | AV14 | Amperes | 5 | Branch 11 CT Size | 0-32767 | 50
12 | A,B,C | R/W | NV | 84 |  |  |  | Branch CT Size | Branch 12 CT Size | AV15 | Amperes | 5 | Branch 12 CT Size | 0-32767 | 50
13 | A,B,C | R/W | NV | 85 |  |  |  | Branch CT Size | Branch 13 CT Size | AV16 | Amperes | 5 | Branch 13 CT Size | 0-32767 | 50
14 | A,B,C | R/W | NV | 86 |  |  |  | Branch CT Size | Branch 14 CT Size | AV17 | Amperes | 5 | Branch 14 CT Size | 0-32767 | 50
15 | A,B,C | R/W | NV | 87 |  |  |  | Branch CT Size | Branch 15 CT Size | AV18 | Amperes | 5 | Branch 15 CT Size | 0-32767 | 50
16 | A,B,C | R/W | NV | 88 |  |  |  | Branch CT Size | Branch 16 CT Size | AV19 | Amperes | 5 | Branch 16 CT Size | 0-32767 | 50
17 | A,B,C | R/W | NV | 89 |  |  |  | Branch CT Size | Branch 17 CT Size | AV20 | Amperes | 5 | Branch 17 CT Size | 0-32767 | 50
18 | A,B,C | R/W | NV | 90 |  |  |  | Branch CT Size | Branch 18 CT Size | AV21 | Amperes | 5 | Branch 18 CT Size | 0-32767 | 50
19 | A,B,C | R/W | NV | 91 |  |  |  | Branch CT Size | Branch 19 CT Size | AV22 | Amperes | 5 | Branch 19 CT Size | 0-32767 | 50
20 | A,B,C | R/W | NV | 92 |  |  |  | Branch CT Size | Branch 20 CT Size | AV23 | Amperes | 5 | Branch 20 CT Size | 0-32767 | 50
21 | A,B,C | R/W | NV | 93 |  |  |  | Branch CT Size | Branch 21 CT Size | AV24 | Amperes | 5 | Branch 21 CT Size | 0-32767 | 50
22 | A,B,C | R/W | NV | 94 |  |  |  | Branch CT Size | Branch 22 CT Size | AV25 | Amperes | 5 | Branch 22 CT Size | 0-32767 | 50
23 | A,B,C | R/W | NV | 95 |  |  |  | Branch CT Size | Branch 23 CT Size | AV26 | Amperes | 5 | Branch 23 CT Size | 0-32767 | 50
24 | A,B,C | R/W | NV | 96 |  |  |  | Branch CT Size | Branch 24 CT Size | AV27 | Amperes | 5 | Branch 24 CT Size | 0-32767 | 50
25 | A,B,C | R/W | NV | 97 |  |  |  | Branch CT Size | Branch 25 CT Size | AV28 | Amperes | 5 | Branch 25 CT Size | 0-32767 | 50
26 | A,B,C | R/W | NV | 98 |  |  |  | Branch CT Size | Branch 26 CT Size | AV29 | Amperes | 5 | Branch 26 CT Size | 0-32767 | 50
27 | A,B,C | R/W | NV | 99 |  |  |  | Branch CT Size | Branch 27 CT Size | AV30 | Amperes | 5 | Branch 27 CT Size | 0-32767 | 50
28 | A,B,C | R/W | NV | 100 |  |  |  | Branch CT Size | Branch 28 CT Size | AV31 | Amperes | 5 | Branch 28 CT Size | 0-32767 | 50
29 | A,B,C | R/W | NV | 101 |  |  |  | Branch CT Size | Branch 29 CT Size | AV32 | Amperes | 5 | Branch 29 CT Size | 0-32767 | 50
30 | A,B,C | R/W | NV | 102 |  |  |  | Branch CT Size | Branch 30 CT Size | AV33 | Amperes | 5 | Branch 30 CT Size | 0-32767 | 50
31 | A,B,C | R/W | NV | 103 |  |  |  | Branch CT Size | Branch 31 CT Size | AV34 | Amperes | 5 | Branch 31 CT Size | 0-32767 | 50
32 | A,B,C | R/W | NV | 104 |  |  |  | Branch CT Size | Branch 32 CT Size | AV35 | Amperes | 5 | Branch 32 CT Size | 0-32767 | 50
33 | A,B,C | R/W | NV | 105 |  |  |  | Branch CT Size | Branch 33 CT Size | AV36 | Amperes | 5 | Branch 33 CT Size | 0-32767 | 50
34 | A,B,C | R/W | NV | 106 |  |  |  | Branch CT Size | Branch 34 CT Size | AV37 | Amperes | 5 | Branch 34 CT Size | 0-32767 | 50
35 | A,B,C | R/W | NV | 107 |  |  |  | Branch CT Size | Branch 35 CT Size | AV38 | Amperes | 5 | Branch 35 CT Size | 0-32767 | 50
36 | A,B,C | R/W | NV | 108 |  |  |  | Branch CT Size | Branch 36 CT Size | AV39 | Amperes | 5 | Branch 36 CT Size | 0-32767 | 50
37 | A,B,C | R/W | NV | 109 |  |  |  | Branch CT Size | Branch 37 CT Size | AV40 | Amperes | 5 | Branch 37 CT Size | 0-32767 | 50
38 | A,B,C | R/W | NV | 110 |  |  |  | Branch CT Size | Branch 38 CT Size | AV41 | Amperes | 5 | Branch 38 CT Size | 0-32767 | 50
39 | A,B,C | R/W | NV | 111 |  |  |  | Branch CT Size | Branch 39 CT Size | AV42 | Amperes | 5 | Branch 39 CT Size | 0-32767 | 50
40 | A,B,C | R/W | NV | 112 |  |  |  | Branch CT Size | Branch 40 CT Size | AV43 | Amperes | 5 | Branch 40 CT Size | 0-32767 | 50
41 | A,B,C | R/W | NV | 113 |  |  |  | Branch CT Size | Branch 41 CT Size | AV44 | Amperes | 5 | Branch 41 CT Size | 0-32767 | 50
42 | A,B,C | R/W | NV | 114 |  |  |  | Branch CT Size | Branch 42 CT Size | AV45 | Amperes | 5 | Branch 42 CT Size | 0-32767 | 50
43 | A,B,C | R/W | NV | 115 |  |  |  | AUX CT Size | AUX Channel (phase 1) CT Size | AV46 | Amperes | 5 | AUX Channel (phase 1) CT Size | 0-32767 | 200
44 | A,B,C | R/W | NV | 116 |  |  |  | AUX CT Size | AUX Channel (phase 2) CT Size | AV47 | Amperes | 5 | AUX Channel (phase 2) CT Size | 0-32767 | 200
45 | A,B,C | R/W | NV | 117 |  |  |  | AUX CT Size | AUX Channel (phase 3) CT Size | AV48 | Amperes | 5 | AUX Channel (phase 3) CT Size | 0-32767 | 200
46 | A,B,C | R/W | NV | 118 |  |  |  | AUX CT Size | AUX Channel (Neutral) CT Size | AV49 | Amperes | 5 | AUX Channel (Neutral) CT Size | 0-32767 | 200
E31 Series Only <end>
Breaker Sizes (Amps)
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
1 | A,B,C | R/W | NV | 119 |  |  |  | Branch Breaker Size | Branch 1 Breaker Size | AV50 | Amperes | 5 | Branch 1 Breaker Size | 0-32767 | 20
2 | A,B,C | R/W | NV | 120 |  |  |  | Branch Breaker Size | Branch 2 Breaker Size | AV51 | Amperes | 5 | Branch 2 Breaker Size | 0-32767 | 20
3 | A,B,C | R/W | NV | 121 |  |  |  | Branch Breaker Size | Branch 3 Breaker Size | AV52 | Amperes | 5 | Branch 3 Breaker Size | 0-32767 | 20
4 | A,B,C | R/W | NV | 122 |  |  |  | Branch Breaker Size | Branch 4 Breaker Size | AV53 | Amperes | 5 | Branch 4 Breaker Size | 0-32767 | 20
5 | A,B,C | R/W | NV | 123 |  |  |  | Branch Breaker Size | Branch 5 Breaker Size | AV54 | Amperes | 5 | Branch 5 Breaker Size | 0-32767 | 20
6 | A,B,C | R/W | NV | 124 |  |  |  | Branch Breaker Size | Branch 6 Breaker Size | AV55 | Amperes | 5 | Branch 6 Breaker Size | 0-32767 | 20
7 | A,B,C | R/W | NV | 125 |  |  |  | Branch Breaker Size | Branch 7 Breaker Size | AV56 | Amperes | 5 | Branch 7 Breaker Size | 0-32767 | 20
8 | A,B,C | R/W | NV | 126 |  |  |  | Branch Breaker Size | Branch 8 Breaker Size | AV57 | Amperes | 5 | Branch 8 Breaker Size | 0-32767 | 20
9 | A,B,C | R/W | NV | 127 |  |  |  | Branch Breaker Size | Branch 9 Breaker Size | AV58 | Amperes | 5 | Branch 9 Breaker Size | 0-32767 | 20
10 | A,B,C | R/W | NV | 128 |  |  |  | Branch Breaker Size | Branch 10 Breaker Size | AV59 | Amperes | 5 | Branch 10 Breaker Size | 0-32767 | 20
11 | A,B,C | R/W | NV | 129 |  |  |  | Branch Breaker Size | Branch 11 Breaker Size | AV60 | Amperes | 5 | Branch 11 Breaker Size | 0-32767 | 20
12 | A,B,C | R/W | NV | 130 |  |  |  | Branch Breaker Size | Branch 12 Breaker Size | AV61 | Amperes | 5 | Branch 12 Breaker Size | 0-32767 | 20
13 | A,B,C | R/W | NV | 131 |  |  |  | Branch Breaker Size | Branch 13 Breaker Size | AV62 | Amperes | 5 | Branch 13 Breaker Size | 0-32767 | 20
14 | A,B,C | R/W | NV | 132 |  |  |  | Branch Breaker Size | Branch 14 Breaker Size | AV63 | Amperes | 5 | Branch 14 Breaker Size | 0-32767 | 20
15 | A,B,C | R/W | NV | 133 |  |  |  | Branch Breaker Size | Branch 15 Breaker Size | AV64 | Amperes | 5 | Branch 15 Breaker Size | 0-32767 | 20
16 | A,B,C | R/W | NV | 134 |  |  |  | Branch Breaker Size | Branch 16 Breaker Size | AV65 | Amperes | 5 | Branch 16 Breaker Size | 0-32767 | 20
17 | A,B,C | R/W | NV | 135 |  |  |  | Branch Breaker Size | Branch 17 Breaker Size | AV66 | Amperes | 5 | Branch 17 Breaker Size | 0-32767 | 20
18 | A,B,C | R/W | NV | 136 |  |  |  | Branch Breaker Size | Branch 18 Breaker Size | AV67 | Amperes | 5 | Branch 18 Breaker Size | 0-32767 | 20
19 | A,B,C | R/W | NV | 137 |  |  |  | Branch Breaker Size | Branch 19 Breaker Size | AV68 | Amperes | 5 | Branch 19 Breaker Size | 0-32767 | 20
20 | A,B,C | R/W | NV | 138 |  |  |  | Branch Breaker Size | Branch 20 Breaker Size | AV69 | Amperes | 5 | Branch 20 Breaker Size | 0-32767 | 20
21 | A,B,C | R/W | NV | 139 |  |  |  | Branch Breaker Size | Branch 21 Breaker Size | AV70 | Amperes | 5 | Branch 21 Breaker Size | 0-32767 | 20
22 | A,B,C | R/W | NV | 140 |  |  |  | Branch Breaker Size | Branch 22 Breaker Size | AV71 | Amperes | 5 | Branch 22 Breaker Size | 0-32767 | 20
23 | A,B,C | R/W | NV | 141 |  |  |  | Branch Breaker Size | Branch 23 Breaker Size | AV72 | Amperes | 5 | Branch 23 Breaker Size | 0-32767 | 20
24 | A,B,C | R/W | NV | 142 |  |  |  | Branch Breaker Size | Branch 24 Breaker Size | AV73 | Amperes | 5 | Branch 24 Breaker Size | 0-32767 | 20
25 | A,B,C | R/W | NV | 143 |  |  |  | Branch Breaker Size | Branch 25 Breaker Size | AV74 | Amperes | 5 | Branch 25 Breaker Size | 0-32767 | 20
26 | A,B,C | R/W | NV | 144 |  |  |  | Branch Breaker Size | Branch 26 Breaker Size | AV75 | Amperes | 5 | Branch 26 Breaker Size | 0-32767 | 20
27 | A,B,C | R/W | NV | 145 |  |  |  | Branch Breaker Size | Branch 27 Breaker Size | AV76 | Amperes | 5 | Branch 27 Breaker Size | 0-32767 | 20
28 | A,B,C | R/W | NV | 146 |  |  |  | Branch Breaker Size | Branch 28 Breaker Size | AV77 | Amperes | 5 | Branch 28 Breaker Size | 0-32767 | 20
29 | A,B,C | R/W | NV | 147 |  |  |  | Branch Breaker Size | Branch 29 Breaker Size | AV78 | Amperes | 5 | Branch 29 Breaker Size | 0-32767 | 20
30 | A,B,C | R/W | NV | 148 |  |  |  | Branch Breaker Size | Branch 30 Breaker Size | AV79 | Amperes | 5 | Branch 30 Breaker Size | 0-32767 | 20
31 | A,B,C | R/W | NV | 149 |  |  |  | Branch Breaker Size | Branch 31 Breaker Size | AV80 | Amperes | 5 | Branch 31 Breaker Size | 0-32767 | 20
32 | A,B,C | R/W | NV | 150 |  |  |  | Branch Breaker Size | Branch 32 Breaker Size | AV81 | Amperes | 5 | Branch 32 Breaker Size | 0-32767 | 20
33 | A,B,C | R/W | NV | 151 |  |  |  | Branch Breaker Size | Branch 33 Breaker Size | AV82 | Amperes | 5 | Branch 33 Breaker Size | 0-32767 | 20
34 | A,B,C | R/W | NV | 152 |  |  |  | Branch Breaker Size | Branch 34 Breaker Size | AV83 | Amperes | 5 | Branch 34 Breaker Size | 0-32767 | 20
35 | A,B,C | R/W | NV | 153 |  |  |  | Branch Breaker Size | Branch 35 Breaker Size | AV84 | Amperes | 5 | Branch 35 Breaker Size | 0-32767 | 20
36 | A,B,C | R/W | NV | 154 |  |  |  | Branch Breaker Size | Branch 36 Breaker Size | AV85 | Amperes | 5 | Branch 36 Breaker Size | 0-32767 | 20
37 | A,B,C | R/W | NV | 155 |  |  |  | Branch Breaker Size | Branch 37 Breaker Size | AV86 | Amperes | 5 | Branch 37 Breaker Size | 0-32767 | 20
38 | A,B,C | R/W | NV | 156 |  |  |  | Branch Breaker Size | Branch 38 Breaker Size | AV87 | Amperes | 5 | Branch 38 Breaker Size | 0-32767 | 20
39 | A,B,C | R/W | NV | 157 |  |  |  | Branch Breaker Size | Branch 39 Breaker Size | AV88 | Amperes | 5 | Branch 39 Breaker Size | 0-32767 | 20
40 | A,B,C | R/W | NV | 158 |  |  |  | Branch Breaker Size | Branch 40 Breaker Size | AV89 | Amperes | 5 | Branch 40 Breaker Size | 0-32767 | 20
41 | A,B,C | R/W | NV | 159 |  |  |  | Branch Breaker Size | Branch 41 Breaker Size | AV90 | Amperes | 5 | Branch 41 Breaker Size | 0-32767 | 20
42 | A,B,C | R/W | NV | 160 |  |  |  | Branch Breaker Size | Branch 42 Breaker Size | AV91 | Amperes | 5 | Branch 42 Breaker Size | 0-32767 | 20
43 | A,B,C | R/W | NV | 161 |  |  |  | AUX Breaker Size | AUX Channel (phase 1) Breaker Size | AV92 | Amperes | 5 | AUX Channel (phase 1) Breaker Size | 0-32767 | 225
44 | A,B,C | R/W | NV | 162 |  |  |  | AUX Breaker Size | AUX Channel (phase 2) Breaker Size | AV93 | Amperes | 5 | AUX Channel (phase 2) Breaker Size | 0-32767 | 225
45 | A,B,C | R/W | NV | 163 |  |  |  | AUX Breaker Size | AUX Channel (phase 3) Breaker Size | AV94 | Amperes | 5 | AUX Channel (phase 3) Breaker Size | 0-32767 | 225
46 | A,B,C | R/W | NV | 164 |  |  |  | AUX Breaker Size | AUX Channel (Neutral) Breaker Size | AV95 | Amperes | 5 | AUX Channel (Neutral) Breaker Size | 0-32767 | 225
Alarm Timers (seconds)
These timers control entry into a latching alarm state. A return to a non-alarm state is instantaneous.
All channels use the same global timers.
Latching Alarm On Time applies to all Latching Alarms.
The paraCircuit measurement rate is expected to be around 2.5 secs, which will limit the effective resolution of these timers.
All | A,B,C | R/W | NV | 165 |  |  |  | High-High Latching Alarm Time Delay | High-High Latching Alarm Time Delay | AV96 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | A,B,C | R/W | NV | 166 |  |  |  | High Latching Alarm Time Delay | High Latching Alarm Time Delay | AV97 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | A,B,C | R/W | NV | 167 |  |  |  | Low Latching Alarm Time Delay | Low Latching Alarm Time Delay | AV98 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | A,B,C | R/W | NV | 168 |  |  |  | Low-Low Latching Alarm Time Delay | Low-Low Latching Alarm Time Delay | AV99 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | A,B,C | R/W | NV | 169 |  |  |  | Latching Alarm ON Time (when current is above Low-Low | Latching Alarm ON Time | AV100 | Seconds | 1 | From initial current to alarms enabled | 0-32767 | 10
alarm & ON Time elapses then ON state is declared for
all latching alarms, ON State enables Alarm Time Delays)
All | A,B,C | R/W | NV | 170 |  |  |  | Latching Alarms time until OFF state declared (current is below | Latching Alarms time until OFF state | AV101 | Seconds | 1 | time until OFF state declared | 0-32767 | 30
Low-Low alarm and a ON state was declared)
Alarm Thresholds
All values are expressed as %breaker-size.
All channels use these same global values.
An entry of 0% for any threshold disables that alarm for all channels.
All Thresholds are scaled by -1 to increase the precision by 1 decimal point
Hysteresis only applies to Non-Latching Alarms
All | A,B,C | R/W | NV | 171 |  |  | -1 | High-High Latching Alarm Threshold | High-High Latching Alarm Threshold | AV102 | Percent | 1 | % of breaker size | 0-1000 | 700
All | A,B,C | R/W | NV | 172 |  |  | -1 | High Alarm Latching Alarm Threshold | High Alarm Latching Alarm Threshold | AV103 | Percent | 1 | % of breaker size | 0-1000 | 600
All | A,B,C | R/W | NV | 173 |  |  | -1 | Low Alarm Latching Alarm Threshold | Low Alarm Latching Alarm Threshold | AV104 | Percent | 1 | % of breaker size | 0-1000 | 75
All | A,B,C | R/W | NV | 174 |  |  | -1 | Low Low Latching Alarm Threshold | Low Low Latching Alarm Threshold | AV105 | Percent | 1 | % of breaker size | 0-1000 | 25
All | A,B,C | R/W | NV | 175 |  |  | -1 | Non-Latching High Threshold | Non-Latching High Threshold | AV106 | Percent | 1 | % of breaker size | 0-1000 | 600
All | A,B,C | R/W | NV | 176 |  |  | -1 | Non-Latching Low Threshold | Non-Latching Low Threshold | AV107 | Percent | 1 | % of breaker size | 0-1000 | 50
All | A,B,C | R/W | NV | 177 |  |  | -1 | Non-Latching Hysteresis (0-100% percent of setpoint) | Non-Latching Hysteresis (0-100%) | AV108 | Percent | 1 | Non-Latching Hysteresis (% of setpoint) | 0-1000 | 50
Alarm Status
1 | A,B,C | R/W | NV | 178 |  |  |  | Branch Alarm Status | Branch 1 Alarm Status | AV109 | No-Units | 1 | Write 0 to alarm bits to clear alarms
Latching Alarms are cleared by writing a 0 to its alarm bit.
A write to a Non-Latching alarm is ignored
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-6: Reserved for future use (reads 0)
Bit 7: Reserved for High High Non-Latching Alarm (reads 0)
Bit 8: High Non-Latching Alarm
Bit 9: Low Non-Latching Alarm
Bit 10: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 11-15: Reserved for future use (reads 0)
2 | A,B,C | R/W | NV | 179 |  |  |  | Branch Alarm Status | Branch 2 Alarm Status | AV110 | No-Units | 1 | Write 0 to alarm bits to clear alarms
3 | A,B,C | R/W | NV | 180 |  |  |  | Branch Alarm Status | Branch 3 Alarm Status | AV111 | No-Units | 1 | Write 0 to alarm bits to clear alarms
4 | A,B,C | R/W | NV | 181 |  |  |  | Branch Alarm Status | Branch 4 Alarm Status | AV112 | No-Units | 1 | Write 0 to alarm bits to clear alarms
5 | A,B,C | R/W | NV | 182 |  |  |  | Branch Alarm Status | Branch 5 Alarm Status | AV113 | No-Units | 1 | Write 0 to alarm bits to clear alarms
6 | A,B,C | R/W | NV | 183 |  |  |  | Branch Alarm Status | Branch 6 Alarm Status | AV114 | No-Units | 1 | Write 0 to alarm bits to clear alarms
7 | A,B,C | R/W | NV | 184 |  |  |  | Branch Alarm Status | Branch 7 Alarm Status | AV115 | No-Units | 1 | Write 0 to alarm bits to clear alarms
8 | A,B,C | R/W | NV | 185 |  |  |  | Branch Alarm Status | Branch 8 Alarm Status | AV116 | No-Units | 1 | Write 0 to alarm bits to clear alarms
9 | A,B,C | R/W | NV | 186 |  |  |  | Branch Alarm Status | Branch 9 Alarm Status | AV117 | No-Units | 1 | Write 0 to alarm bits to clear alarms
10 | A,B,C | R/W | NV | 187 |  |  |  | Branch Alarm Status | Branch 10 Alarm Status | AV118 | No-Units | 1 | Write 0 to alarm bits to clear alarms
11 | A,B,C | R/W | NV | 188 |  |  |  | Branch Alarm Status | Branch 11 Alarm Status | AV119 | No-Units | 1 | Write 0 to alarm bits to clear alarms
12 | A,B,C | R/W | NV | 189 |  |  |  | Branch Alarm Status | Branch 12 Alarm Status | AV120 | No-Units | 1 | Write 0 to alarm bits to clear alarms
13 | A,B,C | R/W | NV | 190 |  |  |  | Branch Alarm Status | Branch 13 Alarm Status | AV121 | No-Units | 1 | Write 0 to alarm bits to clear alarms
14 | A,B,C | R/W | NV | 191 |  |  |  | Branch Alarm Status | Branch 14 Alarm Status | AV122 | No-Units | 1 | Write 0 to alarm bits to clear alarms
15 | A,B,C | R/W | NV | 192 |  |  |  | Branch Alarm Status | Branch 15 Alarm Status | AV123 | No-Units | 1 | Write 0 to alarm bits to clear alarms
16 | A,B,C | R/W | NV | 193 |  |  |  | Branch Alarm Status | Branch 16 Alarm Status | AV124 | No-Units | 1 | Write 0 to alarm bits to clear alarms
17 | A,B,C | R/W | NV | 194 |  |  |  | Branch Alarm Status | Branch 17 Alarm Status | AV125 | No-Units | 1 | Write 0 to alarm bits to clear alarms
18 | A,B,C | R/W | NV | 195 |  |  |  | Branch Alarm Status | Branch 18 Alarm Status | AV126 | No-Units | 1 | Write 0 to alarm bits to clear alarms
19 | A,B,C | R/W | NV | 196 |  |  |  | Branch Alarm Status | Branch 19 Alarm Status | AV127 | No-Units | 1 | Write 0 to alarm bits to clear alarms
20 | A,B,C | R/W | NV | 197 |  |  |  | Branch Alarm Status | Branch 20 Alarm Status | AV128 | No-Units | 1 | Write 0 to alarm bits to clear alarms
21 | A,B,C | R/W | NV | 198 |  |  |  | Branch Alarm Status | Branch 21 Alarm Status | AV129 | No-Units | 1 | Write 0 to alarm bits to clear alarms
22 | A,B,C | R/W | NV | 199 |  |  |  | Branch Alarm Status | Branch 22 Alarm Status | AV130 | No-Units | 1 | Write 0 to alarm bits to clear alarms
23 | A,B,C | R/W | NV | 200 |  |  |  | Branch Alarm Status | Branch 23 Alarm Status | AV131 | No-Units | 1 | Write 0 to alarm bits to clear alarms
24 | A,B,C | R/W | NV | 201 |  |  |  | Branch Alarm Status | Branch 24 Alarm Status | AV132 | No-Units | 1 | Write 0 to alarm bits to clear alarms
25 | A,B,C | R/W | NV | 202 |  |  |  | Branch Alarm Status | Branch 25 Alarm Status | AV133 | No-Units | 1 | Write 0 to alarm bits to clear alarms
26 | A,B,C | R/W | NV | 203 |  |  |  | Branch Alarm Status | Branch 26 Alarm Status | AV134 | No-Units | 1 | Write 0 to alarm bits to clear alarms
27 | A,B,C | R/W | NV | 204 |  |  |  | Branch Alarm Status | Branch 27 Alarm Status | AV135 | No-Units | 1 | Write 0 to alarm bits to clear alarms
28 | A,B,C | R/W | NV | 205 |  |  |  | Branch Alarm Status | Branch 28 Alarm Status | AV136 | No-Units | 1 | Write 0 to alarm bits to clear alarms
29 | A,B,C | R/W | NV | 206 |  |  |  | Branch Alarm Status | Branch 29 Alarm Status | AV137 | No-Units | 1 | Write 0 to alarm bits to clear alarms
30 | A,B,C | R/W | NV | 207 |  |  |  | Branch Alarm Status | Branch 30 Alarm Status | AV138 | No-Units | 1 | Write 0 to alarm bits to clear alarms
31 | A,B,C | R/W | NV | 208 |  |  |  | Branch Alarm Status | Branch 31 Alarm Status | AV139 | No-Units | 1 | Write 0 to alarm bits to clear alarms
32 | A,B,C | R/W | NV | 209 |  |  |  | Branch Alarm Status | Branch 32 Alarm Status | AV140 | No-Units | 1 | Write 0 to alarm bits to clear alarms
33 | A,B,C | R/W | NV | 210 |  |  |  | Branch Alarm Status | Branch 33 Alarm Status | AV141 | No-Units | 1 | Write 0 to alarm bits to clear alarms
34 | A,B,C | R/W | NV | 211 |  |  |  | Branch Alarm Status | Branch 34 Alarm Status | AV142 | No-Units | 1 | Write 0 to alarm bits to clear alarms
35 | A,B,C | R/W | NV | 212 |  |  |  | Branch Alarm Status | Branch 35 Alarm Status | AV143 | No-Units | 1 | Write 0 to alarm bits to clear alarms
36 | A,B,C | R/W | NV | 213 |  |  |  | Branch Alarm Status | Branch 36 Alarm Status | AV144 | No-Units | 1 | Write 0 to alarm bits to clear alarms
37 | A,B,C | R/W | NV | 214 |  |  |  | Branch Alarm Status | Branch 37 Alarm Status | AV145 | No-Units | 1 | Write 0 to alarm bits to clear alarms
38 | A,B,C | R/W | NV | 215 |  |  |  | Branch Alarm Status | Branch 38 Alarm Status | AV146 | No-Units | 1 | Write 0 to alarm bits to clear alarms
39 | A,B,C | R/W | NV | 216 |  |  |  | Branch Alarm Status | Branch 39 Alarm Status | AV147 | No-Units | 1 | Write 0 to alarm bits to clear alarms
40 | A,B,C | R/W | NV | 217 |  |  |  | Branch Alarm Status | Branch 40 Alarm Status | AV148 | No-Units | 1 | Write 0 to alarm bits to clear alarms
41 | A,B,C | R/W | NV | 218 |  |  |  | Branch Alarm Status | Branch 41 Alarm Status | AV149 | No-Units | 1 | Write 0 to alarm bits to clear alarms
42 | A,B,C | R/W | NV | 219 |  |  |  | Branch Alarm Status | Branch 42 Alarm Status | AV150 | No-Units | 1 | Write 0 to alarm bits to clear alarms
43 | A,B,C | R/W | NV | 220 |  |  |  | AUX Alarm Status | AUX Channel (phase 1) Alarm Status | AV151 | No-Units | 1 | Write 0 to alarm bits to clear alarms
44 | A,B,C | R/W | NV | 221 |  |  |  | AUX Alarm Status | AUX Channel (phase 2) Alarm Status | AV152 | No-Units | 1 | Write 0 to alarm bits to clear alarms
45 | A,B,C | R/W | NV | 222 |  |  |  | AUX Alarm Status | AUX Channel (phase 3) Alarm Status | AV153 | No-Units | 1 | Write 0 to alarm bits to clear alarms
46 | A,B,C | R/W | NV | 223 |  |  |  | AUX Alarm Status | AUX Channel (Neutral) Alarm Status | AV154 | No-Units | 1 | Write 0 to alarm bits to clear alarms
All | A,B,C | R | NV | 224 |  |  |  | Global Latching Alarm Status | Global Latching Alarm Status | AI56 | No-Units | 1 | (HHL;HL;LL;LLL;ON;Rsv;Rsv;Rsv;HVL;LVL)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-7: Reserved for future use (reads 0)
Bit 8: High Voltage Latching Alarm
Bit 9: Low Voltage Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
| A,B,C | R |  | 225 |  |  |  | Global Non-Latching Alarm Status | Global Non-Latching Alarm Status | AI57 | No-Units | 1 | (HL;LL;Rsv;Rsv;Rsv;Rsv;Rsv;Rsv;HVL;LVL)
Bit 0: High Non-Latching Alarm
Bit 1: Low Non-Latching Alarm
Bit 2-7: Reserved for future use (reads 0)
Bit 8: High Voltage Non-Latching Alarm
Bit 9: Low Voltage Non-Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
| A,B,C | R | NV | 226 |  |  |  | Global Most-Recent Latching Alarm Channel | Global Most-Recent Latching Alarm Ch | AI58 | No-Units | 1 | # of Most-Recent Channel (0=none) | 0-46, 0=none
| A,B,C | R | NV | 227 |  |  |  | Global Most-Recent Non-Latching Alarm Channel | Global Most-Recent Non-Latch Alarm Ch | AI59 | No-Units | 1 | # of Most-Recent Channel (0=none) | 0-46, 0=none
| A,B,C | R |  | 228 |  |  |  | Total number of channels in alarm (based on latching alarms) | Total number of Latch ch in alarm | AI60 | No-Units | 1 | # alarm chan (non-latching alarms)
| A,B,C | R |  | 229 |  |  |  | Total number of channels in alarm (based on non-latching alarms) | Total number of non-Latch ch in alarm | AI61 | No-Units | 1 | # alarm chan (based on latching alarms)
All | A,B,C | R/W | NV | 230 |  |  |  | Reserved for Non-Latching Alarm Status w/ all (reads 0) | Error Bitmap1 (placeholder - TBD) | AI62 | No-Units | 1 | Error Bitmap1 (placeholder - bits TBD)
Alarm Thresholds (cont.)
All | A,B,C | R/W | NV | 231 |  |  | -1 | Reserved for Non-Latching High High Threshold | Error Bitmap2 (placeholder - TBD) | AI63 | No-Units | 1 | Error Bitmap2 (placeholder - bits TBD) | 0-1000 | 0
All | A,B,C | R/W | NV | 232 |  |  | -1 | Reserved for Non-Latching Low Low Threshold | Error Bitmap3 (placeholder - TBD) | AI64 | No-Units | 1 | Error Bitmap3 (placeholder - bits TBD) | 0-1000 | 0
| A,B,C | R |  | 233 |  |  |  | Error Bitmap1 (placeholder - bits TBD) | Error Bitmap4 (placeholder - TBD) | AI65 | No-Units | 1 | Error Bitmap4 (placeholder - bits TBD)
| A,B,C | R |  | 234 |  |  |  | Error Bitmap2 (placeholder - bits TBD) | Error Bitmap5 (placeholder - TBD) | AI66 | No-Units | 1 | Error Bitmap5 (placeholder - bits TBD)
| A,B,C | R |  | 235 |  |  |  | Error Bitmap3 (placeholder - bits TBD) | Error Bitmap6 (placeholder - TBD) | AI67 | No-Units | 1 | Error Bitmap6 (placeholder - bits TBD)
L-L Voltage Alarm Timers (seconds)
These timers control entry into an alarm state. A return to a non-alarm state is instantaneous.
All channels use these same global timers.
Note that the paraCircuit measurement update rate is 1.6 secs, which will limit the effective resolution of these timers.
| A,B | R/W | NV | 236 |  |  |  | Overvoltage Alarm Timer | Overvoltage Alarm Timer | AV155 | Seconds | 1 | Alarm event duration threshold | 0-32767
| A,B | R/W | NV | 237 |  |  |  | Undervoltage Alarm Timer | Undervoltage Alarm Timer | AV156 | Seconds | 1 | Alarm event duration threshold | 0-32767
L-L VOLTAGE ALARM THRESHOLDS
All voltage alarm thresholds are expressed as Volts.
All Line-to-Line voltage channels use the same thresholds
An entry of 0 for any threshold disables that alarm for all channels.
Hysteresis is scaled by -1 to increase the precision by 1 decimal point
Hysteresis only applies to Non-Latching Alarms
| A,B | R/W | NV | 238 |  |  | 244 | Overvoltage Alarm Threshold | Overvoltage Alarm Threshold | AV157 | Volts | 5 | Overvoltage level threshold (0=OFF) | 0-32767
| A,B | R/W | NV | 239 |  |  | 244 | Undervoltage Alarm Threshold | Undervoltage Alarm Threshold | AV158 | Volts | 5 | Undervoltage level threshold (0=OFF) | 0-32767
| A,B | R/W | NV | 240 |  |  | -1 | Voltage Alarm Hysteresis (percentage of setpoint) | Voltage Alarm Hysteresis | AV159 | Percent | 1 | Voltage Alarm Hysteresis (% of setpoint) | 0-1000
L-L Voltage Alarm Status
1 | A,B | R/W | NV | 241 |  |  |  | Voltage Alarm Status | Voltage 1 Alarm Status | AV160 | No-Units | 1 | Write 0 to alarm bits to clear alarms
Latching Alarms are cleared by writing a 0 to it's alarm bit.
A write to a Non-Latching alarm is ignored
Bit 0: High Latching Alarm
Bit 1: Low Latching Alarm
Bit 2-7: Reserved for future use (reads 0)
Bit 8: High Non-Latching Alarm
Bit 9: Low Non-Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
2 | A,B | R/W | NV | 242 |  |  |  | Voltage Alarm Status | Voltage 2 Alarm Status | AV161 | No-Units | 1 | Write 0 to alarm bits to clear alarms
3 | A,B | R/W | NV | 243 |  |  |  | Voltage Alarm Status | Voltage 3 Alarm Status | AV162 | No-Units | 1 | Write 0 to alarm bits to clear alarms
VOLTAGE INPUTS
| A,B | R | NV | 244 |  |  |  | Voltage Scale Register
| A,B | R |  | 245 | 600 | 601 | -2 | Frequency (derived from Phase A) | Frequency | AI1 | Hertz | 0.01 | Frequency (derived from Phase A) | 40-70
| A,B | R |  | 246 | 602 | 603 | 244 | VOLTS L-N 3ph Ave | VOLTS L-N: 3ph Ave | AI2 | Volts | 5 | Voltage L-N - average of active phases
| A,B | R |  | 247 | 604 | 605 | 244 | VOLTS L-L 3ph Ave | VOLTS L-L: 3ph Ave | AI3 | Volts | 5 | Voltage L-L - average of active phases
| A,B | R |  | 248 | 606 | 607 | 244 | VOLTS A-N | VOLTS A-N | AI4 | Volts | 5 | Instantaneous Voltage Ph-A to Neutral
| A,B | R |  | 249 | 608 | 609 | 244 | VOLTS B-N | VOLTS B-N | AI5 | Volts | 5 | Instantaneous Voltage Ph-B to Neutral
| A,B | R |  | 250 | 610 | 611 | 244 | VOLTS C-N | VOLTS C-N | AI6 | Volts | 5 | Instantaneous Voltage Ph-C to Neutral
| A,B | R |  | 251 | 612 | 613 | 244 | VOLTS A-B | VOLTS A-B | AI7 | Volts | 5 | Instantaneous Voltage Phase A to B
| A,B | R |  | 252 | 614 | 615 | 244 | VOLTS B-C | VOLTS B-C | AI8 | Volts | 5 | Instantaneous Voltage Phase B to C
| A,B | R |  | 253 | 616 | 617 | 244 | VOLTS C-A | VOLTS A-C | AI9 | Volts | 5 | Instantaneous Voltage Phase A to C
AUX INPUTS
Voltage/Current Phasing
| AUX CT |  | Voltage |  | Current
| Channel |  | Phase |  | Phase
| 1 |  | A |  | 1
| 2 |  | B |  | 2
| 3 |  | C |  | 3
| 4 |  | none |  | 4
43-45 | A,B | R | NV | 254 | 618 | 619 | 291 | 3ph KWH (MSW) | kWh Energy: 3ph Total | AI10 | kWh | 0 | Real Energy - total of active phases
43-45 | A,B | R | NV | 255 |  |  |  | 3ph KWH (LSW)
43-45 | A,B | R |  | 256 | 620 | 621 | 292 | 3ph Total KW | kW: 3ph Total | AI11 | kW | 1 | Inst Real Power- total of active phases
43-45 | A,B | R |  | 257 | 622 | 623 | -3 | 3ph Total PF | Power Factor: 3ph Total | AI12 | PF | 0.01 | Inst Power Factor - average of phases | 0.0 - 1.0
43-45 | A,B,C | R |  | 258 | 624 | 625 | 293 | 3ph Average Current (phases 1,2,3) | Amps: 3ph Average (phases 1 2 3) | AI13 | Amperes | 5 | Inst Current- average of active phases
43 | A,B | R |  | 259 | 626 | 627 | 288 | KW Phase 1 | kW: Phase 1 | AI14 | kW | 1 | Instantaneous Real Power - Phase 1
44 | A,B | R |  | 260 | 628 | 629 | 289 | KW Phase 2 | kW: Phase 2 | AI15 | kW | 1 | Instantaneous Real Power - Phase 2
45 | A,B | R |  | 261 | 630 | 631 | 290 | KW Phase 3 | kW: Phase 3 | AI16 | kW | 1 | Instantaneous Real Power - Phase 3
43 | A,B | R |  | 262 | 632 | 633 | -3 | PF Phase 1 (+ for leading, - for lagging) | Power Factor: Phase 1 | AI17 | PF | 0.01 | Instantaneous Power Factor - Phase 1 | 0.0 - 1.0
44 | A,B | R |  | 263 | 634 | 635 | -3 | PF Phase 2 (+ for leading, - for lagging) | Power Factor: Phase 2 | AI18 | PF | 0.01 | Instantaneous Power Factor - Phase 2 | 0.0 - 1.0
45 | A,B | R |  | 264 | 636 | 637 | -3 | PF Phase 3 (+ for leading, - for lagging) | Power Factor: Phase 3 | AI19 | PF | 0.01 | Instantaneous Power Factor - Phase 3 | 0.0 - 1.0
43 | A,B,C | R |  | 265 | 638 | 639 | 284 | Current Phase 1 | Amps: Phase 1 | AI20 | Amperes | 5 | Instantaneous Current - Phase 1
44 | A,B,C | R |  | 266 | 640 | 641 | 285 | Current Phase 2 | Amps: Phase 2 | AI21 | Amperes | 5 | Instantaneous Current - Phase 2
45 | A,B,C | R |  | 267 | 642 | 643 | 286 | Current Phase 3 | Amps: Phase 3 | AI22 | Amperes | 5 | Instantaneous Current - Phase 3
46 | A,B,C | R |  | 268 | 644 | 645 | 287 | Current Phase 4 | Amps: Phase 4 (Neutral) | AI23 | Amperes | 5 | Instantaneous Neutral Current
43 | A,B,C | R |  | 269 | 646 | 647 | 284 | Present Current Demand Phase 1 | Amps Present Demand: Phase 1 | AI24 | Amperes | 5 | Present Current Demand - Phase 1
44 | A,B,C | R |  | 270 | 648 | 649 | 285 | Present Current Demand Phase 2 | Amps Present Demand: Phase 2 | AI25 | Amperes | 5 | Present Current Demand - Phase 2
45 | A,B,C | R |  | 271 | 650 | 651 | 286 | Present Current Demand Phase 3 | Amps Present Demand: Phase 3 | AI26 | Amperes | 5 | Present Current Demand - Phase 3
46 | A,B,C | R |  | 272 | 652 | 653 | 287 | Present Current Demand Phase 4 | Amps Present Demand: (Neutral) | AI27 | Amperes | 5 | Present Current Demand - Neutral
43 | A,B,C | R | NV | 273 | 654 | 655 | 284 | Max Current Demand Phase 1 | Amps Max Demand: Phase 1 | AI28 | Amperes | 5 | Max Current Demand - Phase 1
44 | A,B,C | R | NV | 274 | 656 | 657 | 285 | Max Current Demand Phase 2 | Amps Max Demand: Phase 2 | AI29 | Amperes | 5 | Max Current Demand - Phase 2
45 | A,B,C | R | NV | 275 | 658 | 659 | 286 | Max Current Demand Phase 3 | Amps Max Demand: Phase 3 | AI30 | Amperes | 5 | Max Current Demand - Phase 3
46 | A,B,C | R | NV | 276 | 660 | 661 | 287 | Max Current Demand Phase 4 | Amps Max Demand: (Neutral) | AI31 | Amperes | 5 | Max Current Demand - Neutral
43-45 | A,B | R |  | 277 | 662 | 663 | 292 | 3ph Present KW-Total Demand | kW Present Demand: 3ph Total | AI32 | kW | 1 | Real Power Present Demand - 3ph Total
43-45 | A,B | R | NV | 278 | 664 | 665 | 292 | 3ph Max KW-Total Demand | kW Max Demand: 3ph Total | AI33 | kW | 1 | Real Power Max Demand - 3ph Total
43 | A,B,C | R | NV | 279 | 666 | 667 | 284 | Max Current Phase 1 | Max Amps: Phase 1 | AI34 | Amperes | 5 | Max Instantaneous Current - Phase 1
44 | A,B,C | R | NV | 280 | 668 | 669 | 285 | Max Current Phase 2 | Max Amps: Phase 2 | AI35 | Amperes | 5 | Max Instantaneous Current - Phase 2
45 | A,B,C | R | NV | 281 | 670 | 671 | 286 | Max Current Phase 3 | Max Amps: Phase 3 | AI36 | Amperes | 5 | Max Instantaneous Current - Phase 3
46 | A,B,C | R | NV | 282 | 672 | 673 | 287 | Max Current Phase 4 | Max Amps: (Neutral) | AI37 | Amperes | 5 | Max Instantaneous Neutral Current
43-45 | A,B | R | NV | 283 | 674 | 675 | 292 | 3ph Max KW-Total | kW: 3ph Max | AI38 | kW | 1 | Max Instantaneous Real Power- 3ph Total
43 | A,B,C | R | NV | 284 |  |  |  | Current Scale Phase 1
44 | A,B,C | R | NV | 285 |  |  |  | Current Scale Phase 2
45 | A,B,C | R | NV | 286 |  |  |  | Current Scale Phase 3
46 | A,B,C | R | NV | 287 |  |  |  | Current Scale Phase 4
43 | A,B | R | NV | 288 |  |  |  | Power Scale Phase 1
44 | A,B | R | NV | 289 |  |  |  | Power Scale Phase 2
45 | A,B | R | NV | 290 |  |  |  | Power Scale Phase 3
43-45 | A,B | R | NV | 291 |  |  |  | Energy Scale (3ph)
43-45 | A,B | R | NV | 292 |  |  |  | Power Scale (3ph)
43-45 | A,B,C | R | NV | 293 |  |  |  | Current Scale 3ph (Avg)
All | A,B,C | W |  | 294 |  |  |  | AUX Resets - Write the listed value to perform the listed reset: | AUX Resets: Write value to reset | AO1 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
10203 = Clear KWH value to zero
29877 = Clear Max Current and Max KW values to zero
Global Resets
All | A,B,C | W |  | 295 |  |  |  | Global Reset - Write the listed value to perform the listed reset: | Global Resets: Write value to reset | AO2 | No-Units | 1 | 10203=kWh; others…
12345 = Reset Device
24658 = Clear Logical Circuits Assignments
26012 = Begin new Demand Sub-interval
26013 = Reset Demand
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
Global Latching Alarm Counters
Global Latching Alarm Counters are incremented each time any one of the 46 corresponding Latching Alarm Counters are incremented
All Global Counters will rollover to the value of 1
Values are saved over a power cycle
All | A,B,C | R | NV | 296 |  |  |  | High High Latching Alarm Global Counter | [5 empty] | 0-32767
All | A,B,C | R | NV | 297 |  |  |  | High Latching Alarm Global Counter | [5 empty] | 0-32767
All | A,B,C | R | NV | 298 |  |  |  | Low Latching Alarm Global Counter | [5 empty] | 0-32767
All | A,B,C | R | NV | 299 |  |  |  | Low Low Latching Alarm Global Counter | [5 empty] | 0-32767
All | A,B,C | R | NV | 300 |  |  |  | Latching Alarm OFF state Global Counter | [5 empty] | 0-32767
Latching Alarm Counters
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
1 | A,B,C | R |  | 301 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 302 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 303 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
4 | A,B,C | R |  | 304 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
5 | A,B,C | R |  | 305 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
6 | A,B,C | R |  | 306 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
7 | A,B,C | R |  | 307 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
8 | A,B,C | R |  | 308 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
9 | A,B,C | R |  | 309 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
10 | A,B,C | R |  | 310 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
11 | A,B,C | R |  | 311 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
12 | A,B,C | R |  | 312 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
13 | A,B,C | R |  | 313 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
14 | A,B,C | R |  | 314 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
15 | A,B,C | R |  | 315 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
16 | A,B,C | R |  | 316 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
17 | A,B,C | R |  | 317 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
18 | A,B,C | R |  | 318 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
19 | A,B,C | R |  | 319 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
20 | A,B,C | R |  | 320 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
21 | A,B,C | R |  | 321 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
22 | A,B,C | R |  | 322 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
23 | A,B,C | R |  | 323 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
24 | A,B,C | R |  | 324 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
25 | A,B,C | R |  | 325 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
26 | A,B,C | R |  | 326 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
27 | A,B,C | R |  | 327 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
28 | A,B,C | R |  | 328 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
29 | A,B,C | R |  | 329 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
30 | A,B,C | R |  | 330 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
31 | A,B,C | R |  | 331 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
32 | A,B,C | R |  | 332 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
33 | A,B,C | R |  | 333 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
34 | A,B,C | R |  | 334 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
35 | A,B,C | R |  | 335 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
36 | A,B,C | R |  | 336 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
37 | A,B,C | R |  | 337 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
38 | A,B,C | R |  | 338 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
39 | A,B,C | R |  | 339 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
40 | A,B,C | R |  | 340 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
41 | A,B,C | R |  | 341 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
42 | A,B,C | R |  | 342 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
43 | A,B,C | R |  | 343 |  |  |  | AUX High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
44 | A,B,C | R |  | 344 |  |  |  | AUX High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
45 | A,B,C | R |  | 345 |  |  |  | AUX High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
46 | A,B,C | R |  | 346 |  |  |  | AUX High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 347 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 348 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 349 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
4 | A,B,C | R |  | 350 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
5 | A,B,C | R |  | 351 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
6 | A,B,C | R |  | 352 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
7 | A,B,C | R |  | 353 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
8 | A,B,C | R |  | 354 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
9 | A,B,C | R |  | 355 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
10 | A,B,C | R |  | 356 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
11 | A,B,C | R |  | 357 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
12 | A,B,C | R |  | 358 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
13 | A,B,C | R |  | 359 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
14 | A,B,C | R |  | 360 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
15 | A,B,C | R |  | 361 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
16 | A,B,C | R |  | 362 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
17 | A,B,C | R |  | 363 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
18 | A,B,C | R |  | 364 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
19 | A,B,C | R |  | 365 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
20 | A,B,C | R |  | 366 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
21 | A,B,C | R |  | 367 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
22 | A,B,C | R |  | 368 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
23 | A,B,C | R |  | 369 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
24 | A,B,C | R |  | 370 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
25 | A,B,C | R |  | 371 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
26 | A,B,C | R |  | 372 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
27 | A,B,C | R |  | 373 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
28 | A,B,C | R |  | 374 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
29 | A,B,C | R |  | 375 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
30 | A,B,C | R |  | 376 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
31 | A,B,C | R |  | 377 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
32 | A,B,C | R |  | 378 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
33 | A,B,C | R |  | 379 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
34 | A,B,C | R |  | 380 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
35 | A,B,C | R |  | 381 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
36 | A,B,C | R |  | 382 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
37 | A,B,C | R |  | 383 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
38 | A,B,C | R |  | 384 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
39 | A,B,C | R |  | 385 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
40 | A,B,C | R |  | 386 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
41 | A,B,C | R |  | 387 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
42 | A,B,C | R |  | 388 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
43 | A,B,C | R |  | 389 |  |  |  | AUX High Latching Alarm Counter | [5 empty] | 0-10922 | 0
44 | A,B,C | R |  | 390 |  |  |  | AUX High Latching Alarm Counter | [5 empty] | 0-10922 | 0
45 | A,B,C | R |  | 391 |  |  |  | AUX High Latching Alarm Counter | [5 empty] | 0-10922 | 0
46 | A,B,C | R |  | 392 |  |  |  | AUX High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 393 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 394 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 395 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
4 | A,B,C | R |  | 396 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
5 | A,B,C | R |  | 397 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
6 | A,B,C | R |  | 398 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
7 | A,B,C | R |  | 399 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
8 | A,B,C | R |  | 400 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
9 | A,B,C | R |  | 401 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
10 | A,B,C | R |  | 402 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
11 | A,B,C | R |  | 403 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
12 | A,B,C | R |  | 404 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
13 | A,B,C | R |  | 405 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
14 | A,B,C | R |  | 406 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
15 | A,B,C | R |  | 407 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
16 | A,B,C | R |  | 408 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
17 | A,B,C | R |  | 409 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
18 | A,B,C | R |  | 410 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
19 | A,B,C | R |  | 411 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
20 | A,B,C | R |  | 412 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
21 | A,B,C | R |  | 413 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
22 | A,B,C | R |  | 414 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
23 | A,B,C | R |  | 415 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
24 | A,B,C | R |  | 416 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
25 | A,B,C | R |  | 417 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
26 | A,B,C | R |  | 418 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
27 | A,B,C | R |  | 419 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
28 | A,B,C | R |  | 420 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
29 | A,B,C | R |  | 421 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
30 | A,B,C | R |  | 422 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
31 | A,B,C | R |  | 423 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
32 | A,B,C | R |  | 424 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
33 | A,B,C | R |  | 425 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
34 | A,B,C | R |  | 426 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
35 | A,B,C | R |  | 427 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
36 | A,B,C | R |  | 428 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
37 | A,B,C | R |  | 429 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
38 | A,B,C | R |  | 430 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
39 | A,B,C | R |  | 431 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
40 | A,B,C | R |  | 432 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
41 | A,B,C | R |  | 433 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
42 | A,B,C | R |  | 434 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
43 | A,B,C | R |  | 435 |  |  |  | AUX Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
44 | A,B,C | R |  | 436 |  |  |  | AUX Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
45 | A,B,C | R |  | 437 |  |  |  | AUX Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
46 | A,B,C | R |  | 438 |  |  |  | AUX Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 439 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 440 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 441 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
4 | A,B,C | R |  | 442 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
5 | A,B,C | R |  | 443 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
6 | A,B,C | R |  | 444 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
7 | A,B,C | R |  | 445 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
8 | A,B,C | R |  | 446 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
9 | A,B,C | R |  | 447 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
10 | A,B,C | R |  | 448 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
11 | A,B,C | R |  | 449 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
12 | A,B,C | R |  | 450 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
13 | A,B,C | R |  | 451 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
14 | A,B,C | R |  | 452 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
15 | A,B,C | R |  | 453 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
16 | A,B,C | R |  | 454 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
17 | A,B,C | R |  | 455 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
18 | A,B,C | R |  | 456 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
19 | A,B,C | R |  | 457 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
20 | A,B,C | R |  | 458 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
21 | A,B,C | R |  | 459 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
22 | A,B,C | R |  | 460 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
23 | A,B,C | R |  | 461 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
24 | A,B,C | R |  | 462 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
25 | A,B,C | R |  | 463 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
26 | A,B,C | R |  | 464 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
27 | A,B,C | R |  | 465 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
28 | A,B,C | R |  | 466 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
29 | A,B,C | R |  | 467 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
30 | A,B,C | R |  | 468 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
31 | A,B,C | R |  | 469 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
32 | A,B,C | R |  | 470 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
33 | A,B,C | R |  | 471 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
34 | A,B,C | R |  | 472 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
35 | A,B,C | R |  | 473 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
36 | A,B,C | R |  | 474 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
37 | A,B,C | R |  | 475 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
38 | A,B,C | R |  | 476 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
39 | A,B,C | R |  | 477 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
40 | A,B,C | R |  | 478 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
41 | A,B,C | R |  | 479 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
42 | A,B,C | R |  | 480 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
43 | A,B,C | R |  | 481 |  |  |  | AUX Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
44 | A,B,C | R |  | 482 |  |  |  | AUX Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
45 | A,B,C | R |  | 483 |  |  |  | AUX Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
46 | A,B,C | R |  | 484 |  |  |  | AUX Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 485 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 486 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 487 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
4 | A,B,C | R |  | 488 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
5 | A,B,C | R |  | 489 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
6 | A,B,C | R |  | 490 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
7 | A,B,C | R |  | 491 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
8 | A,B,C | R |  | 492 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
9 | A,B,C | R |  | 493 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
10 | A,B,C | R |  | 494 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
11 | A,B,C | R |  | 495 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
12 | A,B,C | R |  | 496 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
13 | A,B,C | R |  | 497 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
14 | A,B,C | R |  | 498 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
15 | A,B,C | R |  | 499 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
16 | A,B,C | R |  | 500 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
17 | A,B,C | R |  | 501 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
18 | A,B,C | R |  | 502 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
19 | A,B,C | R |  | 503 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
20 | A,B,C | R |  | 504 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
21 | A,B,C | R |  | 505 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
22 | A,B,C | R |  | 506 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
23 | A,B,C | R |  | 507 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
24 | A,B,C | R |  | 508 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
25 | A,B,C | R |  | 509 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
26 | A,B,C | R |  | 510 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
27 | A,B,C | R |  | 511 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
28 | A,B,C | R |  | 512 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
29 | A,B,C | R |  | 513 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
30 | A,B,C | R |  | 514 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
31 | A,B,C | R |  | 515 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
32 | A,B,C | R |  | 516 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
33 | A,B,C | R |  | 517 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
34 | A,B,C | R |  | 518 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
35 | A,B,C | R |  | 519 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
36 | A,B,C | R |  | 520 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
37 | A,B,C | R |  | 521 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
38 | A,B,C | R |  | 522 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
39 | A,B,C | R |  | 523 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
40 | A,B,C | R |  | 524 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
41 | A,B,C | R |  | 525 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
42 | A,B,C | R |  | 526 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
43 | A,B,C | R |  | 527 |  |  |  | AUX Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
44 | A,B,C | R |  | 528 |  |  |  | AUX Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
45 | A,B,C | R |  | 529 |  |  |  | AUX Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
46 | A,B,C | R |  | 530 |  |  |  | AUX Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
Diagnostic Registers
| A,B,C | R/W | NV | 531 |  |  |  | Power Up Counter | Power Up Counter | AV163 | No-Units | 1 | Power Up Counter | 0-32767 | 0
| A,B,C | R |  | 532 |  |  |  | Device Health | Device Health | AI43 | No-Units | 1 | Bit Map of Device Health Indicators
Bit 0: Reserved
Bit 1: Frequency Out of Range or insufficient voltage on Phase A
to determine frequency range. *Frequency Range is 40-70 Hz.
Bit 2: Phase A Voltage Clipping
Bit 3: Phase B Voltage Clipping
Bit 4: Phase C Voltage Clipping
Bit 5: Current Clipping on at least 1 channel (AUX & Circuit)
Bit 6-7: Reserved
Bit 8: Strip Connection Error
Bit 9-12: Reserved
Bit 13: Current Model, Model C
Bit 14: Power Model, Model B
Bit 15: Branch Power, Model A
| A,B,C | R |  | 533 |  |  |  | Reserved for future use | Reserved for future use | AI44 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 534 |  |  |  | Reserved for future use | Reserved for future use | AI45 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 535 |  |  |  | Reserved for future use | Reserved for future use | AI46 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 536 |  |  |  | Reserved for future use | Reserved for future use | AI47 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 537 |  |  |  | Reserved for future use | Reserved for future use | AI48 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 538 |  |  |  | Reserved for future use | Reserved for future use | AI49 | No-Units | 1 | Reserved for future use
| A,B,C | R |  | 539 |  |  |  | Product ID | Product ID | AI50 | No-Units | 1 | bit Map of Model configuration
Bit 0: Default Solid-Core
Bit 1: Default Split-Core
Bit 3-9: Reserved
Bit 10: Reserved
Bit 11: Logical Circuits Capable
Bit 12: Custom V-Phase Capable
Bit 13: Reserved (Model C)
Bit 14: Reserved (Model B)
Bit 15: Reserved (Model A)
AUX INPUTS (cont.)
43-45 | A,B | R |  | 540 | 676 | 677 | 292 | 3ph Total KVA | kVA: 3ph Total | AI39 | kVA | 1 | Instantaneous Apparent Power- 3ph Total
43 | A,B | R |  | 541 | 678 | 679 | 288 | KVA Phase 1 | kVA: Phase 1 | AI40 | kVA | 1 | Instantaneous Apparent Power - Phase 1
44 | A,B | R |  | 542 | 680 | 681 | 289 | KVA Phase 2 | kVA: Phase 2 | AI41 | kVA | 1 | Instantaneous Apparent Power - Phase 2
45 | A,B | R |  | 543 | 682 | 683 | 290 | KVA Phase 3 | kVA: Phase 3 | AI42 | kVA | 1 | Instantaneous Apparent Power - Phase 3
|  | R |  | 544 | 684 | 685 |  | Reserved
43 | A,B | R |  | 545 | 686 | 687 | -1 | Amperage Angle Aux. Phase 1 (selectable in User Defined Status Register - 62017) | Amp Phase Angle: Aux Phase 1 (Ch 43) | AI530 | degrees-phase | 10 | Amperage Phase Angle - Aux ph1 (Ch 43)
44 | A,B | R |  | 546 | 688 | 689 | -1 | Amperage Angle Aux. Phase 2 (selectable in User Defined Status Register - 62017) | Amp Phase Angle: Aux Phase 2 (Ch 44) | AI531 | degrees-phase | 10 | Amperage Phase Angle - Aux ph2 (Ch 44)
45 | A,B | R |  | 547 | 690 | 691 | -1 | Amperage Angle Aux. Phase 3 (selectable in User Defined Status Register - 62017) | Amp Phase Angle: Aux Phase 3 (Ch 45) | AI532 | degrees-phase | 10 | Amperage Phase Angle - Aux ph3 (Ch 45)
|  | R |  | 548 | 692 | 693 |  | Reserved
VOLTAGE INPUTS (cont.)
| A,B | R |  | 549 | 694 | 695 | -1 | V1 Phase Angle (reference phase, always 0) | Voltage Phase Angle - V1 | AI533 | degrees-phase | 10 | Voltage Phase Angle - Aux ph1 (Ch 43)
| A,B | R |  | 550 | 696 | 697 | -1 | V2 Phase Angle (in relation to V1) | Voltage Phase Angle - V2 | AI534 | degrees-phase | 10 | Voltage Phase Angle - Aux ph2 (Ch 44)
| A,B | R |  | 551 | 698 | 699 | -1 | V3 Phase Angle (in relation to V1) | Voltage Phase Angle - V3 | AI535 | degrees-phase | 10 | Voltage Phase Angle - Aux ph3 (Ch 45)
Energy Snapshot
43-45 | A,B | R |  | 552 | 700 | 701 | 291 | 3ph KWH Snapshot (MSW)
43-45 | A,B | R |  | 553 |  |  |  | 3ph KWH Snapshot (LSW)
Real Time Clock
Time is always in UTC
| A,B,C | R/W |  | 554 |  |  |  | Year (as years since 2000, ie 14 = 2014) | [5 empty] | 0-2095 | 0
| A,B,C | R/W |  | 555 |  |  |  | Month (MSB) Day (LSB) 0x0201 = Feb 1st | [5 empty] | 1-31,1-12 | 0x0101
| A,B,C | R/W |  | 556 |  |  |  | Hour (MSB) Minute (LSB) 0x0D1E = 1:30 PM | [5 empty] | 0-23,0-59 | 0x0000
| A,B,C | R/W |  | 557 |  |  |  | Milliseconds - RTC starts on write to this register | [5 empty] | 0-59000 | 0
Demand/Snapshot Time Stamp
Time is always in UTC
| A,B,C | R |  | 558 |  |  |  | Year (as years since 2000, ie 14 = 2014) | [5 empty] | 0-2095 | 0
| A,B,C | R |  | 559 |  |  |  | Month (MSB) Day (LSB) 0x0201 = Feb 1st | [5 empty] | 1-31,1-12 | 0x0101
| A,B,C | R |  | 560 |  |  |  | Hour (MSB) Minute (LSB) 0x0D1E = 1:30 PM | [5 empty] | 0-23,0-59 | 0x0000
| A,B,C | R |  | 561 |  |  |  | Milliseconds | [5 empty] | 0-59000 | 0
FW Download Support
| A,B,C | R |  | 60000 |  |  |  | Modbus Address (based on DIPswitch settings)
| A,B,C | R |  | 60001 |  |  |  | Baudrate (based on DIPswitch settings)
| A,B,C | R |  | 60002 |  |  |  | Password (always reads 0)
| A,B,C | R |  | 60003 |  |  |  | Selftest (always reads 0)
| A,B,C | R |  | 60004 |  |  |  | PLOS (reads 0 if application missing, reads > 0 if application running)
| A,B,C | R/W |  | 60005 |  |  |  | Command interface
through
60153
EEPROM Update Support
| A,B,C | W |  | 61000 |  |  |  | EEPROM Update Password
| A,B,C | R/W |  | 61001 |  |  |  | EEPROM Strip Select
| A,B,C | R/W |  | 61002 |  |  |  | EEPROM Address LSW
| A,B,C | R/W |  | 61003 |  |  |  | EEPROM Address MSW
| A,B,C | R/W |  | 61004 |  |  |  | EEPROM Data Byte Registers
through
61129
User Defined Settings
all | A,B,C | R/W | NV | 62017 |  |  |  | User Defined Settings Status Register Bit 0: Enable User CT Phase Assignment Bit 1: Phase Angle Ref. (0 - V1, 1 - Assigned V-phase) Bit 2: Signed Power (Split-Core Only) Bit 3: Signed Power Factor (sign denotes lead/lag) Bit 4: Disable 2PH/3PH Pointmap Bit 5: Disable Second Panel Modbus Address Bit 6: Use Trig. Identity for 2PH KVA/PF Calculations Bit 7: Use RTC for Demand Sync. Bit 8-15: Reserved | User Defined Status Register | AV164 | No-Units | 1 | 1 in bit 0 enables CT phase assignment |  | 0
Logical Circuit (Breaker) Assignment
Logical Circuit Assignment will be cleared if Configuration Register is Changed, set Configuration first
Logical Circuits should be unassigned before a block write. Global Resets Clear Logical Circuits Assignments command can be used for this.
1 | A,B,C | R/W | NV | 62068 |  |  |  | Circuit # for Branch Channel 1 | Logical Circuit for Branch Channel 1 | AV210 | No-Units | 1 | Logical Circuit Number for Branch Channel 1 | 0 - unassigned 0-46 | 0
2 | A,B,C | R/W | NV | 62069 |  |  |  | Circuit # for Branch Channel 2 | Logical Circuit for Branch Channel 2 | AV211 | No-Units | 1 | Logical Circuit Number for Branch Channel 2 | 0-46 | 0
3 | A,B,C | R/W | NV | 62070 |  |  |  | Circuit # for Branch Channel 3 | Logical Circuit for Branch Channel 3 | AV212 | No-Units | 1 | Logical Circuit Number for Branch Channel 3 | 0-46 | 0
4 | A,B,C | R/W | NV | 62071 |  |  |  | Circuit # for Branch Channel 4 | Logical Circuit for Branch Channel 4 | AV213 | No-Units | 1 | Logical Circuit Number for Branch Channel 4 | 0-46 | 0
5 | A,B,C | R/W | NV | 62072 |  |  |  | Circuit # for Branch Channel 5 | Logical Circuit for Branch Channel 5 | AV214 | No-Units | 1 | Logical Circuit Number for Branch Channel 5 | 0-46 | 0
6 | A,B,C | R/W | NV | 62073 |  |  |  | Circuit # for Branch Channel 6 | Logical Circuit for Branch Channel 6 | AV215 | No-Units | 1 | Logical Circuit Number for Branch Channel 6 | 0-46 | 0
7 | A,B,C | R/W | NV | 62074 |  |  |  | Circuit # for Branch Channel 7 | Logical Circuit for Branch Channel 7 | AV216 | No-Units | 1 | Logical Circuit Number for Branch Channel 7 | 0-46 | 0
8 | A,B,C | R/W | NV | 62075 |  |  |  | Circuit # for Branch Channel 8 | Logical Circuit for Branch Channel 8 | AV217 | No-Units | 1 | Logical Circuit Number for Branch Channel 8 | 0-46 | 0
9 | A,B,C | R/W | NV | 62076 |  |  |  | Circuit # for Branch Channel 9 | Logical Circuit for Branch Channel 9 | AV218 | No-Units | 1 | Logical Circuit Number for Branch Channel 9 | 0-46 | 0
10 | A,B,C | R/W | NV | 62077 |  |  |  | Circuit # for Branch Channel 10 | Logical Circuit for Branch Channel 10 | AV219 | No-Units | 1 | Logical Circuit Number for Branch Channel 10 | 0-46 | 0
11 | A,B,C | R/W | NV | 62078 |  |  |  | Circuit # for Branch Channel 11 | Logical Circuit for Branch Channel 11 | AV220 | No-Units | 1 | Logical Circuit Number for Branch Channel 11 | 0-46 | 0
12 | A,B,C | R/W | NV | 62079 |  |  |  | Circuit # for Branch Channel 12 | Logical Circuit for Branch Channel 12 | AV221 | No-Units | 1 | Logical Circuit Number for Branch Channel 12 | 0-46 | 0
13 | A,B,C | R/W | NV | 62080 |  |  |  | Circuit # for Branch Channel 13 | Logical Circuit for Branch Channel 13 | AV222 | No-Units | 1 | Logical Circuit Number for Branch Channel 13 | 0-46 | 0
14 | A,B,C | R/W | NV | 62081 |  |  |  | Circuit # for Branch Channel 14 | Logical Circuit for Branch Channel 14 | AV223 | No-Units | 1 | Logical Circuit Number for Branch Channel 14 | 0-46 | 0
15 | A,B,C | R/W | NV | 62082 |  |  |  | Circuit # for Branch Channel 15 | Logical Circuit for Branch Channel 15 | AV224 | No-Units | 1 | Logical Circuit Number for Branch Channel 15 | 0-46 | 0
16 | A,B,C | R/W | NV | 62083 |  |  |  | Circuit # for Branch Channel 16 | Logical Circuit for Branch Channel 16 | AV225 | No-Units | 1 | Logical Circuit Number for Branch Channel 16 | 0-46 | 0
17 | A,B,C | R/W | NV | 62084 |  |  |  | Circuit # for Branch Channel 17 | Logical Circuit for Branch Channel 17 | AV226 | No-Units | 1 | Logical Circuit Number for Branch Channel 17 | 0-46 | 0
18 | A,B,C | R/W | NV | 62085 |  |  |  | Circuit # for Branch Channel 18 | Logical Circuit for Branch Channel 18 | AV227 | No-Units | 1 | Logical Circuit Number for Branch Channel 18 | 0-46 | 0
19 | A,B,C | R/W | NV | 62086 |  |  |  | Circuit # for Branch Channel 19 | Logical Circuit for Branch Channel 19 | AV228 | No-Units | 1 | Logical Circuit Number for Branch Channel 19 | 0-46 | 0
20 | A,B,C | R/W | NV | 62087 |  |  |  | Circuit # for Branch Channel 20 | Logical Circuit for Branch Channel 20 | AV229 | No-Units | 1 | Logical Circuit Number for Branch Channel 20 | 0-46 | 0
21 | A,B,C | R/W | NV | 62088 |  |  |  | Circuit # for Branch Channel 21 | Logical Circuit for Branch Channel 21 | AV230 | No-Units | 1 | Logical Circuit Number for Branch Channel 21 | 0-46 | 0
22 | A,B,C | R/W | NV | 62089 |  |  |  | Circuit # for Branch Channel 22 | Logical Circuit for Branch Channel 22 | AV231 | No-Units | 1 | Logical Circuit Number for Branch Channel 22 | 0-46 | 0
23 | A,B,C | R/W | NV | 62090 |  |  |  | Circuit # for Branch Channel 23 | Logical Circuit for Branch Channel 23 | AV232 | No-Units | 1 | Logical Circuit Number for Branch Channel 23 | 0-46 | 0
24 | A,B,C | R/W | NV | 62091 |  |  |  | Circuit # for Branch Channel 24 | Logical Circuit for Branch Channel 24 | AV233 | No-Units | 1 | Logical Circuit Number for Branch Channel 24 | 0-46 | 0
25 | A,B,C | R/W | NV | 62092 |  |  |  | Circuit # for Branch Channel 25 | Logical Circuit for Branch Channel 25 | AV234 | No-Units | 1 | Logical Circuit Number for Branch Channel 25 | 0-46 | 0
26 | A,B,C | R/W | NV | 62093 |  |  |  | Circuit # for Branch Channel 26 | Logical Circuit for Branch Channel 26 | AV235 | No-Units | 1 | Logical Circuit Number for Branch Channel 26 | 0-46 | 0
27 | A,B,C | R/W | NV | 62094 |  |  |  | Circuit # for Branch Channel 27 | Logical Circuit for Branch Channel 27 | AV236 | No-Units | 1 | Logical Circuit Number for Branch Channel 27 | 0-46 | 0
28 | A,B,C | R/W | NV | 62095 |  |  |  | Circuit # for Branch Channel 28 | Logical Circuit for Branch Channel 28 | AV237 | No-Units | 1 | Logical Circuit Number for Branch Channel 28 | 0-46 | 0
29 | A,B,C | R/W | NV | 62096 |  |  |  | Circuit # for Branch Channel 29 | Logical Circuit for Branch Channel 29 | AV238 | No-Units | 1 | Logical Circuit Number for Branch Channel 29 | 0-46 | 0
30 | A,B,C | R/W | NV | 62097 |  |  |  | Circuit # for Branch Channel 30 | Logical Circuit for Branch Channel 30 | AV239 | No-Units | 1 | Logical Circuit Number for Branch Channel 30 | 0-46 | 0
31 | A,B,C | R/W | NV | 62098 |  |  |  | Circuit # for Branch Channel 31 | Logical Circuit for Branch Channel 31 | AV240 | No-Units | 1 | Logical Circuit Number for Branch Channel 31 | 0-46 | 0
32 | A,B,C | R/W | NV | 62099 |  |  |  | Circuit # for Branch Channel 32 | Logical Circuit for Branch Channel 32 | AV241 | No-Units | 1 | Logical Circuit Number for Branch Channel 32 | 0-46 | 0
33 | A,B,C | R/W | NV | 62100 |  |  |  | Circuit # for Branch Channel 33 | Logical Circuit for Branch Channel 33 | AV242 | No-Units | 1 | Logical Circuit Number for Branch Channel 33 | 0-46 | 0
34 | A,B,C | R/W | NV | 62101 |  |  |  | Circuit # for Branch Channel 34 | Logical Circuit for Branch Channel 34 | AV243 | No-Units | 1 | Logical Circuit Number for Branch Channel 34 | 0-46 | 0
35 | A,B,C | R/W | NV | 62102 |  |  |  | Circuit # for Branch Channel 35 | Logical Circuit for Branch Channel 35 | AV244 | No-Units | 1 | Logical Circuit Number for Branch Channel 35 | 0-46 | 0
36 | A,B,C | R/W | NV | 62103 |  |  |  | Circuit # for Branch Channel 36 | Logical Circuit for Branch Channel 36 | AV245 | No-Units | 1 | Logical Circuit Number for Branch Channel 36 | 0-46 | 0
37 | A,B,C | R/W | NV | 62104 |  |  |  | Circuit # for Branch Channel 37 | Logical Circuit for Branch Channel 37 | AV246 | No-Units | 1 | Logical Circuit Number for Branch Channel 37 | 0-46 | 0
38 | A,B,C | R/W | NV | 62105 |  |  |  | Circuit # for Branch Channel 38 | Logical Circuit for Branch Channel 38 | AV247 | No-Units | 1 | Logical Circuit Number for Branch Channel 38 | 0-46 | 0
39 | A,B,C | R/W | NV | 62106 |  |  |  | Circuit # for Branch Channel 39 | Logical Circuit for Branch Channel 39 | AV248 | No-Units | 1 | Logical Circuit Number for Branch Channel 39 | 0-46 | 0
40 | A,B,C | R/W | NV | 62107 |  |  |  | Circuit # for Branch Channel 40 | Logical Circuit for Branch Channel 40 | AV249 | No-Units | 1 | Logical Circuit Number for Branch Channel 40 | 0-46 | 0
41 | A,B,C | R/W | NV | 62108 |  |  |  | Circuit # for Branch Channel 41 | Logical Circuit for Branch Channel 41 | AV250 | No-Units | 1 | Logical Circuit Number for Branch Channel 41 | 0-46 | 0
42 | A,B,C | R/W | NV | 62109 |  |  |  | Circuit # for Branch Channel 42 | Logical Circuit for Branch Channel 42 | AV251 | No-Units | 1 | Logical Circuit Number for Branch Channel 42 | 0-46 | 0
43 | A,B,C | R/W | NV | 62110 |  |  |  | Circuit # for Aux Channel 1 | Logical Circuit for Aux Channel 1 | AV252 | No-Units | 1 | Logical Circuit Number for Aux Channel 1 | 0-46 | 0
44 | A,B,C | R/W | NV | 62111 |  |  |  | Circuit # for Aux Channel 2 | Logical Circuit for Aux Channel 2 | AV253 | No-Units | 1 | Logical Circuit Number for Aux Channel 2 | 0-46 | 0
45 | A,B,C | R/W | NV | 62112 |  |  |  | Circuit # for Aux Channel 3 | Logical Circuit for Aux Channel 3 | AV254 | No-Units | 1 | Logical Circuit Number for Aux Channel 3 | 0-46 | 0
46 | A,B,C | R/W | NV | 62113 |  |  |  | Circuit # for Aux Channel 4 | [5 empty] | 0-46 | 0
Custom Phase Map Support
1 | A | R/W | NV | 62116 |  |  |  | Voltage Phase for Branch Channel 1 | Voltage Phase for Branch Channel 1 | AV165 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 0 - Phase A 1 - Phase B 2 - Phase C | 0
2 | A | R/W | NV | 62117 |  |  |  | Voltage Phase for Branch Channel 2 | Voltage Phase for Branch Channel 2 | AV166 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
3 | A | R/W | NV | 62118 |  |  |  | Voltage Phase for Branch Channel 3 | Voltage Phase for Branch Channel 3 | AV167 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
4 | A | R/W | NV | 62119 |  |  |  | Voltage Phase for Branch Channel 4 | Voltage Phase for Branch Channel 4 | AV168 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
5 | A | R/W | NV | 62120 |  |  |  | Voltage Phase for Branch Channel 5 | Voltage Phase for Branch Channel 5 | AV169 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
6 | A | R/W | NV | 62121 |  |  |  | Voltage Phase for Branch Channel 6 | Voltage Phase for Branch Channel 6 | AV170 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
7 | A | R/W | NV | 62122 |  |  |  | Voltage Phase for Branch Channel 7 | Voltage Phase for Branch Channel 7 | AV171 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
8 | A | R/W | NV | 62123 |  |  |  | Voltage Phase for Branch Channel 8 | Voltage Phase for Branch Channel 8 | AV172 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
9 | A | R/W | NV | 62124 |  |  |  | Voltage Phase for Branch Channel 9 | Voltage Phase for Branch Channel 9 | AV173 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
10 | A | R/W | NV | 62125 |  |  |  | Voltage Phase for Branch Channel 10 | Voltage Phase for Branch Channel 10 | AV174 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
11 | A | R/W | NV | 62126 |  |  |  | Voltage Phase for Branch Channel 11 | Voltage Phase for Branch Channel 11 | AV175 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
12 | A | R/W | NV | 62127 |  |  |  | Voltage Phase for Branch Channel 12 | Voltage Phase for Branch Channel 12 | AV176 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
13 | A | R/W | NV | 62128 |  |  |  | Voltage Phase for Branch Channel 13 | Voltage Phase for Branch Channel 13 | AV177 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
14 | A | R/W | NV | 62129 |  |  |  | Voltage Phase for Branch Channel 14 | Voltage Phase for Branch Channel 14 | AV178 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
15 | A | R/W | NV | 62130 |  |  |  | Voltage Phase for Branch Channel 15 | Voltage Phase for Branch Channel 15 | AV179 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
16 | A | R/W | NV | 62131 |  |  |  | Voltage Phase for Branch Channel 16 | Voltage Phase for Branch Channel 16 | AV180 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
17 | A | R/W | NV | 62132 |  |  |  | Voltage Phase for Branch Channel 17 | Voltage Phase for Branch Channel 17 | AV181 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
18 | A | R/W | NV | 62133 |  |  |  | Voltage Phase for Branch Channel 18 | Voltage Phase for Branch Channel 18 | AV182 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
19 | A | R/W | NV | 62134 |  |  |  | Voltage Phase for Branch Channel 19 | Voltage Phase for Branch Channel 19 | AV183 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
20 | A | R/W | NV | 62135 |  |  |  | Voltage Phase for Branch Channel 20 | Voltage Phase for Branch Channel 20 | AV184 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
21 | A | R/W | NV | 62136 |  |  |  | Voltage Phase for Branch Channel 21 | Voltage Phase for Branch Channel 21 | AV185 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
22 | A | R/W | NV | 62137 |  |  |  | Voltage Phase for Branch Channel 22 | Voltage Phase for Branch Channel 22 | AV186 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
23 | A | R/W | NV | 62138 |  |  |  | Voltage Phase for Branch Channel 23 | Voltage Phase for Branch Channel 23 | AV187 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
24 | A | R/W | NV | 62139 |  |  |  | Voltage Phase for Branch Channel 24 | Voltage Phase for Branch Channel 24 | AV188 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
25 | A | R/W | NV | 62140 |  |  |  | Voltage Phase for Branch Channel 25 | Voltage Phase for Branch Channel 25 | AV189 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
26 | A | R/W | NV | 62141 |  |  |  | Voltage Phase for Branch Channel 26 | Voltage Phase for Branch Channel 26 | AV190 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
27 | A | R/W | NV | 62142 |  |  |  | Voltage Phase for Branch Channel 27 | Voltage Phase for Branch Channel 27 | AV191 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
28 | A | R/W | NV | 62143 |  |  |  | Voltage Phase for Branch Channel 28 | Voltage Phase for Branch Channel 28 | AV192 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
29 | A | R/W | NV | 62144 |  |  |  | Voltage Phase for Branch Channel 29 | Voltage Phase for Branch Channel 29 | AV193 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
30 | A | R/W | NV | 62145 |  |  |  | Voltage Phase for Branch Channel 30 | Voltage Phase for Branch Channel 30 | AV194 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
31 | A | R/W | NV | 62146 |  |  |  | Voltage Phase for Branch Channel 31 | Voltage Phase for Branch Channel 31 | AV195 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
32 | A | R/W | NV | 62147 |  |  |  | Voltage Phase for Branch Channel 32 | Voltage Phase for Branch Channel 32 | AV196 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
33 | A | R/W | NV | 62148 |  |  |  | Voltage Phase for Branch Channel 33 | Voltage Phase for Branch Channel 33 | AV197 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
34 | A | R/W | NV | 62149 |  |  |  | Voltage Phase for Branch Channel 34 | Voltage Phase for Branch Channel 34 | AV198 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
35 | A | R/W | NV | 62150 |  |  |  | Voltage Phase for Branch Channel 35 | Voltage Phase for Branch Channel 35 | AV199 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
36 | A | R/W | NV | 62151 |  |  |  | Voltage Phase for Branch Channel 36 | Voltage Phase for Branch Channel 36 | AV200 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
37 | A | R/W | NV | 62152 |  |  |  | Voltage Phase for Branch Channel 37 | Voltage Phase for Branch Channel 37 | AV201 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
38 | A | R/W | NV | 62153 |  |  |  | Voltage Phase for Branch Channel 38 | Voltage Phase for Branch Channel 38 | AV202 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
39 | A | R/W | NV | 62154 |  |  |  | Voltage Phase for Branch Channel 39 | Voltage Phase for Branch Channel 39 | AV203 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
40 | A | R/W | NV | 62155 |  |  |  | Voltage Phase for Branch Channel 40 | Voltage Phase for Branch Channel 40 | AV204 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
41 | A | R/W | NV | 62156 |  |  |  | Voltage Phase for Branch Channel 41 | Voltage Phase for Branch Channel 41 | AV205 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
42 | A | R/W | NV | 62157 |  |  |  | Voltage Phase for Branch Channel 42 | Voltage Phase for Branch Channel 42 | AV206 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
43 | A,B | R/W | NV | 62158 |  |  |  | Voltage Phase for Aux Channel 1 | Voltage Phase for Aux Channel 1 | AV207 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
44 | A,B | R/W | NV | 62159 |  |  |  | Voltage Phase for Aux Channel 2 | Voltage Phase for Aux Channel 2 | AV208 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
45 | A,B | R/W | NV | 62160 |  |  |  | Voltage Phase for Aux Channel 3 | Voltage Phase for Aux Channel 3 | AV209 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
46 | A,B | R/W | NV | 62161 |  |  |  | N/A No Power Calculations for Aux Channel 4 | [5 empty] | 0-2 | 0
total registers in this section
1040

## -=E30 1PH Circuits=-
42 SINGLE-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed, Bottom Feed, Single Row: Odd / Even configuration
[5 empty] | Top Feed | Bottom Feed
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
| 2 | 2 | 1 | A
| 3 | 3 | 1 | B
| 4 | 4 | 1 | B
| 5 | 5 | 1 | C
| 6 | 6 | 1 | C
| 7 | 7 | 1 | A
| 8 | 8 | 1 | A
| 9 | 9 | 1 | B
| 10 | 10 | 1 | B
| 11 | 11 | 1 | C
| 12 | 12 | 1 | C
| 13 | 13 | 1 | A
| 14 | 14 | 1 | A
| 15 | 15 | 1 | B | Odd/Even
| 16 | 16 | 1 | B
| 17 | 17 | 1 | C
| 18 | 18 | 1 | C
| 19 | 19 | 1 | A
| 20 | 20 | 1 | A
| 21 | 21 | 1 | B
| 22 | 22 | 1 | B
| 23 | 23 | 1 | C
| 24 | 24 | 1 | C
| 25 | 25 | 1 | A
| 26 | 26 | 1 | A
| 27 | 27 | 1 | B
| 28 | 28 | 1 | B
| 29 | 29 | 1 | C
| 30 | 30 | 1 | C
| 31 | 31 | 1 | A
| 32 | 32 | 1 | A
| 33 | 33 | 1 | B
| 34 | 34 | 1 | B
| 35 | 35 | 1 | C
| 36 | 36 | 1 | C
| 37 | 37 | 1 | A
| 38 | 38 | 1 | A
| 39 | 39 | 1 | B
| 40 | 40 | 1 | B
| 41 | 41 | 1 | C
| 42 | 42 | 1 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A | Sequential
| 2 | 2 | 1 | B
| 3 | 3 | 1 | C
| 4 | 4 | 1 | A
| 5 | 5 | 1 | B
| 6 | 6 | 1 | C
| 7 | 7 | 1 | A
| 8 | 8 | 1 | B
| 9 | 9 | 1 | C
| 10 | 10 | 1 | A
| 11 | 11 | 1 | B
| 12 | 12 | 1 | C
| 13 | 13 | 1 | A
| 14 | 14 | 1 | B
| 15 | 15 | 1 | C
| 16 | 16 | 1 | A
| 17 | 17 | 1 | B
| 18 | 18 | 1 | C
| 19 | 19 | 1 | A
| 20 | 20 | 1 | B
| 21 | 21 | 1 | C
| 22 | 22 | 1 | A
| 23 | 23 | 1 | B
| 24 | 24 | 1 | C
| 25 | 25 | 1 | A
| 26 | 26 | 1 | B
| 27 | 27 | 1 | C
| 28 | 28 | 1 | A
| 29 | 29 | 1 | B
| 30 | 30 | 1 | C
| 31 | 31 | 1 | A
| 32 | 32 | 1 | B
| 33 | 33 | 1 | C
| 34 | 34 | 1 | A
| 35 | 35 | 1 | B
| 36 | 36 | 1 | C
| 37 | 37 | 1 | A
| 38 | 38 | 1 | B
| 39 | 39 | 1 | C
| 40 | 40 | 1 | A
| 41 | 41 | 1 | B
| 42 | 42 | 1 | C

## -=E31 1PH Circuits=-
42 SINGLE-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
| 2 | 2 | 1 | A
| 3 | 3 | 1 | B
| 4 | 4 | 1 | B
| 5 | 5 | 1 | C
| 6 | 6 | 1 | C
| 7 | 7 | 1 | A
| 8 | 8 | 1 | A
| 9 | 9 | 1 | B
| 10 | 10 | 1 | B
| 11 | 11 | 1 | C
| 12 | 12 | 1 | C
| 13 | 13 | 1 | A
| 14 | 14 | 1 | A
| 15 | 15 | 1 | B
| 16 | 16 | 1 | B
| 17 | 17 | 1 | C
| 18 | 18 | 1 | C
| 19 | 19 | 1 | A
| 20 | 20 | 1 | A
| 21 | 21 | 1 | B
| 22 | 22 | 1 | B
| 23 | 23 | 1 | C
| 24 | 24 | 1 | C
| 25 | 25 | 1 | A
| 26 | 26 | 1 | A
| 27 | 27 | 1 | B
| 28 | 28 | 1 | B
| 29 | 29 | 1 | C
| 30 | 30 | 1 | C
| 31 | 31 | 1 | A
| 32 | 32 | 1 | A
| 33 | 33 | 1 | B
| 34 | 34 | 1 | B
| 35 | 35 | 1 | C
| 36 | 36 | 1 | C
| 37 | 37 | 1 | A
| 38 | 38 | 1 | A
| 39 | 39 | 1 | B
| 40 | 40 | 1 | B
| 41 | 41 | 1 | C
| 42 | 42 | 1 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
| 2 | 2 | 1 | B
| 3 | 3 | 1 | C
| 4 | 4 | 1 | A
| 5 | 5 | 1 | B
| 6 | 6 | 1 | C
| 7 | 7 | 1 | A
| 8 | 8 | 1 | B
| 9 | 9 | 1 | C
| 10 | 10 | 1 | A
| 11 | 11 | 1 | B
| 12 | 12 | 1 | C
| 13 | 13 | 1 | A
| 14 | 14 | 1 | B
| 15 | 15 | 1 | C
| 16 | 16 | 1 | A
| 17 | 17 | 1 | B
| 18 | 18 | 1 | C
| 19 | 19 | 1 | A
| 20 | 20 | 1 | B
| 21 | 21 | 1 | C
| 22 | 22 | 1 | A
| 23 | 23 | 1 | B
| 24 | 24 | 1 | C
| 25 | 25 | 1 | A
| 26 | 26 | 1 | B
| 27 | 27 | 1 | C
| 28 | 28 | 1 | A
| 29 | 29 | 1 | B
| 30 | 30 | 1 | C
| 31 | 31 | 1 | A
| 32 | 32 | 1 | B
| 33 | 33 | 1 | C
| 34 | 34 | 1 | A
| 35 | 35 | 1 | B
| 36 | 36 | 1 | C
| 37 | 37 | 1 | A
| 38 | 38 | 1 | B
| 39 | 39 | 1 | C
| 40 | 40 | 1 | A
| 41 | 41 | 1 | B
| 42 | 42 | 1 | C

## 1PH Point Map
[8 empty] | Modbus |  |  |  |  | BACnet
Channel | Model (A,B,C) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description | Object Name | Object ID | Units | COV Increment | BACnet Description
SCALE REGISTERS
1 | A,B,C | R | NV | 1000 |  |  |  | Current Scale
2 | A,B,C | R | NV | 1001 |  |  |  | Current Scale
3 | A,B,C | R | NV | 1002 |  |  |  | Current Scale
4 | A,B,C | R | NV | 1003 |  |  |  | Current Scale
5 | A,B,C | R | NV | 1004 |  |  |  | Current Scale
6 | A,B,C | R | NV | 1005 |  |  |  | Current Scale
7 | A,B,C | R | NV | 1006 |  |  |  | Current Scale
8 | A,B,C | R | NV | 1007 |  |  |  | Current Scale
9 | A,B,C | R | NV | 1008 |  |  |  | Current Scale
10 | A,B,C | R | NV | 1009 |  |  |  | Current Scale
11 | A,B,C | R | NV | 1010 |  |  |  | Current Scale
12 | A,B,C | R | NV | 1011 |  |  |  | Current Scale
13 | A,B,C | R | NV | 1012 |  |  |  | Current Scale
14 | A,B,C | R | NV | 1013 |  |  |  | Current Scale
15 | A,B,C | R | NV | 1014 |  |  |  | Current Scale
16 | A,B,C | R | NV | 1015 |  |  |  | Current Scale
17 | A,B,C | R | NV | 1016 |  |  |  | Current Scale
18 | A,B,C | R | NV | 1017 |  |  |  | Current Scale
19 | A,B,C | R | NV | 1018 |  |  |  | Current Scale
20 | A,B,C | R | NV | 1019 |  |  |  | Current Scale
21 | A,B,C | R | NV | 1020 |  |  |  | Current Scale
22 | A,B,C | R | NV | 1021 |  |  |  | Current Scale
23 | A,B,C | R | NV | 1022 |  |  |  | Current Scale
24 | A,B,C | R | NV | 1023 |  |  |  | Current Scale
25 | A,B,C | R | NV | 1024 |  |  |  | Current Scale
26 | A,B,C | R | NV | 1025 |  |  |  | Current Scale
27 | A,B,C | R | NV | 1026 |  |  |  | Current Scale
28 | A,B,C | R | NV | 1027 |  |  |  | Current Scale
29 | A,B,C | R | NV | 1028 |  |  |  | Current Scale
30 | A,B,C | R | NV | 1029 |  |  |  | Current Scale
31 | A,B,C | R | NV | 1030 |  |  |  | Current Scale
32 | A,B,C | R | NV | 1031 |  |  |  | Current Scale
33 | A,B,C | R | NV | 1032 |  |  |  | Current Scale
34 | A,B,C | R | NV | 1033 |  |  |  | Current Scale
35 | A,B,C | R | NV | 1034 |  |  |  | Current Scale
36 | A,B,C | R | NV | 1035 |  |  |  | Current Scale
37 | A,B,C | R | NV | 1036 |  |  |  | Current Scale
38 | A,B,C | R | NV | 1037 |  |  |  | Current Scale
39 | A,B,C | R | NV | 1038 |  |  |  | Current Scale
40 | A,B,C | R | NV | 1039 |  |  |  | Current Scale
41 | A,B,C | R | NV | 1040 |  |  |  | Current Scale
42 | A,B,C | R | NV | 1041 |  |  |  | Current Scale
1 | A | R | NV | 1042 |  |  |  | Power Scale
2 | A | R | NV | 1043 |  |  |  | Power Scale
3 | A | R | NV | 1044 |  |  |  | Power Scale
4 | A | R | NV | 1045 |  |  |  | Power Scale
5 | A | R | NV | 1046 |  |  |  | Power Scale
6 | A | R | NV | 1047 |  |  |  | Power Scale
7 | A | R | NV | 1048 |  |  |  | Power Scale
8 | A | R | NV | 1049 |  |  |  | Power Scale
9 | A | R | NV | 1050 |  |  |  | Power Scale
10 | A | R | NV | 1051 |  |  |  | Power Scale
11 | A | R | NV | 1052 |  |  |  | Power Scale
12 | A | R | NV | 1053 |  |  |  | Power Scale
13 | A | R | NV | 1054 |  |  |  | Power Scale
14 | A | R | NV | 1055 |  |  |  | Power Scale
15 | A | R | NV | 1056 |  |  |  | Power Scale
16 | A | R | NV | 1057 |  |  |  | Power Scale
17 | A | R | NV | 1058 |  |  |  | Power Scale
18 | A | R | NV | 1059 |  |  |  | Power Scale
19 | A | R | NV | 1060 |  |  |  | Power Scale
20 | A | R | NV | 1061 |  |  |  | Power Scale
21 | A | R | NV | 1062 |  |  |  | Power Scale
22 | A | R | NV | 1063 |  |  |  | Power Scale
23 | A | R | NV | 1064 |  |  |  | Power Scale
24 | A | R | NV | 1065 |  |  |  | Power Scale
25 | A | R | NV | 1066 |  |  |  | Power Scale
26 | A | R | NV | 1067 |  |  |  | Power Scale
27 | A | R | NV | 1068 |  |  |  | Power Scale
28 | A | R | NV | 1069 |  |  |  | Power Scale
29 | A | R | NV | 1070 |  |  |  | Power Scale
30 | A | R | NV | 1071 |  |  |  | Power Scale
31 | A | R | NV | 1072 |  |  |  | Power Scale
32 | A | R | NV | 1073 |  |  |  | Power Scale
33 | A | R | NV | 1074 |  |  |  | Power Scale
34 | A | R | NV | 1075 |  |  |  | Power Scale
35 | A | R | NV | 1076 |  |  |  | Power Scale
36 | A | R | NV | 1077 |  |  |  | Power Scale
37 | A | R | NV | 1078 |  |  |  | Power Scale
38 | A | R | NV | 1079 |  |  |  | Power Scale
39 | A | R | NV | 1080 |  |  |  | Power Scale
40 | A | R | NV | 1081 |  |  |  | Power Scale
41 | A | R | NV | 1082 |  |  |  | Power Scale
42 | A | R | NV | 1083 |  |  |  | Power Scale
1 | A | R | NV | 1084 |  |  |  | Energy Scale
2 | A | R | NV | 1085 |  |  |  | Energy Scale
3 | A | R | NV | 1086 |  |  |  | Energy Scale
4 | A | R | NV | 1087 |  |  |  | Energy Scale
5 | A | R | NV | 1088 |  |  |  | Energy Scale
6 | A | R | NV | 1089 |  |  |  | Energy Scale
7 | A | R | NV | 1090 |  |  |  | Energy Scale
8 | A | R | NV | 1091 |  |  |  | Energy Scale
9 | A | R | NV | 1092 |  |  |  | Energy Scale
10 | A | R | NV | 1093 |  |  |  | Energy Scale
11 | A | R | NV | 1094 |  |  |  | Energy Scale
12 | A | R | NV | 1095 |  |  |  | Energy Scale
13 | A | R | NV | 1096 |  |  |  | Energy Scale
14 | A | R | NV | 1097 |  |  |  | Energy Scale
15 | A | R | NV | 1098 |  |  |  | Energy Scale
16 | A | R | NV | 1099 |  |  |  | Energy Scale
17 | A | R | NV | 1100 |  |  |  | Energy Scale
18 | A | R | NV | 1101 |  |  |  | Energy Scale
19 | A | R | NV | 1102 |  |  |  | Energy Scale
20 | A | R | NV | 1103 |  |  |  | Energy Scale
21 | A | R | NV | 1104 |  |  |  | Energy Scale
22 | A | R | NV | 1105 |  |  |  | Energy Scale
23 | A | R | NV | 1106 |  |  |  | Energy Scale
24 | A | R | NV | 1107 |  |  |  | Energy Scale
25 | A | R | NV | 1108 |  |  |  | Energy Scale
26 | A | R | NV | 1109 |  |  |  | Energy Scale
27 | A | R | NV | 1110 |  |  |  | Energy Scale
28 | A | R | NV | 1111 |  |  |  | Energy Scale
29 | A | R | NV | 1112 |  |  |  | Energy Scale
30 | A | R | NV | 1113 |  |  |  | Energy Scale
31 | A | R | NV | 1114 |  |  |  | Energy Scale
32 | A | R | NV | 1115 |  |  |  | Energy Scale
33 | A | R | NV | 1116 |  |  |  | Energy Scale
34 | A | R | NV | 1117 |  |  |  | Energy Scale
35 | A | R | NV | 1118 |  |  |  | Energy Scale
36 | A | R | NV | 1119 |  |  |  | Energy Scale
37 | A | R | NV | 1120 |  |  |  | Energy Scale
38 | A | R | NV | 1121 |  |  |  | Energy Scale
39 | A | R | NV | 1122 |  |  |  | Energy Scale
40 | A | R | NV | 1123 |  |  |  | Energy Scale
41 | A | R | NV | 1124 |  |  |  | Energy Scale
42 | A | R | NV | 1125 |  |  |  | Energy Scale
RESETS
Also resets corresponding registers in 2PH and 3PH point maps
1 | A,B,C | W |  | 1126 |  |  |  | Reset - Write the listed value to perform the listed reset: | Channel 1 Reset | AO3 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
0 = No Action
10203 = Clear KWH value to zero
29877 = Clear all Max Current and Max KW values to zero
2 | A,B,C | W |  | 1127 |  |  |  | Reset | Channel 2 Reset | AO4 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
3 | A,B,C | W |  | 1128 |  |  |  | Reset | Channel 3 Reset | AO5 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
4 | A,B,C | W |  | 1129 |  |  |  | Reset | Channel 4 Reset | AO6 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
5 | A,B,C | W |  | 1130 |  |  |  | Reset | Channel 5 Reset | AO7 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
6 | A,B,C | W |  | 1131 |  |  |  | Reset | Channel 6 Reset | AO8 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
7 | A,B,C | W |  | 1132 |  |  |  | Reset | Channel 7 Reset | AO9 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
8 | A,B,C | W |  | 1133 |  |  |  | Reset | Channel 8 Reset | AO10 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
9 | A,B,C | W |  | 1134 |  |  |  | Reset | Channel 9 Reset | AO11 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
10 | A,B,C | W |  | 1135 |  |  |  | Reset | Channel 10 Reset | AO12 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
11 | A,B,C | W |  | 1136 |  |  |  | Reset | Channel 11 Reset | AO13 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
12 | A,B,C | W |  | 1137 |  |  |  | Reset | Channel 12 Reset | AO14 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
13 | A,B,C | W |  | 1138 |  |  |  | Reset | Channel 13 Reset | AO15 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
14 | A,B,C | W |  | 1139 |  |  |  | Reset | Channel 14 Reset | AO16 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
15 | A,B,C | W |  | 1140 |  |  |  | Reset | Channel 15 Reset | AO17 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
16 | A,B,C | W |  | 1141 |  |  |  | Reset | Channel 16 Reset | AO18 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
17 | A,B,C | W |  | 1142 |  |  |  | Reset | Channel 17 Reset | AO19 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
18 | A,B,C | W |  | 1143 |  |  |  | Reset | Channel 18 Reset | AO20 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
19 | A,B,C | W |  | 1144 |  |  |  | Reset | Channel 19 Reset | AO21 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
20 | A,B,C | W |  | 1145 |  |  |  | Reset | Channel 20 Reset | AO22 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
21 | A,B,C | W |  | 1146 |  |  |  | Reset | Channel 21 Reset | AO23 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
22 | A,B,C | W |  | 1147 |  |  |  | Reset | Channel 22 Reset | AO24 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
23 | A,B,C | W |  | 1148 |  |  |  | Reset | Channel 23 Reset | AO25 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
24 | A,B,C | W |  | 1149 |  |  |  | Reset | Channel 24 Reset | AO26 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
25 | A,B,C | W |  | 1150 |  |  |  | Reset | Channel 25 Reset | AO27 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
26 | A,B,C | W |  | 1151 |  |  |  | Reset | Channel 26 Reset | AO28 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
27 | A,B,C | W |  | 1152 |  |  |  | Reset | Channel 27 Reset | AO29 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
28 | A,B,C | W |  | 1153 |  |  |  | Reset | Channel 28 Reset | AO30 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
29 | A,B,C | W |  | 1154 |  |  |  | Reset | Channel 29 Reset | AO31 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
30 | A,B,C | W |  | 1155 |  |  |  | Reset | Channel 30 Reset | AO32 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
31 | A,B,C | W |  | 1156 |  |  |  | Reset | Channel 31 Reset | AO33 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
32 | A,B,C | W |  | 1157 |  |  |  | Reset | Channel 32 Reset | AO34 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
33 | A,B,C | W |  | 1158 |  |  |  | Reset | Channel 33 Reset | AO35 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
34 | A,B,C | W |  | 1159 |  |  |  | Reset | Channel 34 Reset | AO36 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
35 | A,B,C | W |  | 1160 |  |  |  | Reset | Channel 35 Reset | AO37 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
36 | A,B,C | W |  | 1161 |  |  |  | Reset | Channel 36 Reset | AO38 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
37 | A,B,C | W |  | 1162 |  |  |  | Reset | Channel 37 Reset | AO39 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
38 | A,B,C | W |  | 1163 |  |  |  | Reset | Channel 38 Reset | AO40 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
39 | A,B,C | W |  | 1164 |  |  |  | Reset | Channel 39 Reset | AO41 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
40 | A,B,C | W |  | 1165 |  |  |  | Reset | Channel 40 Reset | AO42 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
41 | A,B,C | W |  | 1166 |  |  |  | Reset | Channel 41 Reset | AO43 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
42 | A,B,C | W |  | 1167 |  |  |  | Reset | Channel 42 Reset | AO44 | No-Units | 1 | 10203=kWh; 29877=Max Current & Max kW
DATA
1 | A | R | NV | 1168 | 2000 | 2001 | 1084 | KWH (MSW) | kWh: Channel 1 | AI68 | kWh | 0 | Real Energy - Channel 1
1 | A | R | NV | 1169 |  |  |  | KWH (LSW)
2 | A | R | NV | 1170 | 2002 | 2003 | 1085 | KWH (MSW) | kWh: Channel 2 | AI69 | kWh | 0 | Real Energy - Channel 2
2 | A | R | NV | 1171 |  |  |  | KWH (LSW)
3 | A | R | NV | 1172 | 2004 | 2005 | 1086 | KWH (MSW) | kWh: Channel 3 | AI70 | kWh | 0 | Real Energy - Channel 3
3 | A | R | NV | 1173 |  |  |  | KWH (LSW)
4 | A | R | NV | 1174 | 2006 | 2007 | 1087 | KWH (MSW) | kWh: Channel 4 | AI71 | kWh | 0 | Real Energy - Channel 4
4 | A | R | NV | 1175 |  |  |  | KWH (LSW)
5 | A | R | NV | 1176 | 2008 | 2009 | 1088 | KWH (MSW) | kWh: Channel 5 | AI72 | kWh | 0 | Real Energy - Channel 5
5 | A | R | NV | 1177 |  |  |  | KWH (LSW)
6 | A | R | NV | 1178 | 2010 | 2011 | 1089 | KWH (MSW) | kWh: Channel 6 | AI73 | kWh | 0 | Real Energy - Channel 6
6 | A | R | NV | 1179 |  |  |  | KWH (LSW)
7 | A | R | NV | 1180 | 2012 | 2013 | 1090 | KWH (MSW) | kWh: Channel 7 | AI74 | kWh | 0 | Real Energy - Channel 7
7 | A | R | NV | 1181 |  |  |  | KWH (LSW)
8 | A | R | NV | 1182 | 2014 | 2015 | 1091 | KWH (MSW) | kWh: Channel 8 | AI75 | kWh | 0 | Real Energy - Channel 8
8 | A | R | NV | 1183 |  |  |  | KWH (LSW)
9 | A | R | NV | 1184 | 2016 | 2017 | 1092 | KWH (MSW) | kWh: Channel 9 | AI76 | kWh | 0 | Real Energy - Channel 9
9 | A | R | NV | 1185 |  |  |  | KWH (LSW)
10 | A | R | NV | 1186 | 2018 | 2019 | 1093 | KWH (MSW) | kWh: Channel 10 | AI77 | kWh | 0 | Real Energy - Channel 10
10 | A | R | NV | 1187 |  |  |  | KWH (LSW)
11 | A | R | NV | 1188 | 2020 | 2021 | 1094 | KWH (MSW) | kWh: Channel 11 | AI78 | kWh | 0 | Real Energy - Channel 11
11 | A | R | NV | 1189 |  |  |  | KWH (LSW)
12 | A | R | NV | 1190 | 2022 | 2023 | 1095 | KWH (MSW) | kWh: Channel 12 | AI79 | kWh | 0 | Real Energy - Channel 12
12 | A | R | NV | 1191 |  |  |  | KWH (LSW)
13 | A | R | NV | 1192 | 2024 | 2025 | 1096 | KWH (MSW) | kWh: Channel 13 | AI80 | kWh | 0 | Real Energy - Channel 13
13 | A | R | NV | 1193 |  |  |  | KWH (LSW)
14 | A | R | NV | 1194 | 2026 | 2027 | 1097 | KWH (MSW) | kWh: Channel 14 | AI81 | kWh | 0 | Real Energy - Channel 14
14 | A | R | NV | 1195 |  |  |  | KWH (LSW)
15 | A | R | NV | 1196 | 2028 | 2029 | 1098 | KWH (MSW) | kWh: Channel 15 | AI82 | kWh | 0 | Real Energy - Channel 15
15 | A | R | NV | 1197 |  |  |  | KWH (LSW)
16 | A | R | NV | 1198 | 2030 | 2031 | 1099 | KWH (MSW) | kWh: Channel 16 | AI83 | kWh | 0 | Real Energy - Channel 16
16 | A | R | NV | 1199 |  |  |  | KWH (LSW)
17 | A | R | NV | 1200 | 2032 | 2033 | 1100 | KWH (MSW) | kWh: Channel 17 | AI84 | kWh | 0 | Real Energy - Channel 17
17 | A | R | NV | 1201 |  |  |  | KWH (LSW)
18 | A | R | NV | 1202 | 2034 | 2035 | 1101 | KWH (MSW) | kWh: Channel 18 | AI85 | kWh | 0 | Real Energy - Channel 18
18 | A | R | NV | 1203 |  |  |  | KWH (LSW)
19 | A | R | NV | 1204 | 2036 | 2037 | 1102 | KWH (MSW) | kWh: Channel 19 | AI86 | kWh | 0 | Real Energy - Channel 19
19 | A | R | NV | 1205 |  |  |  | KWH (LSW)
20 | A | R | NV | 1206 | 2038 | 2039 | 1103 | KWH (MSW) | kWh: Channel 20 | AI87 | kWh | 0 | Real Energy - Channel 20
20 | A | R | NV | 1207 |  |  |  | KWH (LSW)
21 | A | R | NV | 1208 | 2040 | 2041 | 1104 | KWH (MSW) | kWh: Channel 21 | AI88 | kWh | 0 | Real Energy - Channel 21
21 | A | R | NV | 1209 |  |  |  | KWH (LSW)
22 | A | R | NV | 1210 | 2042 | 2043 | 1105 | KWH (MSW) | kWh: Channel 22 | AI89 | kWh | 0 | Real Energy - Channel 22
22 | A | R | NV | 1211 |  |  |  | KWH (LSW)
23 | A | R | NV | 1212 | 2044 | 2045 | 1106 | KWH (MSW) | kWh: Channel 23 | AI90 | kWh | 0 | Real Energy - Channel 23
23 | A | R | NV | 1213 |  |  |  | KWH (LSW)
24 | A | R | NV | 1214 | 2046 | 2047 | 1107 | KWH (MSW) | kWh: Channel 24 | AI91 | kWh | 0 | Real Energy - Channel 24
24 | A | R | NV | 1215 |  |  |  | KWH (LSW)
25 | A | R | NV | 1216 | 2048 | 2049 | 1108 | KWH (MSW) | kWh: Channel 25 | AI92 | kWh | 0 | Real Energy - Channel 25
25 | A | R | NV | 1217 |  |  |  | KWH (LSW)
26 | A | R | NV | 1218 | 2050 | 2051 | 1109 | KWH (MSW) | kWh: Channel 26 | AI93 | kWh | 0 | Real Energy - Channel 26
26 | A | R | NV | 1219 |  |  |  | KWH (LSW)
27 | A | R | NV | 1220 | 2052 | 2053 | 1110 | KWH (MSW) | kWh: Channel 27 | AI94 | kWh | 0 | Real Energy - Channel 27
27 | A | R | NV | 1221 |  |  |  | KWH (LSW)
28 | A | R | NV | 1222 | 2054 | 2055 | 1111 | KWH (MSW) | kWh: Channel 28 | AI95 | kWh | 0 | Real Energy - Channel 28
28 | A | R | NV | 1223 |  |  |  | KWH (LSW)
29 | A | R | NV | 1224 | 2056 | 2057 | 1112 | KWH (MSW) | kWh: Channel 29 | AI96 | kWh | 0 | Real Energy - Channel 29
29 | A | R | NV | 1225 |  |  |  | KWH (LSW)
30 | A | R | NV | 1226 | 2058 | 2059 | 1113 | KWH (MSW) | kWh: Channel 30 | AI97 | kWh | 0 | Real Energy - Channel 30
30 | A | R | NV | 1227 |  |  |  | KWH (LSW)
31 | A | R | NV | 1228 | 2060 | 2061 | 1114 | KWH (MSW) | kWh: Channel 31 | AI98 | kWh | 0 | Real Energy - Channel 31
31 | A | R | NV | 1229 |  |  |  | KWH (LSW)
32 | A | R | NV | 1230 | 2062 | 2063 | 1115 | KWH (MSW) | kWh: Channel 32 | AI99 | kWh | 0 | Real Energy - Channel 32
32 | A | R | NV | 1231 |  |  |  | KWH (LSW)
33 | A | R | NV | 1232 | 2064 | 2065 | 1116 | KWH (MSW) | kWh: Channel 33 | AI100 | kWh | 0 | Real Energy - Channel 33
33 | A | R | NV | 1233 |  |  |  | KWH (LSW)
34 | A | R | NV | 1234 | 2066 | 2067 | 1117 | KWH (MSW) | kWh: Channel 34 | AI101 | kWh | 0 | Real Energy - Channel 34
34 | A | R | NV | 1235 |  |  |  | KWH (LSW)
35 | A | R | NV | 1236 | 2068 | 2069 | 1118 | KWH (MSW) | kWh: Channel 35 | AI102 | kWh | 0 | Real Energy - Channel 35
35 | A | R | NV | 1237 |  |  |  | KWH (LSW)
36 | A | R | NV | 1238 | 2070 | 2071 | 1119 | KWH (MSW) | kWh: Channel 36 | AI103 | kWh | 0 | Real Energy - Channel 36
36 | A | R | NV | 1239 |  |  |  | KWH (LSW)
37 | A | R | NV | 1240 | 2072 | 2073 | 1120 | KWH (MSW) | kWh: Channel 37 | AI104 | kWh | 0 | Real Energy - Channel 37
37 | A | R | NV | 1241 |  |  |  | KWH (LSW)
38 | A | R | NV | 1242 | 2074 | 2075 | 1121 | KWH (MSW) | kWh: Channel 38 | AI105 | kWh | 0 | Real Energy - Channel 38
38 | A | R | NV | 1243 |  |  |  | KWH (LSW)
39 | A | R | NV | 1244 | 2076 | 2077 | 1122 | KWH (MSW) | kWh: Channel 39 | AI106 | kWh | 0 | Real Energy - Channel 39
39 | A | R | NV | 1245 |  |  |  | KWH (LSW)
40 | A | R | NV | 1246 | 2078 | 2079 | 1123 | KWH (MSW) | kWh: Channel 40 | AI107 | kWh | 0 | Real Energy - Channel 40
40 | A | R | NV | 1247 |  |  |  | KWH (LSW)
41 | A | R | NV | 1248 | 2080 | 2081 | 1124 | KWH (MSW) | kWh: Channel 41 | AI108 | kWh | 0 | Real Energy - Channel 41
41 | A | R | NV | 1249 |  |  |  | KWH (LSW)
42 | A | R | NV | 1250 | 2082 | 2083 | 1125 | KWH (MSW) | kWh: Channel 42 | AI109 | kWh | 0 | Real Energy - Channel 42
42 | A | R | NV | 1251 |  |  |  | KWH (LSW)
1 | A | R |  | 1252 | 2084 | 2085 | 1042 | KW | kW: Channel 1 | AI110 | kW | 1 | Instantaneous Real Power - Channel 1
2 | A | R |  | 1253 | 2086 | 2087 | 1043 | KW | kW: Channel 2 | AI111 | kW | 1 | Instantaneous Real Power - Channel 2
3 | A | R |  | 1254 | 2088 | 2089 | 1044 | KW | kW: Channel 3 | AI112 | kW | 1 | Instantaneous Real Power - Channel 3
4 | A | R |  | 1255 | 2090 | 2091 | 1045 | KW | kW: Channel 4 | AI113 | kW | 1 | Instantaneous Real Power - Channel 4
5 | A | R |  | 1256 | 2092 | 2093 | 1046 | KW | kW: Channel 5 | AI114 | kW | 1 | Instantaneous Real Power - Channel 5
6 | A | R |  | 1257 | 2094 | 2095 | 1047 | KW | kW: Channel 6 | AI115 | kW | 1 | Instantaneous Real Power - Channel 6
7 | A | R |  | 1258 | 2096 | 2097 | 1048 | KW | kW: Channel 7 | AI116 | kW | 1 | Instantaneous Real Power - Channel 7
8 | A | R |  | 1259 | 2098 | 2099 | 1049 | KW | kW: Channel 8 | AI117 | kW | 1 | Instantaneous Real Power - Channel 8
9 | A | R |  | 1260 | 2100 | 2101 | 1050 | KW | kW: Channel 9 | AI118 | kW | 1 | Instantaneous Real Power - Channel 9
10 | A | R |  | 1261 | 2102 | 2103 | 1051 | KW | kW: Channel 10 | AI119 | kW | 1 | Instantaneous Real Power - Channel 10
11 | A | R |  | 1262 | 2104 | 2105 | 1052 | KW | kW: Channel 11 | AI120 | kW | 1 | Instantaneous Real Power - Channel 11
12 | A | R |  | 1263 | 2106 | 2107 | 1053 | KW | kW: Channel 12 | AI121 | kW | 1 | Instantaneous Real Power - Channel 12
13 | A | R |  | 1264 | 2108 | 2109 | 1054 | KW | kW: Channel 13 | AI122 | kW | 1 | Instantaneous Real Power - Channel 13
14 | A | R |  | 1265 | 2110 | 2111 | 1055 | KW | kW: Channel 14 | AI123 | kW | 1 | Instantaneous Real Power - Channel 14
15 | A | R |  | 1266 | 2112 | 2113 | 1056 | KW | kW: Channel 15 | AI124 | kW | 1 | Instantaneous Real Power - Channel 15
16 | A | R |  | 1267 | 2114 | 2115 | 1057 | KW | kW: Channel 16 | AI125 | kW | 1 | Instantaneous Real Power - Channel 16
17 | A | R |  | 1268 | 2116 | 2117 | 1058 | KW | kW: Channel 17 | AI126 | kW | 1 | Instantaneous Real Power - Channel 17
18 | A | R |  | 1269 | 2118 | 2119 | 1059 | KW | kW: Channel 18 | AI127 | kW | 1 | Instantaneous Real Power - Channel 18
19 | A | R |  | 1270 | 2120 | 2121 | 1060 | KW | kW: Channel 19 | AI128 | kW | 1 | Instantaneous Real Power - Channel 19
20 | A | R |  | 1271 | 2122 | 2123 | 1061 | KW | kW: Channel 20 | AI129 | kW | 1 | Instantaneous Real Power - Channel 20
21 | A | R |  | 1272 | 2124 | 2125 | 1062 | KW | kW: Channel 21 | AI130 | kW | 1 | Instantaneous Real Power - Channel 21
22 | A | R |  | 1273 | 2126 | 2127 | 1063 | KW | kW: Channel 22 | AI131 | kW | 1 | Instantaneous Real Power - Channel 22
23 | A | R |  | 1274 | 2128 | 2129 | 1064 | KW | kW: Channel 23 | AI132 | kW | 1 | Instantaneous Real Power - Channel 23
24 | A | R |  | 1275 | 2130 | 2131 | 1065 | KW | kW: Channel 24 | AI133 | kW | 1 | Instantaneous Real Power - Channel 24
25 | A | R |  | 1276 | 2132 | 2133 | 1066 | KW | kW: Channel 25 | AI134 | kW | 1 | Instantaneous Real Power - Channel 25
26 | A | R |  | 1277 | 2134 | 2135 | 1067 | KW | kW: Channel 26 | AI135 | kW | 1 | Instantaneous Real Power - Channel 26
27 | A | R |  | 1278 | 2136 | 2137 | 1068 | KW | kW: Channel 27 | AI136 | kW | 1 | Instantaneous Real Power - Channel 27
28 | A | R |  | 1279 | 2138 | 2139 | 1069 | KW | kW: Channel 28 | AI137 | kW | 1 | Instantaneous Real Power - Channel 28
29 | A | R |  | 1280 | 2140 | 2141 | 1070 | KW | kW: Channel 29 | AI138 | kW | 1 | Instantaneous Real Power - Channel 29
30 | A | R |  | 1281 | 2142 | 2143 | 1071 | KW | kW: Channel 30 | AI139 | kW | 1 | Instantaneous Real Power - Channel 30
31 | A | R |  | 1282 | 2144 | 2145 | 1072 | KW | kW: Channel 31 | AI140 | kW | 1 | Instantaneous Real Power - Channel 31
32 | A | R |  | 1283 | 2146 | 2147 | 1073 | KW | kW: Channel 32 | AI141 | kW | 1 | Instantaneous Real Power - Channel 32
33 | A | R |  | 1284 | 2148 | 2149 | 1074 | KW | kW: Channel 33 | AI142 | kW | 1 | Instantaneous Real Power - Channel 33
34 | A | R |  | 1285 | 2150 | 2151 | 1075 | KW | kW: Channel 34 | AI143 | kW | 1 | Instantaneous Real Power - Channel 34
35 | A | R |  | 1286 | 2152 | 2153 | 1076 | KW | kW: Channel 35 | AI144 | kW | 1 | Instantaneous Real Power - Channel 35
36 | A | R |  | 1287 | 2154 | 2155 | 1077 | KW | kW: Channel 36 | AI145 | kW | 1 | Instantaneous Real Power - Channel 36
37 | A | R |  | 1288 | 2156 | 2157 | 1078 | KW | kW: Channel 37 | AI146 | kW | 1 | Instantaneous Real Power - Channel 37
38 | A | R |  | 1289 | 2158 | 2159 | 1079 | KW | kW: Channel 38 | AI147 | kW | 1 | Instantaneous Real Power - Channel 38
39 | A | R |  | 1290 | 2160 | 2161 | 1080 | KW | kW: Channel 39 | AI148 | kW | 1 | Instantaneous Real Power - Channel 39
40 | A | R |  | 1291 | 2162 | 2163 | 1081 | KW | kW: Channel 40 | AI149 | kW | 1 | Instantaneous Real Power - Channel 40
41 | A | R |  | 1292 | 2164 | 2165 | 1082 | KW | kW: Channel 41 | AI150 | kW | 1 | Instantaneous Real Power - Channel 41
42 | A | R |  | 1293 | 2166 | 2167 | 1083 | KW | kW: Channel 42 | AI151 | kW | 1 | Instantaneous Real Power - Channel 42
1 | A | R |  | 1294 | 2168 | 2169 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 1 | AI152 | PF | 0.01 | Instantaneous Power Factor - Channel 1
2 | A | R |  | 1295 | 2170 | 2171 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 2 | AI153 | PF | 0.01 | Instantaneous Power Factor - Channel 2
3 | A | R |  | 1296 | 2172 | 2173 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 3 | AI154 | PF | 0.01 | Instantaneous Power Factor - Channel 3
4 | A | R |  | 1297 | 2174 | 2175 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 4 | AI155 | PF | 0.01 | Instantaneous Power Factor - Channel 4
5 | A | R |  | 1298 | 2176 | 2177 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 5 | AI156 | PF | 0.01 | Instantaneous Power Factor - Channel 5
6 | A | R |  | 1299 | 2178 | 2179 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 6 | AI157 | PF | 0.01 | Instantaneous Power Factor - Channel 6
7 | A | R |  | 1300 | 2180 | 2181 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 7 | AI158 | PF | 0.01 | Instantaneous Power Factor - Channel 7
8 | A | R |  | 1301 | 2182 | 2183 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 8 | AI159 | PF | 0.01 | Instantaneous Power Factor - Channel 8
9 | A | R |  | 1302 | 2184 | 2185 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 9 | AI160 | PF | 0.01 | Instantaneous Power Factor - Channel 9
10 | A | R |  | 1303 | 2186 | 2187 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 10 | AI161 | PF | 0.01 | Instantaneous Power Factor - Channel 10
11 | A | R |  | 1304 | 2188 | 2189 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 11 | AI162 | PF | 0.01 | Instantaneous Power Factor - Channel 11
12 | A | R |  | 1305 | 2190 | 2191 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 12 | AI163 | PF | 0.01 | Instantaneous Power Factor - Channel 12
13 | A | R |  | 1306 | 2192 | 2193 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 13 | AI164 | PF | 0.01 | Instantaneous Power Factor - Channel 13
14 | A | R |  | 1307 | 2194 | 2195 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 14 | AI165 | PF | 0.01 | Instantaneous Power Factor - Channel 14
15 | A | R |  | 1308 | 2196 | 2197 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 15 | AI166 | PF | 0.01 | Instantaneous Power Factor - Channel 15
16 | A | R |  | 1309 | 2198 | 2199 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 16 | AI167 | PF | 0.01 | Instantaneous Power Factor - Channel 16
17 | A | R |  | 1310 | 2200 | 2201 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 17 | AI168 | PF | 0.01 | Instantaneous Power Factor - Channel 17
18 | A | R |  | 1311 | 2202 | 2203 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 18 | AI169 | PF | 0.01 | Instantaneous Power Factor - Channel 18
19 | A | R |  | 1312 | 2204 | 2205 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 19 | AI170 | PF | 0.01 | Instantaneous Power Factor - Channel 19
20 | A | R |  | 1313 | 2206 | 2207 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 20 | AI171 | PF | 0.01 | Instantaneous Power Factor - Channel 20
21 | A | R |  | 1314 | 2208 | 2209 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 21 | AI172 | PF | 0.01 | Instantaneous Power Factor - Channel 21
22 | A | R |  | 1315 | 2210 | 2211 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 22 | AI173 | PF | 0.01 | Instantaneous Power Factor - Channel 22
23 | A | R |  | 1316 | 2212 | 2213 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 23 | AI174 | PF | 0.01 | Instantaneous Power Factor - Channel 23
24 | A | R |  | 1317 | 2214 | 2215 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 24 | AI175 | PF | 0.01 | Instantaneous Power Factor - Channel 24
25 | A | R |  | 1318 | 2216 | 2217 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 25 | AI176 | PF | 0.01 | Instantaneous Power Factor - Channel 25
26 | A | R |  | 1319 | 2218 | 2219 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 26 | AI177 | PF | 0.01 | Instantaneous Power Factor - Channel 26
27 | A | R |  | 1320 | 2220 | 2221 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 27 | AI178 | PF | 0.01 | Instantaneous Power Factor - Channel 27
28 | A | R |  | 1321 | 2222 | 2223 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 28 | AI179 | PF | 0.01 | Instantaneous Power Factor - Channel 28
29 | A | R |  | 1322 | 2224 | 2225 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 29 | AI180 | PF | 0.01 | Instantaneous Power Factor - Channel 29
30 | A | R |  | 1323 | 2226 | 2227 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 30 | AI181 | PF | 0.01 | Instantaneous Power Factor - Channel 30
31 | A | R |  | 1324 | 2228 | 2229 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 31 | AI182 | PF | 0.01 | Instantaneous Power Factor - Channel 31
32 | A | R |  | 1325 | 2230 | 2231 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 32 | AI183 | PF | 0.01 | Instantaneous Power Factor - Channel 32
33 | A | R |  | 1326 | 2232 | 2233 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 33 | AI184 | PF | 0.01 | Instantaneous Power Factor - Channel 33
34 | A | R |  | 1327 | 2234 | 2235 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 34 | AI185 | PF | 0.01 | Instantaneous Power Factor - Channel 34
35 | A | R |  | 1328 | 2236 | 2237 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 35 | AI186 | PF | 0.01 | Instantaneous Power Factor - Channel 35
36 | A | R |  | 1329 | 2238 | 2239 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 36 | AI187 | PF | 0.01 | Instantaneous Power Factor - Channel 36
37 | A | R |  | 1330 | 2240 | 2241 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 37 | AI188 | PF | 0.01 | Instantaneous Power Factor - Channel 37
38 | A | R |  | 1331 | 2242 | 2243 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 38 | AI189 | PF | 0.01 | Instantaneous Power Factor - Channel 38
39 | A | R |  | 1332 | 2244 | 2245 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 39 | AI190 | PF | 0.01 | Instantaneous Power Factor - Channel 39
40 | A | R |  | 1333 | 2246 | 2247 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 40 | AI191 | PF | 0.01 | Instantaneous Power Factor - Channel 40
41 | A | R |  | 1334 | 2248 | 2249 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 41 | AI192 | PF | 0.01 | Instantaneous Power Factor - Channel 41
42 | A | R |  | 1335 | 2250 | 2251 | -3 | PF (+ for leading, - for lagging) | Power Factor: Channel 42 | AI193 | PF | 0.01 | Instantaneous Power Factor - Channel 42
1 | A,B,C | R |  | 1336 | 2252 | 2253 | 1000 | Current | Amps: Channel 1 | AI194 | Amperes | 5 | Instantaneous Current - Channel 1
2 | A,B,C | R |  | 1337 | 2254 | 2255 | 1001 | Current | Amps: Channel 2 | AI195 | Amperes | 5 | Instantaneous Current - Channel 2
3 | A,B,C | R |  | 1338 | 2256 | 2257 | 1002 | Current | Amps: Channel 3 | AI196 | Amperes | 5 | Instantaneous Current - Channel 3
4 | A,B,C | R |  | 1339 | 2258 | 2259 | 1003 | Current | Amps: Channel 4 | AI197 | Amperes | 5 | Instantaneous Current - Channel 4
5 | A,B,C | R |  | 1340 | 2260 | 2261 | 1004 | Current | Amps: Channel 5 | AI198 | Amperes | 5 | Instantaneous Current - Channel 5
6 | A,B,C | R |  | 1341 | 2262 | 2263 | 1005 | Current | Amps: Channel 6 | AI199 | Amperes | 5 | Instantaneous Current - Channel 6
7 | A,B,C | R |  | 1342 | 2264 | 2265 | 1006 | Current | Amps: Channel 7 | AI200 | Amperes | 5 | Instantaneous Current - Channel 7
8 | A,B,C | R |  | 1343 | 2266 | 2267 | 1007 | Current | Amps: Channel 8 | AI201 | Amperes | 5 | Instantaneous Current - Channel 8
9 | A,B,C | R |  | 1344 | 2268 | 2269 | 1008 | Current | Amps: Channel 9 | AI202 | Amperes | 5 | Instantaneous Current - Channel 9
10 | A,B,C | R |  | 1345 | 2270 | 2271 | 1009 | Current | Amps: Channel 10 | AI203 | Amperes | 5 | Instantaneous Current - Channel 10
11 | A,B,C | R |  | 1346 | 2272 | 2273 | 1010 | Current | Amps: Channel 11 | AI204 | Amperes | 5 | Instantaneous Current - Channel 11
12 | A,B,C | R |  | 1347 | 2274 | 2275 | 1011 | Current | Amps: Channel 12 | AI205 | Amperes | 5 | Instantaneous Current - Channel 12
13 | A,B,C | R |  | 1348 | 2276 | 2277 | 1012 | Current | Amps: Channel 13 | AI206 | Amperes | 5 | Instantaneous Current - Channel 13
14 | A,B,C | R |  | 1349 | 2278 | 2279 | 1013 | Current | Amps: Channel 14 | AI207 | Amperes | 5 | Instantaneous Current - Channel 14
15 | A,B,C | R |  | 1350 | 2280 | 2281 | 1014 | Current | Amps: Channel 15 | AI208 | Amperes | 5 | Instantaneous Current - Channel 15
16 | A,B,C | R |  | 1351 | 2282 | 2283 | 1015 | Current | Amps: Channel 16 | AI209 | Amperes | 5 | Instantaneous Current - Channel 16
17 | A,B,C | R |  | 1352 | 2284 | 2285 | 1016 | Current | Amps: Channel 17 | AI210 | Amperes | 5 | Instantaneous Current - Channel 17
18 | A,B,C | R |  | 1353 | 2286 | 2287 | 1017 | Current | Amps: Channel 18 | AI211 | Amperes | 5 | Instantaneous Current - Channel 18
19 | A,B,C | R |  | 1354 | 2288 | 2289 | 1018 | Current | Amps: Channel 19 | AI212 | Amperes | 5 | Instantaneous Current - Channel 19
20 | A,B,C | R |  | 1355 | 2290 | 2291 | 1019 | Current | Amps: Channel 20 | AI213 | Amperes | 5 | Instantaneous Current - Channel 20
21 | A,B,C | R |  | 1356 | 2292 | 2293 | 1020 | Current | Amps: Channel 21 | AI214 | Amperes | 5 | Instantaneous Current - Channel 21
22 | A,B,C | R |  | 1357 | 2294 | 2295 | 1021 | Current | Amps: Channel 22 | AI215 | Amperes | 5 | Instantaneous Current - Channel 22
23 | A,B,C | R |  | 1358 | 2296 | 2297 | 1022 | Current | Amps: Channel 23 | AI216 | Amperes | 5 | Instantaneous Current - Channel 23
24 | A,B,C | R |  | 1359 | 2298 | 2299 | 1023 | Current | Amps: Channel 24 | AI217 | Amperes | 5 | Instantaneous Current - Channel 24
25 | A,B,C | R |  | 1360 | 2300 | 2301 | 1024 | Current | Amps: Channel 25 | AI218 | Amperes | 5 | Instantaneous Current - Channel 25
26 | A,B,C | R |  | 1361 | 2302 | 2303 | 1025 | Current | Amps: Channel 26 | AI219 | Amperes | 5 | Instantaneous Current - Channel 26
27 | A,B,C | R |  | 1362 | 2304 | 2305 | 1026 | Current | Amps: Channel 27 | AI220 | Amperes | 5 | Instantaneous Current - Channel 27
28 | A,B,C | R |  | 1363 | 2306 | 2307 | 1027 | Current | Amps: Channel 28 | AI221 | Amperes | 5 | Instantaneous Current - Channel 28
29 | A,B,C | R |  | 1364 | 2308 | 2309 | 1028 | Current | Amps: Channel 29 | AI222 | Amperes | 5 | Instantaneous Current - Channel 29
30 | A,B,C | R |  | 1365 | 2310 | 2311 | 1029 | Current | Amps: Channel 30 | AI223 | Amperes | 5 | Instantaneous Current - Channel 30
31 | A,B,C | R |  | 1366 | 2312 | 2313 | 1030 | Current | Amps: Channel 31 | AI224 | Amperes | 5 | Instantaneous Current - Channel 31
32 | A,B,C | R |  | 1367 | 2314 | 2315 | 1031 | Current | Amps: Channel 32 | AI225 | Amperes | 5 | Instantaneous Current - Channel 32
33 | A,B,C | R |  | 1368 | 2316 | 2317 | 1032 | Current | Amps: Channel 33 | AI226 | Amperes | 5 | Instantaneous Current - Channel 33
34 | A,B,C | R |  | 1369 | 2318 | 2319 | 1033 | Current | Amps: Channel 34 | AI227 | Amperes | 5 | Instantaneous Current - Channel 34
35 | A,B,C | R |  | 1370 | 2320 | 2321 | 1034 | Current | Amps: Channel 35 | AI228 | Amperes | 5 | Instantaneous Current - Channel 35
36 | A,B,C | R |  | 1371 | 2322 | 2323 | 1035 | Current | Amps: Channel 36 | AI229 | Amperes | 5 | Instantaneous Current - Channel 36
37 | A,B,C | R |  | 1372 | 2324 | 2325 | 1036 | Current | Amps: Channel 37 | AI230 | Amperes | 5 | Instantaneous Current - Channel 37
38 | A,B,C | R |  | 1373 | 2326 | 2327 | 1037 | Current | Amps: Channel 38 | AI231 | Amperes | 5 | Instantaneous Current - Channel 38
39 | A,B,C | R |  | 1374 | 2328 | 2329 | 1038 | Current | Amps: Channel 39 | AI232 | Amperes | 5 | Instantaneous Current - Channel 39
40 | A,B,C | R |  | 1375 | 2330 | 2331 | 1039 | Current | Amps: Channel 40 | AI233 | Amperes | 5 | Instantaneous Current - Channel 40
41 | A,B,C | R |  | 1376 | 2332 | 2333 | 1040 | Current | Amps: Channel 41 | AI234 | Amperes | 5 | Instantaneous Current - Channel 41
42 | A,B,C | R |  | 1377 | 2334 | 2335 | 1041 | Current | Amps: Channel 42 | AI235 | Amperes | 5 | Instantaneous Current - Channel 42
1 | A | R |  | 1378 | 2336 | 2337 | 1042 | Present KW Demand | kW Present Demand: Channel 1 | AI236 | kW | 1 | Present Real Power Demand - Channel 1
2 | A | R |  | 1379 | 2338 | 2339 | 1043 | Present KW Demand | kW Present Demand: Channel 2 | AI237 | kW | 1 | Present Real Power Demand - Channel 2
3 | A | R |  | 1380 | 2340 | 2341 | 1044 | Present KW Demand | kW Present Demand: Channel 3 | AI238 | kW | 1 | Present Real Power Demand - Channel 3
4 | A | R |  | 1381 | 2342 | 2343 | 1045 | Present KW Demand | kW Present Demand: Channel 4 | AI239 | kW | 1 | Present Real Power Demand - Channel 4
5 | A | R |  | 1382 | 2344 | 2345 | 1046 | Present KW Demand | kW Present Demand: Channel 5 | AI240 | kW | 1 | Present Real Power Demand - Channel 5
6 | A | R |  | 1383 | 2346 | 2347 | 1047 | Present KW Demand | kW Present Demand: Channel 6 | AI241 | kW | 1 | Present Real Power Demand - Channel 6
7 | A | R |  | 1384 | 2348 | 2349 | 1048 | Present KW Demand | kW Present Demand: Channel 7 | AI242 | kW | 1 | Present Real Power Demand - Channel 7
8 | A | R |  | 1385 | 2350 | 2351 | 1049 | Present KW Demand | kW Present Demand: Channel 8 | AI243 | kW | 1 | Present Real Power Demand - Channel 8
9 | A | R |  | 1386 | 2352 | 2353 | 1050 | Present KW Demand | kW Present Demand: Channel 9 | AI244 | kW | 1 | Present Real Power Demand - Channel 9
10 | A | R |  | 1387 | 2354 | 2355 | 1051 | Present KW Demand | kW Present Demand: Channel 10 | AI245 | kW | 1 | Present Real Power Demand - Channel 10
11 | A | R |  | 1388 | 2356 | 2357 | 1052 | Present KW Demand | kW Present Demand: Channel 11 | AI246 | kW | 1 | Present Real Power Demand - Channel 11
12 | A | R |  | 1389 | 2358 | 2359 | 1053 | Present KW Demand | kW Present Demand: Channel 12 | AI247 | kW | 1 | Present Real Power Demand - Channel 12
13 | A | R |  | 1390 | 2360 | 2361 | 1054 | Present KW Demand | kW Present Demand: Channel 13 | AI248 | kW | 1 | Present Real Power Demand - Channel 13
14 | A | R |  | 1391 | 2362 | 2363 | 1055 | Present KW Demand | kW Present Demand: Channel 14 | AI249 | kW | 1 | Present Real Power Demand - Channel 14
15 | A | R |  | 1392 | 2364 | 2365 | 1056 | Present KW Demand | kW Present Demand: Channel 15 | AI250 | kW | 1 | Present Real Power Demand - Channel 15
16 | A | R |  | 1393 | 2366 | 2367 | 1057 | Present KW Demand | kW Present Demand: Channel 16 | AI251 | kW | 1 | Present Real Power Demand - Channel 16
17 | A | R |  | 1394 | 2368 | 2369 | 1058 | Present KW Demand | kW Present Demand: Channel 17 | AI252 | kW | 1 | Present Real Power Demand - Channel 17
18 | A | R |  | 1395 | 2370 | 2371 | 1059 | Present KW Demand | kW Present Demand: Channel 18 | AI253 | kW | 1 | Present Real Power Demand - Channel 18
19 | A | R |  | 1396 | 2372 | 2373 | 1060 | Present KW Demand | kW Present Demand: Channel 19 | AI254 | kW | 1 | Present Real Power Demand - Channel 19
20 | A | R |  | 1397 | 2374 | 2375 | 1061 | Present KW Demand | kW Present Demand: Channel 20 | AI255 | kW | 1 | Present Real Power Demand - Channel 20
21 | A | R |  | 1398 | 2376 | 2377 | 1062 | Present KW Demand | kW Present Demand: Channel 21 | AI256 | kW | 1 | Present Real Power Demand - Channel 21
22 | A | R |  | 1399 | 2378 | 2379 | 1063 | Present KW Demand | kW Present Demand: Channel 22 | AI257 | kW | 1 | Present Real Power Demand - Channel 22
23 | A | R |  | 1400 | 2380 | 2381 | 1064 | Present KW Demand | kW Present Demand: Channel 23 | AI258 | kW | 1 | Present Real Power Demand - Channel 23
24 | A | R |  | 1401 | 2382 | 2383 | 1065 | Present KW Demand | kW Present Demand: Channel 24 | AI259 | kW | 1 | Present Real Power Demand - Channel 24
25 | A | R |  | 1402 | 2384 | 2385 | 1066 | Present KW Demand | kW Present Demand: Channel 25 | AI260 | kW | 1 | Present Real Power Demand - Channel 25
26 | A | R |  | 1403 | 2386 | 2387 | 1067 | Present KW Demand | kW Present Demand: Channel 26 | AI261 | kW | 1 | Present Real Power Demand - Channel 26
27 | A | R |  | 1404 | 2388 | 2389 | 1068 | Present KW Demand | kW Present Demand: Channel 27 | AI262 | kW | 1 | Present Real Power Demand - Channel 27
28 | A | R |  | 1405 | 2390 | 2391 | 1069 | Present KW Demand | kW Present Demand: Channel 28 | AI263 | kW | 1 | Present Real Power Demand - Channel 28
29 | A | R |  | 1406 | 2392 | 2393 | 1070 | Present KW Demand | kW Present Demand: Channel 29 | AI264 | kW | 1 | Present Real Power Demand - Channel 29
30 | A | R |  | 1407 | 2394 | 2395 | 1071 | Present KW Demand | kW Present Demand: Channel 30 | AI265 | kW | 1 | Present Real Power Demand - Channel 30
31 | A | R |  | 1408 | 2396 | 2397 | 1072 | Present KW Demand | kW Present Demand: Channel 31 | AI266 | kW | 1 | Present Real Power Demand - Channel 31
32 | A | R |  | 1409 | 2398 | 2399 | 1073 | Present KW Demand | kW Present Demand: Channel 32 | AI267 | kW | 1 | Present Real Power Demand - Channel 32
33 | A | R |  | 1410 | 2400 | 2401 | 1074 | Present KW Demand | kW Present Demand: Channel 33 | AI268 | kW | 1 | Present Real Power Demand - Channel 33
34 | A | R |  | 1411 | 2402 | 2403 | 1075 | Present KW Demand | kW Present Demand: Channel 34 | AI269 | kW | 1 | Present Real Power Demand - Channel 34
35 | A | R |  | 1412 | 2404 | 2405 | 1076 | Present KW Demand | kW Present Demand: Channel 35 | AI270 | kW | 1 | Present Real Power Demand - Channel 35
36 | A | R |  | 1413 | 2406 | 2407 | 1077 | Present KW Demand | kW Present Demand: Channel 36 | AI271 | kW | 1 | Present Real Power Demand - Channel 36
37 | A | R |  | 1414 | 2408 | 2409 | 1078 | Present KW Demand | kW Present Demand: Channel 37 | AI272 | kW | 1 | Present Real Power Demand - Channel 37
38 | A | R |  | 1415 | 2410 | 2411 | 1079 | Present KW Demand | kW Present Demand: Channel 38 | AI273 | kW | 1 | Present Real Power Demand - Channel 38
39 | A | R |  | 1416 | 2412 | 2413 | 1080 | Present KW Demand | kW Present Demand: Channel 39 | AI274 | kW | 1 | Present Real Power Demand - Channel 39
40 | A | R |  | 1417 | 2414 | 2415 | 1081 | Present KW Demand | kW Present Demand: Channel 40 | AI275 | kW | 1 | Present Real Power Demand - Channel 40
41 | A | R |  | 1418 | 2416 | 2417 | 1082 | Present KW Demand | kW Present Demand: Channel 41 | AI276 | kW | 1 | Present Real Power Demand - Channel 41
42 | A | R |  | 1419 | 2418 | 2419 | 1083 | Present KW Demand | kW Present Demand: Channel 42 | AI277 | kW | 1 | Present Real Power Demand - Channel 42
1 | A | R | NV | 1420 | 2420 | 2421 | 1042 | Max KW Demand | kW Max Demand: Channel 1 | AI278 | kW | 1 | Max Real Power Demand - Channel 1
2 | A | R | NV | 1421 | 2422 | 2423 | 1043 | Max KW Demand | kW Max Demand: Channel 2 | AI279 | kW | 1 | Max Real Power Demand - Channel 2
3 | A | R | NV | 1422 | 2424 | 2425 | 1044 | Max KW Demand | kW Max Demand: Channel 3 | AI280 | kW | 1 | Max Real Power Demand - Channel 3
4 | A | R | NV | 1423 | 2426 | 2427 | 1045 | Max KW Demand | kW Max Demand: Channel 4 | AI281 | kW | 1 | Max Real Power Demand - Channel 4
5 | A | R | NV | 1424 | 2428 | 2429 | 1046 | Max KW Demand | kW Max Demand: Channel 5 | AI282 | kW | 1 | Max Real Power Demand - Channel 5
6 | A | R | NV | 1425 | 2430 | 2431 | 1047 | Max KW Demand | kW Max Demand: Channel 6 | AI283 | kW | 1 | Max Real Power Demand - Channel 6
7 | A | R | NV | 1426 | 2432 | 2433 | 1048 | Max KW Demand | kW Max Demand: Channel 7 | AI284 | kW | 1 | Max Real Power Demand - Channel 7
8 | A | R | NV | 1427 | 2434 | 2435 | 1049 | Max KW Demand | kW Max Demand: Channel 8 | AI285 | kW | 1 | Max Real Power Demand - Channel 8
9 | A | R | NV | 1428 | 2436 | 2437 | 1050 | Max KW Demand | kW Max Demand: Channel 9 | AI286 | kW | 1 | Max Real Power Demand - Channel 9
10 | A | R | NV | 1429 | 2438 | 2439 | 1051 | Max KW Demand | kW Max Demand: Channel 10 | AI287 | kW | 1 | Max Real Power Demand - Channel 10
11 | A | R | NV | 1430 | 2440 | 2441 | 1052 | Max KW Demand | kW Max Demand: Channel 11 | AI288 | kW | 1 | Max Real Power Demand - Channel 11
12 | A | R | NV | 1431 | 2442 | 2443 | 1053 | Max KW Demand | kW Max Demand: Channel 12 | AI289 | kW | 1 | Max Real Power Demand - Channel 12
13 | A | R | NV | 1432 | 2444 | 2445 | 1054 | Max KW Demand | kW Max Demand: Channel 13 | AI290 | kW | 1 | Max Real Power Demand - Channel 13
14 | A | R | NV | 1433 | 2446 | 2447 | 1055 | Max KW Demand | kW Max Demand: Channel 14 | AI291 | kW | 1 | Max Real Power Demand - Channel 14
15 | A | R | NV | 1434 | 2448 | 2449 | 1056 | Max KW Demand | kW Max Demand: Channel 15 | AI292 | kW | 1 | Max Real Power Demand - Channel 15
16 | A | R | NV | 1435 | 2450 | 2451 | 1057 | Max KW Demand | kW Max Demand: Channel 16 | AI293 | kW | 1 | Max Real Power Demand - Channel 16
17 | A | R | NV | 1436 | 2452 | 2453 | 1058 | Max KW Demand | kW Max Demand: Channel 17 | AI294 | kW | 1 | Max Real Power Demand - Channel 17
18 | A | R | NV | 1437 | 2454 | 2455 | 1059 | Max KW Demand | kW Max Demand: Channel 18 | AI295 | kW | 1 | Max Real Power Demand - Channel 18
19 | A | R | NV | 1438 | 2456 | 2457 | 1060 | Max KW Demand | kW Max Demand: Channel 19 | AI296 | kW | 1 | Max Real Power Demand - Channel 19
20 | A | R | NV | 1439 | 2458 | 2459 | 1061 | Max KW Demand | kW Max Demand: Channel 20 | AI297 | kW | 1 | Max Real Power Demand - Channel 20
21 | A | R | NV | 1440 | 2460 | 2461 | 1062 | Max KW Demand | kW Max Demand: Channel 21 | AI298 | kW | 1 | Max Real Power Demand - Channel 21
22 | A | R | NV | 1441 | 2462 | 2463 | 1063 | Max KW Demand | kW Max Demand: Channel 22 | AI299 | kW | 1 | Max Real Power Demand - Channel 22
23 | A | R | NV | 1442 | 2464 | 2465 | 1064 | Max KW Demand | kW Max Demand: Channel 23 | AI300 | kW | 1 | Max Real Power Demand - Channel 23
24 | A | R | NV | 1443 | 2466 | 2467 | 1065 | Max KW Demand | kW Max Demand: Channel 24 | AI301 | kW | 1 | Max Real Power Demand - Channel 24
25 | A | R | NV | 1444 | 2468 | 2469 | 1066 | Max KW Demand | kW Max Demand: Channel 25 | AI302 | kW | 1 | Max Real Power Demand - Channel 25
26 | A | R | NV | 1445 | 2470 | 2471 | 1067 | Max KW Demand | kW Max Demand: Channel 26 | AI303 | kW | 1 | Max Real Power Demand - Channel 26
27 | A | R | NV | 1446 | 2472 | 2473 | 1068 | Max KW Demand | kW Max Demand: Channel 27 | AI304 | kW | 1 | Max Real Power Demand - Channel 27
28 | A | R | NV | 1447 | 2474 | 2475 | 1069 | Max KW Demand | kW Max Demand: Channel 28 | AI305 | kW | 1 | Max Real Power Demand - Channel 28
29 | A | R | NV | 1448 | 2476 | 2477 | 1070 | Max KW Demand | kW Max Demand: Channel 29 | AI306 | kW | 1 | Max Real Power Demand - Channel 29
30 | A | R | NV | 1449 | 2478 | 2479 | 1071 | Max KW Demand | kW Max Demand: Channel 30 | AI307 | kW | 1 | Max Real Power Demand - Channel 30
31 | A | R | NV | 1450 | 2480 | 2481 | 1072 | Max KW Demand | kW Max Demand: Channel 31 | AI308 | kW | 1 | Max Real Power Demand - Channel 31
32 | A | R | NV | 1451 | 2482 | 2483 | 1073 | Max KW Demand | kW Max Demand: Channel 32 | AI309 | kW | 1 | Max Real Power Demand - Channel 32
33 | A | R | NV | 1452 | 2484 | 2485 | 1074 | Max KW Demand | kW Max Demand: Channel 33 | AI310 | kW | 1 | Max Real Power Demand - Channel 33
34 | A | R | NV | 1453 | 2486 | 2487 | 1075 | Max KW Demand | kW Max Demand: Channel 34 | AI311 | kW | 1 | Max Real Power Demand - Channel 34
35 | A | R | NV | 1454 | 2488 | 2489 | 1076 | Max KW Demand | kW Max Demand: Channel 35 | AI312 | kW | 1 | Max Real Power Demand - Channel 35
36 | A | R | NV | 1455 | 2490 | 2491 | 1077 | Max KW Demand | kW Max Demand: Channel 36 | AI313 | kW | 1 | Max Real Power Demand - Channel 36
37 | A | R | NV | 1456 | 2492 | 2493 | 1078 | Max KW Demand | kW Max Demand: Channel 37 | AI314 | kW | 1 | Max Real Power Demand - Channel 37
38 | A | R | NV | 1457 | 2494 | 2495 | 1079 | Max KW Demand | kW Max Demand: Channel 38 | AI315 | kW | 1 | Max Real Power Demand - Channel 38
39 | A | R | NV | 1458 | 2496 | 2497 | 1080 | Max KW Demand | kW Max Demand: Channel 39 | AI316 | kW | 1 | Max Real Power Demand - Channel 39
40 | A | R | NV | 1459 | 2498 | 2499 | 1081 | Max KW Demand | kW Max Demand: Channel 40 | AI317 | kW | 1 | Max Real Power Demand - Channel 40
41 | A | R | NV | 1460 | 2500 | 2501 | 1082 | Max KW Demand | kW Max Demand: Channel 41 | AI318 | kW | 1 | Max Real Power Demand - Channel 41
42 | A | R | NV | 1461 | 2502 | 2503 | 1083 | Max KW Demand | kW Max Demand: Channel 42 | AI319 | kW | 1 | Max Real Power Demand - Channel 42
1 | A,B,C | R |  | 1462 | 2504 | 2505 | 1000 | Present Current Demand | Amps Present Demand: Channel 1 | AI320 | Amperes | 5 | Present Current Demand - Channel 1
2 | A,B,C | R |  | 1463 | 2506 | 2507 | 1001 | Present Current Demand | Amps Present Demand: Channel 2 | AI321 | Amperes | 5 | Present Current Demand - Channel 2
3 | A,B,C | R |  | 1464 | 2508 | 2509 | 1002 | Present Current Demand | Amps Present Demand: Channel 3 | AI322 | Amperes | 5 | Present Current Demand - Channel 3
4 | A,B,C | R |  | 1465 | 2510 | 2511 | 1003 | Present Current Demand | Amps Present Demand: Channel 4 | AI323 | Amperes | 5 | Present Current Demand - Channel 4
5 | A,B,C | R |  | 1466 | 2512 | 2513 | 1004 | Present Current Demand | Amps Present Demand: Channel 5 | AI324 | Amperes | 5 | Present Current Demand - Channel 5
6 | A,B,C | R |  | 1467 | 2514 | 2515 | 1005 | Present Current Demand | Amps Present Demand: Channel 6 | AI325 | Amperes | 5 | Present Current Demand - Channel 6
7 | A,B,C | R |  | 1468 | 2516 | 2517 | 1006 | Present Current Demand | Amps Present Demand: Channel 7 | AI326 | Amperes | 5 | Present Current Demand - Channel 7
8 | A,B,C | R |  | 1469 | 2518 | 2519 | 1007 | Present Current Demand | Amps Present Demand: Channel 8 | AI327 | Amperes | 5 | Present Current Demand - Channel 8
9 | A,B,C | R |  | 1470 | 2520 | 2521 | 1008 | Present Current Demand | Amps Present Demand: Channel 9 | AI328 | Amperes | 5 | Present Current Demand - Channel 9
10 | A,B,C | R |  | 1471 | 2522 | 2523 | 1009 | Present Current Demand | Amps Present Demand: Channel 10 | AI329 | Amperes | 5 | Present Current Demand - Channel 10
11 | A,B,C | R |  | 1472 | 2524 | 2525 | 1010 | Present Current Demand | Amps Present Demand: Channel 11 | AI330 | Amperes | 5 | Present Current Demand - Channel 11
12 | A,B,C | R |  | 1473 | 2526 | 2527 | 1011 | Present Current Demand | Amps Present Demand: Channel 12 | AI331 | Amperes | 5 | Present Current Demand - Channel 12
13 | A,B,C | R |  | 1474 | 2528 | 2529 | 1012 | Present Current Demand | Amps Present Demand: Channel 13 | AI332 | Amperes | 5 | Present Current Demand - Channel 13
14 | A,B,C | R |  | 1475 | 2530 | 2531 | 1013 | Present Current Demand | Amps Present Demand: Channel 14 | AI333 | Amperes | 5 | Present Current Demand - Channel 14
15 | A,B,C | R |  | 1476 | 2532 | 2533 | 1014 | Present Current Demand | Amps Present Demand: Channel 15 | AI334 | Amperes | 5 | Present Current Demand - Channel 15
16 | A,B,C | R |  | 1477 | 2534 | 2535 | 1015 | Present Current Demand | Amps Present Demand: Channel 16 | AI335 | Amperes | 5 | Present Current Demand - Channel 16
17 | A,B,C | R |  | 1478 | 2536 | 2537 | 1016 | Present Current Demand | Amps Present Demand: Channel 17 | AI336 | Amperes | 5 | Present Current Demand - Channel 17
18 | A,B,C | R |  | 1479 | 2538 | 2539 | 1017 | Present Current Demand | Amps Present Demand: Channel 18 | AI337 | Amperes | 5 | Present Current Demand - Channel 18
19 | A,B,C | R |  | 1480 | 2540 | 2541 | 1018 | Present Current Demand | Amps Present Demand: Channel 19 | AI338 | Amperes | 5 | Present Current Demand - Channel 19
20 | A,B,C | R |  | 1481 | 2542 | 2543 | 1019 | Present Current Demand | Amps Present Demand: Channel 20 | AI339 | Amperes | 5 | Present Current Demand - Channel 20
21 | A,B,C | R |  | 1482 | 2544 | 2545 | 1020 | Present Current Demand | Amps Present Demand: Channel 21 | AI340 | Amperes | 5 | Present Current Demand - Channel 21
22 | A,B,C | R |  | 1483 | 2546 | 2547 | 1021 | Present Current Demand | Amps Present Demand: Channel 22 | AI341 | Amperes | 5 | Present Current Demand - Channel 22
23 | A,B,C | R |  | 1484 | 2548 | 2549 | 1022 | Present Current Demand | Amps Present Demand: Channel 23 | AI342 | Amperes | 5 | Present Current Demand - Channel 23
24 | A,B,C | R |  | 1485 | 2550 | 2551 | 1023 | Present Current Demand | Amps Present Demand: Channel 24 | AI343 | Amperes | 5 | Present Current Demand - Channel 24
25 | A,B,C | R |  | 1486 | 2552 | 2553 | 1024 | Present Current Demand | Amps Present Demand: Channel 25 | AI344 | Amperes | 5 | Present Current Demand - Channel 25
26 | A,B,C | R |  | 1487 | 2554 | 2555 | 1025 | Present Current Demand | Amps Present Demand: Channel 26 | AI345 | Amperes | 5 | Present Current Demand - Channel 26
27 | A,B,C | R |  | 1488 | 2556 | 2557 | 1026 | Present Current Demand | Amps Present Demand: Channel 27 | AI346 | Amperes | 5 | Present Current Demand - Channel 27
28 | A,B,C | R |  | 1489 | 2558 | 2559 | 1027 | Present Current Demand | Amps Present Demand: Channel 28 | AI347 | Amperes | 5 | Present Current Demand - Channel 28
29 | A,B,C | R |  | 1490 | 2560 | 2561 | 1028 | Present Current Demand | Amps Present Demand: Channel 29 | AI348 | Amperes | 5 | Present Current Demand - Channel 29
30 | A,B,C | R |  | 1491 | 2562 | 2563 | 1029 | Present Current Demand | Amps Present Demand: Channel 30 | AI349 | Amperes | 5 | Present Current Demand - Channel 30
31 | A,B,C | R |  | 1492 | 2564 | 2565 | 1030 | Present Current Demand | Amps Present Demand: Channel 31 | AI350 | Amperes | 5 | Present Current Demand - Channel 31
32 | A,B,C | R |  | 1493 | 2566 | 2567 | 1031 | Present Current Demand | Amps Present Demand: Channel 32 | AI351 | Amperes | 5 | Present Current Demand - Channel 32
33 | A,B,C | R |  | 1494 | 2568 | 2569 | 1032 | Present Current Demand | Amps Present Demand: Channel 33 | AI352 | Amperes | 5 | Present Current Demand - Channel 33
34 | A,B,C | R |  | 1495 | 2570 | 2571 | 1033 | Present Current Demand | Amps Present Demand: Channel 34 | AI353 | Amperes | 5 | Present Current Demand - Channel 34
35 | A,B,C | R |  | 1496 | 2572 | 2573 | 1034 | Present Current Demand | Amps Present Demand: Channel 35 | AI354 | Amperes | 5 | Present Current Demand - Channel 35
36 | A,B,C | R |  | 1497 | 2574 | 2575 | 1035 | Present Current Demand | Amps Present Demand: Channel 36 | AI355 | Amperes | 5 | Present Current Demand - Channel 36
37 | A,B,C | R |  | 1498 | 2576 | 2577 | 1036 | Present Current Demand | Amps Present Demand: Channel 37 | AI356 | Amperes | 5 | Present Current Demand - Channel 37
38 | A,B,C | R |  | 1499 | 2578 | 2579 | 1037 | Present Current Demand | Amps Present Demand: Channel 38 | AI357 | Amperes | 5 | Present Current Demand - Channel 38
39 | A,B,C | R |  | 1500 | 2580 | 2581 | 1038 | Present Current Demand | Amps Present Demand: Channel 39 | AI358 | Amperes | 5 | Present Current Demand - Channel 39
40 | A,B,C | R |  | 1501 | 2582 | 2583 | 1039 | Present Current Demand | Amps Present Demand: Channel 40 | AI359 | Amperes | 5 | Present Current Demand - Channel 40
41 | A,B,C | R |  | 1502 | 2584 | 2585 | 1040 | Present Current Demand | Amps Present Demand: Channel 41 | AI360 | Amperes | 5 | Present Current Demand - Channel 41
42 | A,B,C | R |  | 1503 | 2586 | 2587 | 1041 | Present Current Demand | Amps Present Demand: Channel 42 | AI361 | Amperes | 5 | Present Current Demand - Channel 42
1 | A,B,C | R | NV | 1504 | 2588 | 2589 | 1000 | Max Current Demand | Amps Max Demand: Channel 1 | AI362 | Amperes | 5 | Max Current Demand - Channel 1
2 | A,B,C | R | NV | 1505 | 2590 | 2591 | 1001 | Max Current Demand | Amps Max Demand: Channel 2 | AI363 | Amperes | 5 | Max Current Demand - Channel 2
3 | A,B,C | R | NV | 1506 | 2592 | 2593 | 1002 | Max Current Demand | Amps Max Demand: Channel 3 | AI364 | Amperes | 5 | Max Current Demand - Channel 3
4 | A,B,C | R | NV | 1507 | 2594 | 2595 | 1003 | Max Current Demand | Amps Max Demand: Channel 4 | AI365 | Amperes | 5 | Max Current Demand - Channel 4
5 | A,B,C | R | NV | 1508 | 2596 | 2597 | 1004 | Max Current Demand | Amps Max Demand: Channel 5 | AI366 | Amperes | 5 | Max Current Demand - Channel 5
6 | A,B,C | R | NV | 1509 | 2598 | 2599 | 1005 | Max Current Demand | Amps Max Demand: Channel 6 | AI367 | Amperes | 5 | Max Current Demand - Channel 6
7 | A,B,C | R | NV | 1510 | 2600 | 2601 | 1006 | Max Current Demand | Amps Max Demand: Channel 7 | AI368 | Amperes | 5 | Max Current Demand - Channel 7
8 | A,B,C | R | NV | 1511 | 2602 | 2603 | 1007 | Max Current Demand | Amps Max Demand: Channel 8 | AI369 | Amperes | 5 | Max Current Demand - Channel 8
9 | A,B,C | R | NV | 1512 | 2604 | 2605 | 1008 | Max Current Demand | Amps Max Demand: Channel 9 | AI370 | Amperes | 5 | Max Current Demand - Channel 9
10 | A,B,C | R | NV | 1513 | 2606 | 2607 | 1009 | Max Current Demand | Amps Max Demand: Channel 10 | AI371 | Amperes | 5 | Max Current Demand - Channel 10
11 | A,B,C | R | NV | 1514 | 2608 | 2609 | 1010 | Max Current Demand | Amps Max Demand: Channel 11 | AI372 | Amperes | 5 | Max Current Demand - Channel 11
12 | A,B,C | R | NV | 1515 | 2610 | 2611 | 1011 | Max Current Demand | Amps Max Demand: Channel 12 | AI373 | Amperes | 5 | Max Current Demand - Channel 12
13 | A,B,C | R | NV | 1516 | 2612 | 2613 | 1012 | Max Current Demand | Amps Max Demand: Channel 13 | AI374 | Amperes | 5 | Max Current Demand - Channel 13
14 | A,B,C | R | NV | 1517 | 2614 | 2615 | 1013 | Max Current Demand | Amps Max Demand: Channel 14 | AI375 | Amperes | 5 | Max Current Demand - Channel 14
15 | A,B,C | R | NV | 1518 | 2616 | 2617 | 1014 | Max Current Demand | Amps Max Demand: Channel 15 | AI376 | Amperes | 5 | Max Current Demand - Channel 15
16 | A,B,C | R | NV | 1519 | 2618 | 2619 | 1015 | Max Current Demand | Amps Max Demand: Channel 16 | AI377 | Amperes | 5 | Max Current Demand - Channel 16
17 | A,B,C | R | NV | 1520 | 2620 | 2621 | 1016 | Max Current Demand | Amps Max Demand: Channel 17 | AI378 | Amperes | 5 | Max Current Demand - Channel 17
18 | A,B,C | R | NV | 1521 | 2622 | 2623 | 1017 | Max Current Demand | Amps Max Demand: Channel 18 | AI379 | Amperes | 5 | Max Current Demand - Channel 18
19 | A,B,C | R | NV | 1522 | 2624 | 2625 | 1018 | Max Current Demand | Amps Max Demand: Channel 19 | AI380 | Amperes | 5 | Max Current Demand - Channel 19
20 | A,B,C | R | NV | 1523 | 2626 | 2627 | 1019 | Max Current Demand | Amps Max Demand: Channel 20 | AI381 | Amperes | 5 | Max Current Demand - Channel 20
21 | A,B,C | R | NV | 1524 | 2628 | 2629 | 1020 | Max Current Demand | Amps Max Demand: Channel 21 | AI382 | Amperes | 5 | Max Current Demand - Channel 21
22 | A,B,C | R | NV | 1525 | 2630 | 2631 | 1021 | Max Current Demand | Amps Max Demand: Channel 22 | AI383 | Amperes | 5 | Max Current Demand - Channel 22
23 | A,B,C | R | NV | 1526 | 2632 | 2633 | 1022 | Max Current Demand | Amps Max Demand: Channel 23 | AI384 | Amperes | 5 | Max Current Demand - Channel 23
24 | A,B,C | R | NV | 1527 | 2634 | 2635 | 1023 | Max Current Demand | Amps Max Demand: Channel 24 | AI385 | Amperes | 5 | Max Current Demand - Channel 24
25 | A,B,C | R | NV | 1528 | 2636 | 2637 | 1024 | Max Current Demand | Amps Max Demand: Channel 25 | AI386 | Amperes | 5 | Max Current Demand - Channel 25
26 | A,B,C | R | NV | 1529 | 2638 | 2639 | 1025 | Max Current Demand | Amps Max Demand: Channel 26 | AI387 | Amperes | 5 | Max Current Demand - Channel 26
27 | A,B,C | R | NV | 1530 | 2640 | 2641 | 1026 | Max Current Demand | Amps Max Demand: Channel 27 | AI388 | Amperes | 5 | Max Current Demand - Channel 27
28 | A,B,C | R | NV | 1531 | 2642 | 2643 | 1027 | Max Current Demand | Amps Max Demand: Channel 28 | AI389 | Amperes | 5 | Max Current Demand - Channel 28
29 | A,B,C | R | NV | 1532 | 2644 | 2645 | 1028 | Max Current Demand | Amps Max Demand: Channel 29 | AI390 | Amperes | 5 | Max Current Demand - Channel 29
30 | A,B,C | R | NV | 1533 | 2646 | 2647 | 1029 | Max Current Demand | Amps Max Demand: Channel 30 | AI391 | Amperes | 5 | Max Current Demand - Channel 30
31 | A,B,C | R | NV | 1534 | 2648 | 2649 | 1030 | Max Current Demand | Amps Max Demand: Channel 31 | AI392 | Amperes | 5 | Max Current Demand - Channel 31
32 | A,B,C | R | NV | 1535 | 2650 | 2651 | 1031 | Max Current Demand | Amps Max Demand: Channel 32 | AI393 | Amperes | 5 | Max Current Demand - Channel 32
33 | A,B,C | R | NV | 1536 | 2652 | 2653 | 1032 | Max Current Demand | Amps Max Demand: Channel 33 | AI394 | Amperes | 5 | Max Current Demand - Channel 33
34 | A,B,C | R | NV | 1537 | 2654 | 2655 | 1033 | Max Current Demand | Amps Max Demand: Channel 34 | AI395 | Amperes | 5 | Max Current Demand - Channel 34
35 | A,B,C | R | NV | 1538 | 2656 | 2657 | 1034 | Max Current Demand | Amps Max Demand: Channel 35 | AI396 | Amperes | 5 | Max Current Demand - Channel 35
36 | A,B,C | R | NV | 1539 | 2658 | 2659 | 1035 | Max Current Demand | Amps Max Demand: Channel 36 | AI397 | Amperes | 5 | Max Current Demand - Channel 36
37 | A,B,C | R | NV | 1540 | 2660 | 2661 | 1036 | Max Current Demand | Amps Max Demand: Channel 37 | AI398 | Amperes | 5 | Max Current Demand - Channel 37
38 | A,B,C | R | NV | 1541 | 2662 | 2663 | 1037 | Max Current Demand | Amps Max Demand: Channel 38 | AI399 | Amperes | 5 | Max Current Demand - Channel 38
39 | A,B,C | R | NV | 1542 | 2664 | 2665 | 1038 | Max Current Demand | Amps Max Demand: Channel 39 | AI400 | Amperes | 5 | Max Current Demand - Channel 39
40 | A,B,C | R | NV | 1543 | 2666 | 2667 | 1039 | Max Current Demand | Amps Max Demand: Channel 40 | AI401 | Amperes | 5 | Max Current Demand - Channel 40
41 | A,B,C | R | NV | 1544 | 2668 | 2669 | 1040 | Max Current Demand | Amps Max Demand: Channel 41 | AI402 | Amperes | 5 | Max Current Demand - Channel 41
42 | A,B,C | R | NV | 1545 | 2670 | 2671 | 1041 | Max Current Demand | Amps Max Demand: Channel 42 | AI403 | Amperes | 5 | Max Current Demand - Channel 42
1 | A | R | NV | 1546 | 2672 | 2673 | 1042 | Max KW-Total | kW Max Total: Channel 1 | AI404 | kW | 1 | Max Instantaneous Real Power - Chan 1
2 | A | R | NV | 1547 | 2674 | 2675 | 1043 | Max KW-Total | kW Max Total: Channel 2 | AI405 | kW | 1 | Max Instantaneous Real Power - Chan 2
3 | A | R | NV | 1548 | 2676 | 2677 | 1044 | Max KW-Total | kW Max Total: Channel 3 | AI406 | kW | 1 | Max Instantaneous Real Power - Chan 3
4 | A | R | NV | 1549 | 2678 | 2679 | 1045 | Max KW-Total | kW Max Total: Channel 4 | AI407 | kW | 1 | Max Instantaneous Real Power - Chan 4
5 | A | R | NV | 1550 | 2680 | 2681 | 1046 | Max KW-Total | kW Max Total: Channel 5 | AI408 | kW | 1 | Max Instantaneous Real Power - Chan 5
6 | A | R | NV | 1551 | 2682 | 2683 | 1047 | Max KW-Total | kW Max Total: Channel 6 | AI409 | kW | 1 | Max Instantaneous Real Power - Chan 6
7 | A | R | NV | 1552 | 2684 | 2685 | 1048 | Max KW-Total | kW Max Total: Channel 7 | AI410 | kW | 1 | Max Instantaneous Real Power - Chan 7
8 | A | R | NV | 1553 | 2686 | 2687 | 1049 | Max KW-Total | kW Max Total: Channel 8 | AI411 | kW | 1 | Max Instantaneous Real Power - Chan 8
9 | A | R | NV | 1554 | 2688 | 2689 | 1050 | Max KW-Total | kW Max Total: Channel 9 | AI412 | kW | 1 | Max Instantaneous Real Power - Chan 9
10 | A | R | NV | 1555 | 2690 | 2691 | 1051 | Max KW-Total | kW Max Total: Channel 10 | AI413 | kW | 1 | Max Instantaneous Real Power - Chan 10
11 | A | R | NV | 1556 | 2692 | 2693 | 1052 | Max KW-Total | kW Max Total: Channel 11 | AI414 | kW | 1 | Max Instantaneous Real Power - Chan 11
12 | A | R | NV | 1557 | 2694 | 2695 | 1053 | Max KW-Total | kW Max Total: Channel 12 | AI415 | kW | 1 | Max Instantaneous Real Power - Chan 12
13 | A | R | NV | 1558 | 2696 | 2697 | 1054 | Max KW-Total | kW Max Total: Channel 13 | AI416 | kW | 1 | Max Instantaneous Real Power - Chan 13
14 | A | R | NV | 1559 | 2698 | 2699 | 1055 | Max KW-Total | kW Max Total: Channel 14 | AI417 | kW | 1 | Max Instantaneous Real Power - Chan 14
15 | A | R | NV | 1560 | 2700 | 2701 | 1056 | Max KW-Total | kW Max Total: Channel 15 | AI418 | kW | 1 | Max Instantaneous Real Power - Chan 15
16 | A | R | NV | 1561 | 2702 | 2703 | 1057 | Max KW-Total | kW Max Total: Channel 16 | AI419 | kW | 1 | Max Instantaneous Real Power - Chan 16
17 | A | R | NV | 1562 | 2704 | 2705 | 1058 | Max KW-Total | kW Max Total: Channel 17 | AI420 | kW | 1 | Max Instantaneous Real Power - Chan 17
18 | A | R | NV | 1563 | 2706 | 2707 | 1059 | Max KW-Total | kW Max Total: Channel 18 | AI421 | kW | 1 | Max Instantaneous Real Power - Chan 18
19 | A | R | NV | 1564 | 2708 | 2709 | 1060 | Max KW-Total | kW Max Total: Channel 19 | AI422 | kW | 1 | Max Instantaneous Real Power - Chan 19
20 | A | R | NV | 1565 | 2710 | 2711 | 1061 | Max KW-Total | kW Max Total: Channel 20 | AI423 | kW | 1 | Max Instantaneous Real Power - Chan 20
21 | A | R | NV | 1566 | 2712 | 2713 | 1062 | Max KW-Total | kW Max Total: Channel 21 | AI424 | kW | 1 | Max Instantaneous Real Power - Chan 21
22 | A | R | NV | 1567 | 2714 | 2715 | 1063 | Max KW-Total | kW Max Total: Channel 22 | AI425 | kW | 1 | Max Instantaneous Real Power - Chan 22
23 | A | R | NV | 1568 | 2716 | 2717 | 1064 | Max KW-Total | kW Max Total: Channel 23 | AI426 | kW | 1 | Max Instantaneous Real Power - Chan 23
24 | A | R | NV | 1569 | 2718 | 2719 | 1065 | Max KW-Total | kW Max Total: Channel 24 | AI427 | kW | 1 | Max Instantaneous Real Power - Chan 24
25 | A | R | NV | 1570 | 2720 | 2721 | 1066 | Max KW-Total | kW Max Total: Channel 25 | AI428 | kW | 1 | Max Instantaneous Real Power - Chan 25
26 | A | R | NV | 1571 | 2722 | 2723 | 1067 | Max KW-Total | kW Max Total: Channel 26 | AI429 | kW | 1 | Max Instantaneous Real Power - Chan 26
27 | A | R | NV | 1572 | 2724 | 2725 | 1068 | Max KW-Total | kW Max Total: Channel 27 | AI430 | kW | 1 | Max Instantaneous Real Power - Chan 27
28 | A | R | NV | 1573 | 2726 | 2727 | 1069 | Max KW-Total | kW Max Total: Channel 28 | AI431 | kW | 1 | Max Instantaneous Real Power - Chan 28
29 | A | R | NV | 1574 | 2728 | 2729 | 1070 | Max KW-Total | kW Max Total: Channel 29 | AI432 | kW | 1 | Max Instantaneous Real Power - Chan 29
30 | A | R | NV | 1575 | 2730 | 2731 | 1071 | Max KW-Total | kW Max Total: Channel 30 | AI433 | kW | 1 | Max Instantaneous Real Power - Chan 30
31 | A | R | NV | 1576 | 2732 | 2733 | 1072 | Max KW-Total | kW Max Total: Channel 31 | AI434 | kW | 1 | Max Instantaneous Real Power - Chan 31
32 | A | R | NV | 1577 | 2734 | 2735 | 1073 | Max KW-Total | kW Max Total: Channel 32 | AI435 | kW | 1 | Max Instantaneous Real Power - Chan 32
33 | A | R | NV | 1578 | 2736 | 2737 | 1074 | Max KW-Total | kW Max Total: Channel 33 | AI436 | kW | 1 | Max Instantaneous Real Power - Chan 33
34 | A | R | NV | 1579 | 2738 | 2739 | 1075 | Max KW-Total | kW Max Total: Channel 34 | AI437 | kW | 1 | Max Instantaneous Real Power - Chan 34
35 | A | R | NV | 1580 | 2740 | 2741 | 1076 | Max KW-Total | kW Max Total: Channel 35 | AI438 | kW | 1 | Max Instantaneous Real Power - Chan 35
36 | A | R | NV | 1581 | 2742 | 2743 | 1077 | Max KW-Total | kW Max Total: Channel 36 | AI439 | kW | 1 | Max Instantaneous Real Power - Chan 36
37 | A | R | NV | 1582 | 2744 | 2745 | 1078 | Max KW-Total | kW Max Total: Channel 37 | AI440 | kW | 1 | Max Instantaneous Real Power - Chan 37
38 | A | R | NV | 1583 | 2746 | 2747 | 1079 | Max KW-Total | kW Max Total: Channel 38 | AI441 | kW | 1 | Max Instantaneous Real Power - Chan 38
39 | A | R | NV | 1584 | 2748 | 2749 | 1080 | Max KW-Total | kW Max Total: Channel 39 | AI442 | kW | 1 | Max Instantaneous Real Power - Chan 39
40 | A | R | NV | 1585 | 2750 | 2751 | 1081 | Max KW-Total | kW Max Total: Channel 40 | AI443 | kW | 1 | Max Instantaneous Real Power - Chan 40
41 | A | R | NV | 1586 | 2752 | 2753 | 1082 | Max KW-Total | kW Max Total: Channel 41 | AI444 | kW | 1 | Max Instantaneous Real Power - Chan 41
42 | A | R | NV | 1587 | 2754 | 2755 | 1083 | Max KW-Total | kW Max Total: Channel 42 | AI445 | kW | 1 | Max Instantaneous Real Power - Chan 42
1 | A,B,C | R | NV | 1588 | 2756 | 2757 | 1000 | Max Current | Max Amps: Channel 1 | AI446 | Amperes | 5 | Max Instantaneous Current - Channel 1
2 | A,B,C | R | NV | 1589 | 2758 | 2759 | 1001 | Max Current | Max Amps: Channel 2 | AI447 | Amperes | 5 | Max Instantaneous Current - Channel 2
3 | A,B,C | R | NV | 1590 | 2760 | 2761 | 1002 | Max Current | Max Amps: Channel 3 | AI448 | Amperes | 5 | Max Instantaneous Current - Channel 3
4 | A,B,C | R | NV | 1591 | 2762 | 2763 | 1003 | Max Current | Max Amps: Channel 4 | AI449 | Amperes | 5 | Max Instantaneous Current - Channel 4
5 | A,B,C | R | NV | 1592 | 2764 | 2765 | 1004 | Max Current | Max Amps: Channel 5 | AI450 | Amperes | 5 | Max Instantaneous Current - Channel 5
6 | A,B,C | R | NV | 1593 | 2766 | 2767 | 1005 | Max Current | Max Amps: Channel 6 | AI451 | Amperes | 5 | Max Instantaneous Current - Channel 6
7 | A,B,C | R | NV | 1594 | 2768 | 2769 | 1006 | Max Current | Max Amps: Channel 7 | AI452 | Amperes | 5 | Max Instantaneous Current - Channel 7
8 | A,B,C | R | NV | 1595 | 2770 | 2771 | 1007 | Max Current | Max Amps: Channel 8 | AI453 | Amperes | 5 | Max Instantaneous Current - Channel 8
9 | A,B,C | R | NV | 1596 | 2772 | 2773 | 1008 | Max Current | Max Amps: Channel 9 | AI454 | Amperes | 5 | Max Instantaneous Current - Channel 9
10 | A,B,C | R | NV | 1597 | 2774 | 2775 | 1009 | Max Current | Max Amps: Channel 10 | AI455 | Amperes | 5 | Max Instantaneous Current - Channel 10
11 | A,B,C | R | NV | 1598 | 2776 | 2777 | 1010 | Max Current | Max Amps: Channel 11 | AI456 | Amperes | 5 | Max Instantaneous Current - Channel 11
12 | A,B,C | R | NV | 1599 | 2778 | 2779 | 1011 | Max Current | Max Amps: Channel 12 | AI457 | Amperes | 5 | Max Instantaneous Current - Channel 12
13 | A,B,C | R | NV | 1600 | 2780 | 2781 | 1012 | Max Current | Max Amps: Channel 13 | AI458 | Amperes | 5 | Max Instantaneous Current - Channel 13
14 | A,B,C | R | NV | 1601 | 2782 | 2783 | 1013 | Max Current | Max Amps: Channel 14 | AI459 | Amperes | 5 | Max Instantaneous Current - Channel 14
15 | A,B,C | R | NV | 1602 | 2784 | 2785 | 1014 | Max Current | Max Amps: Channel 15 | AI460 | Amperes | 5 | Max Instantaneous Current - Channel 15
16 | A,B,C | R | NV | 1603 | 2786 | 2787 | 1015 | Max Current | Max Amps: Channel 16 | AI461 | Amperes | 5 | Max Instantaneous Current - Channel 16
17 | A,B,C | R | NV | 1604 | 2788 | 2789 | 1016 | Max Current | Max Amps: Channel 17 | AI462 | Amperes | 5 | Max Instantaneous Current - Channel 17
18 | A,B,C | R | NV | 1605 | 2790 | 2791 | 1017 | Max Current | Max Amps: Channel 18 | AI463 | Amperes | 5 | Max Instantaneous Current - Channel 18
19 | A,B,C | R | NV | 1606 | 2792 | 2793 | 1018 | Max Current | Max Amps: Channel 19 | AI464 | Amperes | 5 | Max Instantaneous Current - Channel 19
20 | A,B,C | R | NV | 1607 | 2794 | 2795 | 1019 | Max Current | Max Amps: Channel 20 | AI465 | Amperes | 5 | Max Instantaneous Current - Channel 20
21 | A,B,C | R | NV | 1608 | 2796 | 2797 | 1020 | Max Current | Max Amps: Channel 21 | AI466 | Amperes | 5 | Max Instantaneous Current - Channel 21
22 | A,B,C | R | NV | 1609 | 2798 | 2799 | 1021 | Max Current | Max Amps: Channel 22 | AI467 | Amperes | 5 | Max Instantaneous Current - Channel 22
23 | A,B,C | R | NV | 1610 | 2800 | 2801 | 1022 | Max Current | Max Amps: Channel 23 | AI468 | Amperes | 5 | Max Instantaneous Current - Channel 23
24 | A,B,C | R | NV | 1611 | 2802 | 2803 | 1023 | Max Current | Max Amps: Channel 24 | AI469 | Amperes | 5 | Max Instantaneous Current - Channel 24
25 | A,B,C | R | NV | 1612 | 2804 | 2805 | 1024 | Max Current | Max Amps: Channel 25 | AI470 | Amperes | 5 | Max Instantaneous Current - Channel 25
26 | A,B,C | R | NV | 1613 | 2806 | 2807 | 1025 | Max Current | Max Amps: Channel 26 | AI471 | Amperes | 5 | Max Instantaneous Current - Channel 26
27 | A,B,C | R | NV | 1614 | 2808 | 2809 | 1026 | Max Current | Max Amps: Channel 27 | AI472 | Amperes | 5 | Max Instantaneous Current - Channel 27
28 | A,B,C | R | NV | 1615 | 2810 | 2811 | 1027 | Max Current | Max Amps: Channel 28 | AI473 | Amperes | 5 | Max Instantaneous Current - Channel 28
29 | A,B,C | R | NV | 1616 | 2812 | 2813 | 1028 | Max Current | Max Amps: Channel 29 | AI474 | Amperes | 5 | Max Instantaneous Current - Channel 29
30 | A,B,C | R | NV | 1617 | 2814 | 2815 | 1029 | Max Current | Max Amps: Channel 30 | AI475 | Amperes | 5 | Max Instantaneous Current - Channel 30
31 | A,B,C | R | NV | 1618 | 2816 | 2817 | 1030 | Max Current | Max Amps: Channel 31 | AI476 | Amperes | 5 | Max Instantaneous Current - Channel 31
32 | A,B,C | R | NV | 1619 | 2818 | 2819 | 1031 | Max Current | Max Amps: Channel 32 | AI477 | Amperes | 5 | Max Instantaneous Current - Channel 32
33 | A,B,C | R | NV | 1620 | 2820 | 2821 | 1032 | Max Current | Max Amps: Channel 33 | AI478 | Amperes | 5 | Max Instantaneous Current - Channel 33
34 | A,B,C | R | NV | 1621 | 2822 | 2823 | 1033 | Max Current | Max Amps: Channel 34 | AI479 | Amperes | 5 | Max Instantaneous Current - Channel 34
35 | A,B,C | R | NV | 1622 | 2824 | 2825 | 1034 | Max Current | Max Amps: Channel 35 | AI480 | Amperes | 5 | Max Instantaneous Current - Channel 35
36 | A,B,C | R | NV | 1623 | 2826 | 2827 | 1035 | Max Current | Max Amps: Channel 36 | AI481 | Amperes | 5 | Max Instantaneous Current - Channel 36
37 | A,B,C | R | NV | 1624 | 2828 | 2829 | 1036 | Max Current | Max Amps: Channel 37 | AI482 | Amperes | 5 | Max Instantaneous Current - Channel 37
38 | A,B,C | R | NV | 1625 | 2830 | 2831 | 1037 | Max Current | Max Amps: Channel 38 | AI483 | Amperes | 5 | Max Instantaneous Current - Channel 38
39 | A,B,C | R | NV | 1626 | 2832 | 2833 | 1038 | Max Current | Max Amps: Channel 39 | AI484 | Amperes | 5 | Max Instantaneous Current - Channel 39
40 | A,B,C | R | NV | 1627 | 2834 | 2835 | 1039 | Max Current | Max Amps: Channel 40 | AI485 | Amperes | 5 | Max Instantaneous Current - Channel 40
41 | A,B,C | R | NV | 1628 | 2836 | 2837 | 1040 | Max Current | Max Amps: Channel 41 | AI486 | Amperes | 5 | Max Instantaneous Current - Channel 41
42 | A,B,C | R | NV | 1629 | 2838 | 2839 | 1041 | Max Current | Max Amps: Channel 42 | AI487 | Amperes | 5 | Max Instantaneous Current - Channel 42
1 | A | R |  | 1630 | 2840 | 2841 | 1042 | KVA | kVA: Channel 1 | AI488 | kVA | 1 | Instantaneous Apparent Power - Chan 1
2 | A | R |  | 1631 | 2842 | 2843 | 1043 | KVA | kVA: Channel 2 | AI489 | kVA | 1 | Instantaneous Apparent Power - Chan 2
3 | A | R |  | 1632 | 2844 | 2845 | 1044 | KVA | kVA: Channel 3 | AI490 | kVA | 1 | Instantaneous Apparent Power - Chan 3
4 | A | R |  | 1633 | 2846 | 2847 | 1045 | KVA | kVA: Channel 4 | AI491 | kVA | 1 | Instantaneous Apparent Power - Chan 4
5 | A | R |  | 1634 | 2848 | 2849 | 1046 | KVA | kVA: Channel 5 | AI492 | kVA | 1 | Instantaneous Apparent Power - Chan 5
6 | A | R |  | 1635 | 2850 | 2851 | 1047 | KVA | kVA: Channel 6 | AI493 | kVA | 1 | Instantaneous Apparent Power - Chan 6
7 | A | R |  | 1636 | 2852 | 2853 | 1048 | KVA | kVA: Channel 7 | AI494 | kVA | 1 | Instantaneous Apparent Power - Chan 7
8 | A | R |  | 1637 | 2854 | 2855 | 1049 | KVA | kVA: Channel 8 | AI495 | kVA | 1 | Instantaneous Apparent Power - Chan 8
9 | A | R |  | 1638 | 2856 | 2857 | 1050 | KVA | kVA: Channel 9 | AI496 | kVA | 1 | Instantaneous Apparent Power - Chan 9
10 | A | R |  | 1639 | 2858 | 2859 | 1051 | KVA | kVA: Channel 10 | AI497 | kVA | 1 | Instantaneous Apparent Power - Chan 10
11 | A | R |  | 1640 | 2860 | 2861 | 1052 | KVA | kVA: Channel 11 | AI498 | kVA | 1 | Instantaneous Apparent Power - Chan 11
12 | A | R |  | 1641 | 2862 | 2863 | 1053 | KVA | kVA: Channel 12 | AI499 | kVA | 1 | Instantaneous Apparent Power - Chan 12
13 | A | R |  | 1642 | 2864 | 2865 | 1054 | KVA | kVA: Channel 13 | AI500 | kVA | 1 | Instantaneous Apparent Power - Chan 13
14 | A | R |  | 1643 | 2866 | 2867 | 1055 | KVA | kVA: Channel 14 | AI501 | kVA | 1 | Instantaneous Apparent Power - Chan 14
15 | A | R |  | 1644 | 2868 | 2869 | 1056 | KVA | kVA: Channel 15 | AI502 | kVA | 1 | Instantaneous Apparent Power - Chan 15
16 | A | R |  | 1645 | 2870 | 2871 | 1057 | KVA | kVA: Channel 16 | AI503 | kVA | 1 | Instantaneous Apparent Power - Chan 16
17 | A | R |  | 1646 | 2872 | 2873 | 1058 | KVA | kVA: Channel 17 | AI504 | kVA | 1 | Instantaneous Apparent Power - Chan 17
18 | A | R |  | 1647 | 2874 | 2875 | 1059 | KVA | kVA: Channel 18 | AI505 | kVA | 1 | Instantaneous Apparent Power - Chan 18
19 | A | R |  | 1648 | 2876 | 2877 | 1060 | KVA | kVA: Channel 19 | AI506 | kVA | 1 | Instantaneous Apparent Power - Chan 19
20 | A | R |  | 1649 | 2878 | 2879 | 1061 | KVA | kVA: Channel 20 | AI507 | kVA | 1 | Instantaneous Apparent Power - Chan 20
21 | A | R |  | 1650 | 2880 | 2881 | 1062 | KVA | kVA: Channel 21 | AI508 | kVA | 1 | Instantaneous Apparent Power - Chan 21
22 | A | R |  | 1651 | 2882 | 2883 | 1063 | KVA | kVA: Channel 22 | AI509 | kVA | 1 | Instantaneous Apparent Power - Chan 22
23 | A | R |  | 1652 | 2884 | 2885 | 1064 | KVA | kVA: Channel 23 | AI510 | kVA | 1 | Instantaneous Apparent Power - Chan 23
24 | A | R |  | 1653 | 2886 | 2887 | 1065 | KVA | kVA: Channel 24 | AI511 | kVA | 1 | Instantaneous Apparent Power - Chan 24
25 | A | R |  | 1654 | 2888 | 2889 | 1066 | KVA | kVA: Channel 25 | AI512 | kVA | 1 | Instantaneous Apparent Power - Chan 25
26 | A | R |  | 1655 | 2890 | 2891 | 1067 | KVA | kVA: Channel 26 | AI513 | kVA | 1 | Instantaneous Apparent Power - Chan 26
27 | A | R |  | 1656 | 2892 | 2893 | 1068 | KVA | kVA: Channel 27 | AI514 | kVA | 1 | Instantaneous Apparent Power - Chan 27
28 | A | R |  | 1657 | 2894 | 2895 | 1069 | KVA | kVA: Channel 28 | AI515 | kVA | 1 | Instantaneous Apparent Power - Chan 28
29 | A | R |  | 1658 | 2896 | 2897 | 1070 | KVA | kVA: Channel 29 | AI516 | kVA | 1 | Instantaneous Apparent Power - Chan 29
30 | A | R |  | 1659 | 2898 | 2899 | 1071 | KVA | kVA: Channel 30 | AI517 | kVA | 1 | Instantaneous Apparent Power - Chan 30
31 | A | R |  | 1660 | 2900 | 2901 | 1072 | KVA | kVA: Channel 31 | AI518 | kVA | 1 | Instantaneous Apparent Power - Chan 31
32 | A | R |  | 1661 | 2902 | 2903 | 1073 | KVA | kVA: Channel 32 | AI519 | kVA | 1 | Instantaneous Apparent Power - Chan 32
33 | A | R |  | 1662 | 2904 | 2905 | 1074 | KVA | kVA: Channel 33 | AI520 | kVA | 1 | Instantaneous Apparent Power - Chan 33
34 | A | R |  | 1663 | 2906 | 2907 | 1075 | KVA | kVA: Channel 34 | AI521 | kVA | 1 | Instantaneous Apparent Power - Chan 34
35 | A | R |  | 1664 | 2908 | 2909 | 1076 | KVA | kVA: Channel 35 | AI522 | kVA | 1 | Instantaneous Apparent Power - Chan 35
36 | A | R |  | 1665 | 2910 | 2911 | 1077 | KVA | kVA: Channel 36 | AI523 | kVA | 1 | Instantaneous Apparent Power - Chan 36
37 | A | R |  | 1666 | 2912 | 2913 | 1078 | KVA | kVA: Channel 37 | AI524 | kVA | 1 | Instantaneous Apparent Power - Chan 37
38 | A | R |  | 1667 | 2914 | 2915 | 1079 | KVA | kVA: Channel 38 | AI525 | kVA | 1 | Instantaneous Apparent Power - Chan 38
39 | A | R |  | 1668 | 2916 | 2917 | 1080 | KVA | kVA: Channel 39 | AI526 | kVA | 1 | Instantaneous Apparent Power - Chan 39
40 | A | R |  | 1669 | 2918 | 2919 | 1081 | KVA | kVA: Channel 40 | AI527 | kVA | 1 | Instantaneous Apparent Power - Chan 40
41 | A | R |  | 1670 | 2920 | 2921 | 1082 | KVA | kVA: Channel 41 | AI528 | kVA | 1 | Instantaneous Apparent Power - Chan 41
42 | A | R |  | 1671 | 2922 | 2923 | 1083 | KVA | kVA: Channel 42 | AI529 | kVA | 1 | Instantaneous Apparent Power - Chan 42
1 | A | R |  | 1672 | 2924 | 2925 | -1 | Amperage Angle (selectable in User Defined Status Register - 62017)
2 | A | R |  | 1673 | 2926 | 2927 | -1 | Amperage Angle
3 | A | R |  | 1674 | 2928 | 2929 | -1 | Amperage Angle
4 | A | R |  | 1675 | 2930 | 2931 | -1 | Amperage Angle
5 | A | R |  | 1676 | 2932 | 2933 | -1 | Amperage Angle
6 | A | R |  | 1677 | 2934 | 2935 | -1 | Amperage Angle
7 | A | R |  | 1678 | 2936 | 2937 | -1 | Amperage Angle
8 | A | R |  | 1679 | 2938 | 2939 | -1 | Amperage Angle
9 | A | R |  | 1680 | 2940 | 2941 | -1 | Amperage Angle
10 | A | R |  | 1681 | 2942 | 2943 | -1 | Amperage Angle
11 | A | R |  | 1682 | 2944 | 2945 | -1 | Amperage Angle
12 | A | R |  | 1683 | 2946 | 2947 | -1 | Amperage Angle
13 | A | R |  | 1684 | 2948 | 2949 | -1 | Amperage Angle
14 | A | R |  | 1685 | 2950 | 2951 | -1 | Amperage Angle
15 | A | R |  | 1686 | 2952 | 2953 | -1 | Amperage Angle
16 | A | R |  | 1687 | 2954 | 2955 | -1 | Amperage Angle
17 | A | R |  | 1688 | 2956 | 2957 | -1 | Amperage Angle
18 | A | R |  | 1689 | 2958 | 2959 | -1 | Amperage Angle
19 | A | R |  | 1690 | 2960 | 2961 | -1 | Amperage Angle
20 | A | R |  | 1691 | 2962 | 2963 | -1 | Amperage Angle
21 | A | R |  | 1692 | 2964 | 2965 | -1 | Amperage Angle
22 | A | R |  | 1693 | 2966 | 2967 | -1 | Amperage Angle
23 | A | R |  | 1694 | 2968 | 2969 | -1 | Amperage Angle
24 | A | R |  | 1695 | 2970 | 2971 | -1 | Amperage Angle
25 | A | R |  | 1696 | 2972 | 2973 | -1 | Amperage Angle
26 | A | R |  | 1697 | 2974 | 2975 | -1 | Amperage Angle
27 | A | R |  | 1698 | 2976 | 2977 | -1 | Amperage Angle
28 | A | R |  | 1699 | 2978 | 2979 | -1 | Amperage Angle
29 | A | R |  | 1700 | 2980 | 2981 | -1 | Amperage Angle
30 | A | R |  | 1701 | 2982 | 2983 | -1 | Amperage Angle
31 | A | R |  | 1702 | 2984 | 2985 | -1 | Amperage Angle
32 | A | R |  | 1703 | 2986 | 2987 | -1 | Amperage Angle
33 | A | R |  | 1704 | 2988 | 2989 | -1 | Amperage Angle
34 | A | R |  | 1705 | 2990 | 2991 | -1 | Amperage Angle
35 | A | R |  | 1706 | 2992 | 2993 | -1 | Amperage Angle
36 | A | R |  | 1707 | 2994 | 2995 | -1 | Amperage Angle
37 | A | R |  | 1708 | 2996 | 2997 | -1 | Amperage Angle
38 | A | R |  | 1709 | 2998 | 2999 | -1 | Amperage Angle
39 | A | R |  | 1710 | 3000 | 3001 | -1 | Amperage Angle
40 | A | R |  | 1711 | 3002 | 3003 | -1 | Amperage Angle
41 | A | R |  | 1712 | 3004 | 3005 | -1 | Amperage Angle
42 | A | R |  | 1713 | 3006 | 3007 | -1 | Amperage Angle
1 | A | R |  | 1714 | 3008 | 3009 | 1084 | KWH Snapshot (MSW)
1 | A | R |  | 1715 |  |  |  | KWH Snapshot (LSW)
2 | A | R |  | 1716 | 3010 | 3011 | 1085 | KWH Snapshot (MSW)
2 | A | R |  | 1717 |  |  |  | KWH Snapshot (LSW)
3 | A | R |  | 1718 | 3012 | 3013 | 1086 | KWH Snapshot (MSW)
3 | A | R |  | 1719 |  |  |  | KWH Snapshot (LSW)
4 | A | R |  | 1720 | 3014 | 3015 | 1087 | KWH Snapshot (MSW)
4 | A | R |  | 1721 |  |  |  | KWH Snapshot (LSW)
5 | A | R |  | 1722 | 3016 | 3017 | 1088 | KWH Snapshot (MSW)
5 | A | R |  | 1723 |  |  |  | KWH Snapshot (LSW)
6 | A | R |  | 1724 | 3018 | 3019 | 1089 | KWH Snapshot (MSW)
6 | A | R |  | 1725 |  |  |  | KWH Snapshot (LSW)
7 | A | R |  | 1726 | 3020 | 3021 | 1090 | KWH Snapshot (MSW)
7 | A | R |  | 1727 |  |  |  | KWH Snapshot (LSW)
8 | A | R |  | 1728 | 3022 | 3023 | 1091 | KWH Snapshot (MSW)
8 | A | R |  | 1729 |  |  |  | KWH Snapshot (LSW)
9 | A | R |  | 1730 | 3024 | 3025 | 1092 | KWH Snapshot (MSW)
9 | A | R |  | 1731 |  |  |  | KWH Snapshot (LSW)
10 | A | R |  | 1732 | 3026 | 3027 | 1093 | KWH Snapshot (MSW)
10 | A | R |  | 1733 |  |  |  | KWH Snapshot (LSW)
11 | A | R |  | 1734 | 3028 | 3029 | 1094 | KWH Snapshot (MSW)
11 | A | R |  | 1735 |  |  |  | KWH Snapshot (LSW)
12 | A | R |  | 1736 | 3030 | 3031 | 1095 | KWH Snapshot (MSW)
12 | A | R |  | 1737 |  |  |  | KWH Snapshot (LSW)
13 | A | R |  | 1738 | 3032 | 3033 | 1096 | KWH Snapshot (MSW)
13 | A | R |  | 1739 |  |  |  | KWH Snapshot (LSW)
14 | A | R |  | 1740 | 3034 | 3035 | 1097 | KWH Snapshot (MSW)
14 | A | R |  | 1741 |  |  |  | KWH Snapshot (LSW)
15 | A | R |  | 1742 | 3036 | 3037 | 1098 | KWH Snapshot (MSW)
15 | A | R |  | 1743 |  |  |  | KWH Snapshot (LSW)
16 | A | R |  | 1744 | 3038 | 3039 | 1099 | KWH Snapshot (MSW)
16 | A | R |  | 1745 |  |  |  | KWH Snapshot (LSW)
17 | A | R |  | 1746 | 3040 | 3041 | 1100 | KWH Snapshot (MSW)
17 | A | R |  | 1747 |  |  |  | KWH Snapshot (LSW)
18 | A | R |  | 1748 | 3042 | 3043 | 1101 | KWH Snapshot (MSW)
18 | A | R |  | 1749 |  |  |  | KWH Snapshot (LSW)
19 | A | R |  | 1750 | 3044 | 3045 | 1102 | KWH Snapshot (MSW)
19 | A | R |  | 1751 |  |  |  | KWH Snapshot (LSW)
20 | A | R |  | 1752 | 3046 | 3047 | 1103 | KWH Snapshot (MSW)
20 | A | R |  | 1753 |  |  |  | KWH Snapshot (LSW)
21 | A | R |  | 1754 | 3048 | 3049 | 1104 | KWH Snapshot (MSW)
21 | A | R |  | 1755 |  |  |  | KWH Snapshot (LSW)
22 | A | R |  | 1756 | 3050 | 3051 | 1105 | KWH Snapshot (MSW)
22 | A | R |  | 1757 |  |  |  | KWH Snapshot (LSW)
23 | A | R |  | 1758 | 3052 | 3053 | 1106 | KWH Snapshot (MSW)
23 | A | R |  | 1759 |  |  |  | KWH Snapshot (LSW)
24 | A | R |  | 1760 | 3054 | 3055 | 1107 | KWH Snapshot (MSW)
24 | A | R |  | 1761 |  |  |  | KWH Snapshot (LSW)
25 | A | R |  | 1762 | 3056 | 3057 | 1108 | KWH Snapshot (MSW)
25 | A | R |  | 1763 |  |  |  | KWH Snapshot (LSW)
26 | A | R |  | 1764 | 3058 | 3059 | 1109 | KWH Snapshot (MSW)
26 | A | R |  | 1765 |  |  |  | KWH Snapshot (LSW)
27 | A | R |  | 1766 | 3060 | 3061 | 1110 | KWH Snapshot (MSW)
27 | A | R |  | 1767 |  |  |  | KWH Snapshot (LSW)
28 | A | R |  | 1768 | 3062 | 3063 | 1111 | KWH Snapshot (MSW)
28 | A | R |  | 1769 |  |  |  | KWH Snapshot (LSW)
29 | A | R |  | 1770 | 3064 | 3065 | 1112 | KWH Snapshot (MSW)
29 | A | R |  | 1771 |  |  |  | KWH Snapshot (LSW)
30 | A | R |  | 1772 | 3066 | 3067 | 1113 | KWH Snapshot (MSW)
30 | A | R |  | 1773 |  |  |  | KWH Snapshot (LSW)
31 | A | R |  | 1774 | 3068 | 3069 | 1114 | KWH Snapshot (MSW)
31 | A | R |  | 1775 |  |  |  | KWH Snapshot (LSW)
32 | A | R |  | 1776 | 3070 | 3071 | 1115 | KWH Snapshot (MSW)
32 | A | R |  | 1777 |  |  |  | KWH Snapshot (LSW)
33 | A | R |  | 1778 | 3072 | 3073 | 1116 | KWH Snapshot (MSW)
33 | A | R |  | 1779 |  |  |  | KWH Snapshot (LSW)
34 | A | R |  | 1780 | 3074 | 3075 | 1117 | KWH Snapshot (MSW)
34 | A | R |  | 1781 |  |  |  | KWH Snapshot (LSW)
35 | A | R |  | 1782 | 3076 | 3077 | 1118 | KWH Snapshot (MSW)
35 | A | R |  | 1783 |  |  |  | KWH Snapshot (LSW)
36 | A | R |  | 1784 | 3078 | 3079 | 1119 | KWH Snapshot (MSW)
36 | A | R |  | 1785 |  |  |  | KWH Snapshot (LSW)
37 | A | R |  | 1786 | 3080 | 3081 | 1120 | KWH Snapshot (MSW)
37 | A | R |  | 1787 |  |  |  | KWH Snapshot (LSW)
38 | A | R |  | 1788 | 3082 | 3083 | 1121 | KWH Snapshot (MSW)
38 | A | R |  | 1789 |  |  |  | KWH Snapshot (LSW)
39 | A | R |  | 1790 | 3084 | 3085 | 1122 | KWH Snapshot (MSW)
39 | A | R |  | 1791 |  |  |  | KWH Snapshot (LSW)
40 | A | R |  | 1792 | 3086 | 3087 | 1123 | KWH Snapshot (MSW)
40 | A | R |  | 1793 |  |  |  | KWH Snapshot (LSW)
41 | A | R |  | 1794 | 3088 | 3089 | 1124 | KWH Snapshot (MSW)
41 | A | R |  | 1795 |  |  |  | KWH Snapshot (LSW)
42 | A | R |  | 1796 | 3090 | 3091 | 1125 | KWH Snapshot (MSW)
42 | A | R |  | 1797 |  |  |  | KWH Snapshot (LSW)
total registers in this section
1806

## Logical Circuits Setup
SETUP OF LOGICAL CIRCUITS
Logical circuits are created by assigning the Logical circuit number to the CT channel in the Logicalible Circuit Assignment registers
Logical circuits, like physical breakers, are limited to 1, 2, or 3 CT channels that must be adjacent (rule applies to both solid-core and split-core)
Writing a 0 to a CT channel's Logical Assignment removes it from any Logical circuit
To keep from violating the adjacency rule, the middle CT channel can not be removed from a 3-phase logical circuit. Start by removing from either end.
Logical circuits can be assigned via block write
All channels should be unassigned before issuing a block write. This can be done with a the Global Clear Logical Circuits Assignment command.
Logical circuits can be numbered in any order
EXAMPLE LOGICAL CIRCUITS SETUPS
Logical Circuit Assignment - Example 1
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Top Feed
| 62069 | Branch Channel 2 | 22
| 62070 | Branch Channel 3 | 2 |  |  |  | Mains
| 62071 | Branch Channel 4 | 23
| 62072 | Branch Channel 5 | 3 |  |  | Aux 1
| 62073 | Branch Channel 6 | 24 |  |  | Aux 2 | ■□ | Logical Circuit 43
| 62074 | Branch Channel 7 | 4 |  |  | Aux 3
| 62075 | Branch Channel 8 | 25
| 62076 | Branch Channel 9 | 5 | CT 1 | Logical Circuit 1 | ■□ |  | □■ | Logical Circuit 22 | CT 2
| 62077 | Branch Channel 10 | 26 | CT 3 | Logical Circuit 2 | ■□ |  | □■ | Logical Circuit 23 | CT 4
| 62078 | Branch Channel 11 | 6 | CT 5 | Logical Circuit 3 | ■□ |  | □■ | Logical Circuit 24 | CT 6
| 62079 | Branch Channel 12 | 27 | CT 7 | Logical Circuit 4 | ■□ |  | □■ | Logical Circuit 25 | CT 8
| 62080 | Branch Channel 13 | 7 | CT 9 | Logical Circuit 5 | ■□ |  | □■ | Logical Circuit 26 | CT 10
| 62081 | Branch Channel 14 | 28 | CT 11 | Logical Circuit 6 | ■□ |  | □■ | Logical Circuit 27 | CT 12
| 62082 | Branch Channel 15 | 8 | CT 13 | Logical Circuit 7 | ■□ |  | □■ | Logical Circuit 28 | CT 14
| 62083 | Branch Channel 16 | 29 | CT 15 | Logical Circuit 8 | ■□ |  | □■ | Logical Circuit 29 | CT 16
| 62084 | Branch Channel 17 | 9 | CT 17 | Logical Circuit 9 | ■□ |  | □■ | Logical Circuit 30 | CT 18
| 62085 | Branch Channel 18 | 30 | CT 19 | Logical Circuit 10 | ■□ |  | □■ | Logical Circuit 31 | CT 20
| 62086 | Branch Channel 19 | 10 | CT 21 | Logical Circuit 11 | ■□ |  | □■ | Logical Circuit 32 | CT 22
| 62087 | Branch Channel 20 | 31 | CT 23 | Logical Circuit 12 | ■□ |  | □■ | Logical Circuit 33 | CT 24
| 62088 | Branch Channel 21 | 11 | CT 25 | Logical Circuit 13 | ■□ |  | □■ | Logical Circuit 34 | CT 26
| 62089 | Branch Channel 22 | 32 | CT 27 | Logical Circuit 14 | ■□ |  | □■ | Logical Circuit 35 | CT 28
| 62090 | Branch Channel 23 | 12 | CT 29 | Logical Circuit 15 | ■□ |  | □■ | Logical Circuit 36 | CT 30
| 62091 | Branch Channel 24 | 33 | CT 31 | Logical Circuit 16 | ■□ |  | □■ | Logical Circuit 37 | CT 32
| 62092 | Branch Channel 25 | 13 | CT 33 | Logical Circuit 17 | ■□ |  | □■ | Logical Circuit 38 | CT 34
| 62093 | Branch Channel 26 | 34 | CT 35 | Logical Circuit 18 | ■□ |  | □■ | Logical Circuit 39 | CT 36
| 62094 | Branch Channel 27 | 14 | CT 37 | Logical Circuit 19 | ■□ |  | □■ | Logical Circuit 40 | CT 38
| 62095 | Branch Channel 28 | 34 | CT 39 | Logical Circuit 20 | ■□ |  | □■ | Logical Circuit 41 | CT 40
| 62096 | Branch Channel 29 | 15 | CT 41 | Logical Circuit 21 | ■□ |  | □■ | Logical Circuit 42 | CT 42
| 62097 | Branch Channel 30 | 36
| 62098 | Branch Channel 31 | 16
| 62099 | Branch Channel 32 | 37
| 62100 | Branch Channel 33 | 17
| 62101 | Branch Channel 34 | 38
| 62102 | Branch Channel 35 | 18
| 62103 | Branch Channel 36 | 39
| 62104 | Branch Channel 37 | 19
| 62105 | Branch Channel 38 | 40
| 62106 | Branch Channel 39 | 20
| 62107 | Branch Channel 40 | 41
| 62108 | Branch Channel 41 | 21
| 62109 | Branch Channel 42 | 42
| 62110 | Aux Channel 1 | 43
| 62111 | Aux Channel 2 | 43
| 62112 | Aux Channel 3 | 43
| 62113 | Aux Channel 4 | 0
Logical Circuit Assignment - Example 2
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Top Feed
| 62069 | Branch Channel 2 | 2
| 62070 | Branch Channel 3 | 1 |  |  |  | Mains
| 62071 | Branch Channel 4 | 2
| 62072 | Branch Channel 5 | 1 |  |  | Aux 1 | ■□ | Logicalible Circuit 45
| 62073 | Branch Channel 6 | 2 |  |  | Aux 2
| 62074 | Branch Channel 7 | 3
| 62075 | Branch Channel 8 | 4
| 62076 | Branch Channel 9 | 3 | CT 1 |  | ■□ |  | □■ |  | CT 2
| 62077 | Branch Channel 10 | 4 | CT 3 | Logical Circuit 1 |  |  |  | Logical Circuit 2 | CT 4
| 62078 | Branch Channel 11 | 5 | CT 5 | [5 empty] | CT 6
| 62079 | Branch Channel 12 | 4 | CT 7 | Logical Circuit 3 | ■□ |  | □■ |  | CT 8
| 62080 | Branch Channel 13 | 7 | CT 9 |  |  |  |  | Logical Circuit 4 | CT 10
| 62081 | Branch Channel 14 | 6 | CT 11 | Logical Circuit 5 | ■□ |  |  |  | CT 12
| 62082 | Branch Channel 15 | 9 | CT 13 | Logical Circuit 7 | ■□ |  | □■ |  | CT 14
| 62083 | Branch Channel 16 | 6 | CT 15 | Logical Circuit 9 | ■□ |  |  | Logical Circuit 6 | CT 16
| 62084 | Branch Channel 17 | 11 | CT 17 | Logical Circuit 11 | ■□ |  |  |  | CT 18
| 62085 | Branch Channel 18 | 6 | CT 19 |  |  |  | □■ |  | CT 20
| 62086 | Branch Channel 19 | 11 | CT 21 | Logical Circuit 13 | ■□ |  |  | Logical Circuit 8 | CT 22
| 62087 | Branch Channel 20 | 8 | CT 23 | [5 empty] | CT 24
| 62088 | Branch Channel 21 | 13 | CT 25 | Logical Circuit 15 | ■□ |  | □■ |  | CT 26
| 62089 | Branch Channel 22 | 8 | CT 27 |  |  |  |  | Logical Circuit 10 | CT 28
| 62090 | Branch Channel 23 | 13 | CT 29 | Logical Circuit 17 | ■□ |  |  |  | CT 30
| 62091 | Branch Channel 24 | 8 | CT 31 | Logical Circuit 19 | ■□ |  | □■ |  | CT 32
| 62092 | Branch Channel 25 | 15 | CT 33 | Logical Circuit 21 | ■□ |  |  | Logical Circuit 12 | CT 34
| 62093 | Branch Channel 26 | 10 | CT 35 | Logical Circuit 23 | ■□ |  |  |  | CT 36
| 62094 | Branch Channel 27 | 15 | CT 37 | Logical Circuit 25 | ■□ |  | □■ |  | CT 38
| 62095 | Branch Channel 28 | 10 | CT 39 | Logical Circuit 27 | ■□ |  |  | Logical Circuit 14 | CT 40
| 62096 | Branch Channel 29 | 17 | CT 41 | Logical Circuit 29 | ■□ |  |  |  | CT 42
| 62097 | Branch Channel 30 | 10
| 62098 | Branch Channel 31 | 19
| 62099 | Branch Channel 32 | 12
| 62100 | Branch Channel 33 | 21
| 62101 | Branch Channel 34 | 12
| 62102 | Branch Channel 35 | 23
| 62103 | Branch Channel 36 | 12
| 62104 | Branch Channel 37 | 25
| 62105 | Branch Channel 38 | 14
| 62106 | Branch Channel 39 | 27
| 62107 | Branch Channel 40 | 14
| 62108 | Branch Channel 41 | 29
| 62109 | Branch Channel 42 | 14
| 62110 | Aux Channel 1 | 45
| 62111 | Aux Channel 2 | 45
| 62112 | Aux Channel 3 | 0
| 62113 | Aux Channel 4 | 0
Logical Circuit Assignment - Example 3
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Bottom Feed
| 62069 | Branch Channel 2 | 8
| 62070 | Branch Channel 3 | 1
| 62071 | Branch Channel 4 | 8
| 62072 | Branch Channel 5 | 1
| 62073 | Branch Channel 6 | 8
| 62074 | Branch Channel 7 | 2
| 62075 | Branch Channel 8 | 9
| 62076 | Branch Channel 9 | 2 | CT 1 |  | ■□ |  | □■ |  | CT 2
| 62077 | Branch Channel 10 | 9 | CT 3 | Logical Circuit 1 |  |  |  | Logical Circuit 8 | CT 4
| 62078 | Branch Channel 11 | 2 | CT 5 | [5 empty] | CT 6
| 62079 | Branch Channel 12 | 9 | CT 7 |  | ■□ |  | □■ |  | CT 8
| 62080 | Branch Channel 13 | 3 | CT 9 | Logical Circuit 2 |  |  |  | Logical Circuit 9 | CT 10
| 62081 | Branch Channel 14 | 10 | CT 11 | [5 empty] | CT 12
| 62082 | Branch Channel 15 | 3 | CT 13 |  | ■□ |  | □■ |  | CT 14
| 62083 | Branch Channel 16 | 10 | CT 15 | Logical Circuit 3 |  |  |  | Logical Circuit 10 | CT 16
| 62084 | Branch Channel 17 | 3 | CT 17 | [5 empty] | CT 18
| 62085 | Branch Channel 18 | 10 | CT 19 |  | ■□ |  | □■ |  | CT 20
| 62086 | Branch Channel 19 | 4 | CT 21 | Logical Circuit 4 |  |  |  | Logical Circuit 11 | CT 22
| 62087 | Branch Channel 20 | 11 | CT 23 | [5 empty] | CT 24
| 62088 | Branch Channel 21 | 4 | CT 25 |  | ■□ |  | □■ |  | CT 26
| 62089 | Branch Channel 22 | 11 | CT 27 | Logical Circuit 5 |  |  |  | Logical Circuit 12 | CT 28
| 62090 | Branch Channel 23 | 4 | CT 29 | [5 empty] | CT 30
| 62091 | Branch Channel 24 | 11 | CT 31 |  | ■□ |  | □■ |  | CT 32
| 62092 | Branch Channel 25 | 5 | CT 33 | Logical Circuit 6 |  |  |  | Logical Circuit 13 | CT 34
| 62093 | Branch Channel 26 | 12 | CT 35 | [5 empty] | CT 36
| 62094 | Branch Channel 27 | 5 | CT 37 |  | ■□ |  | □■ |  | CT 38
| 62095 | Branch Channel 28 | 12 | CT 39 | Logical Circuit 7 |  |  |  | Logical Circuit 14 | CT 40
| 62096 | Branch Channel 29 | 5 | CT 41 | [5 empty] | CT 42
| 62097 | Branch Channel 30 | 12
| 62098 | Branch Channel 31 | 6 |  |  | Aux 1
| 62099 | Branch Channel 32 | 13 |  |  | Aux 2 | ■□ | Logical Circuit 15
| 62100 | Branch Channel 33 | 6 |  |  | Aux 3
| 62101 | Branch Channel 34 | 13
| 62102 | Branch Channel 35 | 6 |  |  |  | Mains
| 62103 | Branch Channel 36 | 13
| 62104 | Branch Channel 37 | 7
| 62105 | Branch Channel 38 | 14
| 62106 | Branch Channel 39 | 7
| 62107 | Branch Channel 40 | 14
| 62108 | Branch Channel 41 | 7
| 62109 | Branch Channel 42 | 14
| 62110 | Aux Channel 1 | 15
| 62111 | Aux Channel 2 | 15
| 62112 | Aux Channel 3 | 15
| 62113 | Aux Channel 4 | 0
Logical Circuit Assignment - Example 4
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Bottom Feed
| 62069 | Branch Channel 2 | 2
| 62070 | Branch Channel 3 | 3
| 62071 | Branch Channel 4 | 2
| 62072 | Branch Channel 5 | 5
| 62073 | Branch Channel 6 | 6
| 62074 | Branch Channel 7 | 7
| 62075 | Branch Channel 8 | 6
| 62076 | Branch Channel 9 | 9 | CT 1 | Logical Circuit 1 | ■□ |  | □■ | Logical Circuit 2 | CT 2
| 62077 | Branch Channel 10 | 10 | CT 3 | Logical Circuit 3 | ■□ |  |  |  | CT 4
| 62078 | Branch Channel 11 | 11 | CT 5 | Logical Circuit 5 | ■□ |  | □■ | Logical Circuit 6 | CT 6
| 62079 | Branch Channel 12 | 10 | CT 7 | Logical Circuit 7 | ■□ |  |  |  | CT 8
| 62080 | Branch Channel 13 | 13 | CT 9 | Logical Circuit 9 | ■□ |  | □■ | Logical Circuit 10 | CT 10
| 62081 | Branch Channel 14 | 14 | CT 11 | Logical Circuit 11 | ■□ |  |  |  | CT 12
| 62082 | Branch Channel 15 | 15 | CT 13 | Logical Circuit 13 | ■□ |  | □■ | Logical Circuit 14 | CT 14
| 62083 | Branch Channel 16 | 14 | CT 15 | Logical Circuit 15 | ■□ |  |  |  | CT 16
| 62084 | Branch Channel 17 | 17 | CT 17 | Logical Circuit 17 | ■□ |  | □■ | Logical Circuit 18 | CT 18
| 62085 | Branch Channel 18 | 18 | CT 19 | Logical Circuit 19 | ■□ |  |  |  | CT 20
| 62086 | Branch Channel 19 | 19 | CT 21 | Logical Circuit 21 | ■□ |  | □■ | Logical Circuit 22 | CT 22
| 62087 | Branch Channel 20 | 18 | CT 23 | Logical Circuit 23 | ■□ |  |  |  | CT 24
| 62088 | Branch Channel 21 | 21 | CT 25 | Logical Circuit 25 | ■□ |  | □■ | Logical Circuit 26 | CT 26
| 62089 | Branch Channel 22 | 22 | CT 27 | Logical Circuit 27 | ■□ |  |  |  | CT 28
| 62090 | Branch Channel 23 | 23 | CT 29 | Logical Circuit 29 | ■□ |  | □■ | Logical Circuit 30 | CT 30
| 62091 | Branch Channel 24 | 22 | CT 31 | Logical Circuit 31 | ■□ |  |  |  | CT 32
| 62092 | Branch Channel 25 | 25 | CT 33 | Logical Circuit 33 | ■□ |  | □■ | Logical Circuit 34 | CT 34
| 62093 | Branch Channel 26 | 26 | CT 35 | Logical Circuit 35 | ■□ |  |  |  | CT 36
| 62094 | Branch Channel 27 | 27 | CT 37 | Logical Circuit 37 | ■□ |  | □■ | Logical Circuit 38 | CT 38
| 62095 | Branch Channel 28 | 26 | CT 39 | Logical Circuit 39 | ■□ |  |  |  | CT 40
| 62096 | Branch Channel 29 | 29 | CT 41 | Logical Circuit 41 | ■□ |  | □■ | Logical Circuit 42 | CT 42
| 62097 | Branch Channel 30 | 30
| 62098 | Branch Channel 31 | 31 |  |  | Aux 1
| 62099 | Branch Channel 32 | 30 |  |  | Aux 2 | ■□ | Logical Circuit 43
| 62100 | Branch Channel 33 | 33 |  |  | Aux 3
| 62101 | Branch Channel 34 | 34
| 62102 | Branch Channel 35 | 35 |  |  |  | Mains
| 62103 | Branch Channel 36 | 34
| 62104 | Branch Channel 37 | 37
| 62105 | Branch Channel 38 | 38
| 62106 | Branch Channel 39 | 39
| 62107 | Branch Channel 40 | 38
| 62108 | Branch Channel 41 | 41
| 62109 | Branch Channel 42 | 42
| 62110 | Aux Channel 1 | 43
| 62111 | Aux Channel 2 | 43
| 62112 | Aux Channel 3 | 43
| 62113 | Aux Channel 4 | 0
Logical Circuit Assignment - Example 5
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Single Row
| 62069 | Branch Channel 2 | 1
| 62070 | Branch Channel 3 | 2 |  |  |  | Mains
| 62071 | Branch Channel 4 | 2
| 62072 | Branch Channel 5 | 3 |  |  | Aux 1
| 62073 | Branch Channel 6 | 3 |  |  | Aux 2 | ■□ | Logical Circuit 22
| 62074 | Branch Channel 7 | 4 |  |  | Aux 3
| 62075 | Branch Channel 8 | 4
| 62076 | Branch Channel 9 | 5 | CT 1 | Logical Circuit 1 | ■□
| 62077 | Branch Channel 10 | 5 | CT 2
| 62078 | Branch Channel 11 | 6 | CT 3 | Logical Circuit 2 | ■□
| 62079 | Branch Channel 12 | 6 | CT 4
| 62080 | Branch Channel 13 | 7 | CT 5 | Logical Circuit 3 | ■□
| 62081 | Branch Channel 14 | 7 | CT 6
| 62082 | Branch Channel 15 | 8 | CT 7 | Logical Circuit 4 | ■□
| 62083 | Branch Channel 16 | 8 | CT 8
| 62084 | Branch Channel 17 | 9 | CT 9 | Logical Circuit 5 | ■□
| 62085 | Branch Channel 18 | 9 | CT 10
| 62086 | Branch Channel 19 | 10 | CT 11 | Logical Circuit 6 | ■□
| 62087 | Branch Channel 20 | 10 | CT 12
| 62088 | Branch Channel 21 | 11 | CT 13 | Logical Circuit 7 | ■□
| 62089 | Branch Channel 22 | 11 | CT 14
| 62090 | Branch Channel 23 | 12 | CT 15 | Logical Circuit 8 | ■□
| 62091 | Branch Channel 24 | 12 | CT 16
| 62092 | Branch Channel 25 | 13 | CT 17 | Logical Circuit 9 | ■□
| 62093 | Branch Channel 26 | 13 | CT 18
| 62094 | Branch Channel 27 | 14 | CT 19 | Logical Circuit 10 | ■□
| 62095 | Branch Channel 28 | 14 | CT 20
| 62096 | Branch Channel 29 | 15 | CT 21 | Logical Circuit 11 | ■□
| 62097 | Branch Channel 30 | 15 | CT 22
| 62098 | Branch Channel 31 | 16 | CT 23 | Logical Circuit 12 | ■□
| 62099 | Branch Channel 32 | 16 | CT 24
| 62100 | Branch Channel 33 | 17 | CT 25 | Logical Circuit 13 | ■□
| 62101 | Branch Channel 34 | 17 | CT 26
| 62102 | Branch Channel 35 | 18 | CT 27 | Logical Circuit 14 | ■□
| 62103 | Branch Channel 36 | 18 | CT 28
| 62104 | Branch Channel 37 | 19 | CT 29 | Logical Circuit 15 | ■□
| 62105 | Branch Channel 38 | 19 | CT 30
| 62106 | Branch Channel 39 | 20 | CT 31 | Logical Circuit 16 | ■□
| 62107 | Branch Channel 40 | 20 | CT 32
| 62108 | Branch Channel 41 | 21 | CT 33 | Logical Circuit 17 | ■□
| 62109 | Branch Channel 42 | 21 | CT 34
| 62110 | Aux Channel 1 | 22 | CT 35 | Logical Circuit 18 | ■□
| 62111 | Aux Channel 2 | 22 | CT 36
| 62112 | Aux Channel 3 | 22 | CT 37 | Logical Circuit 19 | ■□
| 62113 | Aux Channel 4 | 0 | CT 38
|  |  |  | CT 39 | Logical Circuit 20 | ■□
CT 40
|  |  |  | CT 41 | Logical Circuit 21 | ■□
CT 42
Logical Circuit Assignment - Example 6
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Single Row
| 62069 | Branch Channel 2 | 2
| 62070 | Branch Channel 3 | 3 |  |  |  | Mains
| 62071 | Branch Channel 4 | 4
| 62072 | Branch Channel 5 | 5 |  |  | Aux 1
| 62073 | Branch Channel 6 | 6 |  |  | Aux 2 | ■□ | Logical Circuit 43
| 62074 | Branch Channel 7 | 7 |  |  | Aux 3
| 62075 | Branch Channel 8 | 8
| 62076 | Branch Channel 9 | 9 | CT 1 | Logical Circuit 1 | ■□
| 62077 | Branch Channel 10 | 10 | CT 2 | Logical Circuit 2 | ■□
| 62078 | Branch Channel 11 | 11 | CT 3 | Logical Circuit 3 | ■□
| 62079 | Branch Channel 12 | 12 | CT 4 | Logical Circuit 4 | ■□
| 62080 | Branch Channel 13 | 13 | CT 5 | Logical Circuit 5 | ■□
| 62081 | Branch Channel 14 | 14 | CT 6 | Logical Circuit 6 | ■□
| 62082 | Branch Channel 15 | 15 | CT 7 | Logical Circuit 7 | ■□
| 62083 | Branch Channel 16 | 16 | CT 8 | Logical Circuit 8 | ■□
| 62084 | Branch Channel 17 | 17 | CT 9 | Logical Circuit 9 | ■□
| 62085 | Branch Channel 18 | 18 | CT 10 | Logical Circuit 10 | ■□
| 62086 | Branch Channel 19 | 19 | CT 11 | Logical Circuit 11 | ■□
| 62087 | Branch Channel 20 | 20 | CT 12 | Logical Circuit 12 | ■□
| 62088 | Branch Channel 21 | 21 | CT 13 | Logical Circuit 13 | ■□
| 62089 | Branch Channel 22 | 22 | CT 14 | Logical Circuit 14 | ■□
| 62090 | Branch Channel 23 | 23 | CT 15 | Logical Circuit 15 | ■□
| 62091 | Branch Channel 24 | 24 | CT 16 | Logical Circuit 16 | ■□
| 62092 | Branch Channel 25 | 25 | CT 17 | Logical Circuit 17 | ■□
| 62093 | Branch Channel 26 | 26 | CT 18 | Logical Circuit 18 | ■□
| 62094 | Branch Channel 27 | 27 | CT 19 | Logical Circuit 19 | ■□
| 62095 | Branch Channel 28 | 28 | CT 20 | Logical Circuit 20 | ■□
| 62096 | Branch Channel 29 | 29 | CT 21 | Logical Circuit 21 | ■□
| 62097 | Branch Channel 30 | 30 | CT 22 | Logical Circuit 1 | ■□
| 62098 | Branch Channel 31 | 31 | CT 23 | Logical Circuit 2 | ■□
| 62099 | Branch Channel 32 | 32 | CT 24 | Logical Circuit 3 | ■□
| 62100 | Branch Channel 33 | 33 | CT 25 | Logical Circuit 4 | ■□
| 62101 | Branch Channel 34 | 34 | CT 26 | Logical Circuit 5 | ■□
| 62102 | Branch Channel 35 | 35 | CT 27 | Logical Circuit 6 | ■□
| 62103 | Branch Channel 36 | 36 | CT 28 | Logical Circuit 7 | ■□
| 62104 | Branch Channel 37 | 37 | CT 29 | Logical Circuit 8 | ■□
| 62105 | Branch Channel 38 | 38 | CT 30 | Logical Circuit 9 | ■□
| 62106 | Branch Channel 39 | 39 | CT 31 | Logical Circuit 10 | ■□
| 62107 | Branch Channel 40 | 40 | CT 32 | Logical Circuit 11 | ■□
| 62108 | Branch Channel 41 | 41 | CT 33 | Logical Circuit 12 | ■□
| 62109 | Branch Channel 42 | 42 | CT 34 | Logical Circuit 13 | ■□
| 62110 | Aux Channel 1 | 43 | CT 35 | Logical Circuit 14 | ■□
| 62111 | Aux Channel 2 | 43 | CT 36 | Logical Circuit 15 | ■□
| 62112 | Aux Channel 3 | 43 | CT 37 | Logical Circuit 16 | ■□
| 62113 | Aux Channel 4 | 0 | CT 38 | Logical Circuit 17 | ■□
|  |  |  | CT 39 | Logical Circuit 18 | ■□
|  |  |  | CT 40 | Logical Circuit 19 | ■□
|  |  |  | CT 41 | Logical Circuit 20 | ■□
|  |  |  | CT 42 | Logical Circuit 21 | ■□
Logical Circuit Assignment - Example 7
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Odd/Even
| 62069 | Branch Channel 2 | 22
| 62070 | Branch Channel 3 | 2 |  |  |  | Mains
| 62071 | Branch Channel 4 | 23
| 62072 | Branch Channel 5 | 3 |  |  | Aux 1
| 62073 | Branch Channel 6 | 24 |  |  | Aux 2 | ■□ | Logical Circuit 43
| 62074 | Branch Channel 7 | 4 |  |  | Aux 3
| 62075 | Branch Channel 8 | 25
| 62076 | Branch Channel 9 | 5 | CT 1 | Logical Circuit 1 | ■□
| 62077 | Branch Channel 10 | 26 | CT 3 | Logical Circuit 2 | ■□
| 62078 | Branch Channel 11 | 6 | CT 5 | Logical Circuit 3 | ■□
| 62079 | Branch Channel 12 | 27 | CT 7 | Logical Circuit 4 | ■□
| 62080 | Branch Channel 13 | 7 | CT 9 | Logical Circuit 5 | ■□
| 62081 | Branch Channel 14 | 28 | CT 11 | Logical Circuit 6 | ■□
| 62082 | Branch Channel 15 | 8 | CT 13 | Logical Circuit 7 | ■□
| 62083 | Branch Channel 16 | 29 | CT 15 | Logical Circuit 8 | ■□
| 62084 | Branch Channel 17 | 9 | CT 17 | Logical Circuit 9 | ■□
| 62085 | Branch Channel 18 | 30 | CT 19 | Logical Circuit 10 | ■□
| 62086 | Branch Channel 19 | 10 | CT 21 | Logical Circuit 11 | ■□
| 62087 | Branch Channel 20 | 31 | CT 23 | Logical Circuit 12 | ■□
| 62088 | Branch Channel 21 | 11 | CT 25 | Logical Circuit 13 | ■□
| 62089 | Branch Channel 22 | 32 | CT 27 | Logical Circuit 14 | ■□
| 62090 | Branch Channel 23 | 12 | CT 29 | Logical Circuit 15 | ■□
| 62091 | Branch Channel 24 | 33 | CT 31 | Logical Circuit 16 | ■□
| 62092 | Branch Channel 25 | 13 | CT 33 | Logical Circuit 17 | ■□
| 62093 | Branch Channel 26 | 34 | CT 35 | Logical Circuit 18 | ■□
| 62094 | Branch Channel 27 | 14 | CT 37 | Logical Circuit 19 | ■□
| 62095 | Branch Channel 28 | 34 | CT 39 | Logical Circuit 20 | ■□
| 62096 | Branch Channel 29 | 15 | CT 41 | Logical Circuit 21 | ■□
| 62097 | Branch Channel 30 | 36 | CT 2 | Logical Circuit 22 | ■□
| 62098 | Branch Channel 31 | 16 | CT 4 | Logical Circuit 23 | ■□
| 62099 | Branch Channel 32 | 37 | CT 6 | Logical Circuit 24 | ■□
| 62100 | Branch Channel 33 | 17 | CT 8 | Logical Circuit 25 | ■□
| 62101 | Branch Channel 34 | 38 | CT 10 | Logical Circuit 26 | ■□
| 62102 | Branch Channel 35 | 18 | CT 12 | Logical Circuit 27 | ■□
| 62103 | Branch Channel 36 | 39 | CT 14 | Logical Circuit 28 | ■□
| 62104 | Branch Channel 37 | 19 | CT 16 | Logical Circuit 29 | ■□
| 62105 | Branch Channel 38 | 40 | CT 18 | Logical Circuit 30 | ■□
| 62106 | Branch Channel 39 | 20 | CT 20 | Logical Circuit 31 | ■□
| 62107 | Branch Channel 40 | 41 | CT 22 | Logical Circuit 32 | ■□
| 62108 | Branch Channel 41 | 21 | CT 24 | Logical Circuit 33 | ■□
| 62109 | Branch Channel 42 | 42 | CT 26 | Logical Circuit 34 | ■□
| 62110 | Aux Channel 1 | 43 | CT 28 | Logical Circuit 35 | ■□
| 62111 | Aux Channel 2 | 43 | CT 30 | Logical Circuit 36 | ■□
| 62112 | Aux Channel 3 | 43 | CT 32 | Logical Circuit 37 | ■□
| 62113 | Aux Channel 4 | 0 | CT 34 | Logical Circuit 38 | ■□
|  |  |  | CT 36 | Logical Circuit 39 | ■□
|  |  |  | CT 38 | Logical Circuit 40 | ■□
|  |  |  | CT 40 | Logical Circuit 41 | ■□
|  |  |  | CT 42 | Logical Circuit 42 | ■□
Logical Circuit Assignment - Example 8
| reg. | CT channel | Value (Logical Circuit)
| 62068 | Branch Channel 1 | 1 |  |  |  | Odd/Even
| 62069 | Branch Channel 2 | 15
| 62070 | Branch Channel 3 | 1 |  |  |  | Mains
| 62071 | Branch Channel 4 | 15
| 62072 | Branch Channel 5 | 3 |  |  | Aux 1
| 62073 | Branch Channel 6 | 2 |  |  | Aux 2 | ■□ | Logical Circuit 16
| 62074 | Branch Channel 7 | 3 |  |  | Aux 3
| 62075 | Branch Channel 8 | 2
| 62076 | Branch Channel 9 | 3 | CT 1 | Logical Circuit 1 | ■□
| 62077 | Branch Channel 10 | 2 | CT 3
| 62078 | Branch Channel 11 | 5 | CT 5 |  | ■□
| 62079 | Branch Channel 12 | 4 | CT 7 | Logical Circuit 3
| 62080 | Branch Channel 13 | 5 | CT 9
| 62081 | Branch Channel 14 | 4 | CT 11 |  | ■□
| 62082 | Branch Channel 15 | 5 | CT 13 | Logical Circuit 5
| 62083 | Branch Channel 16 | 4 | CT 15
| 62084 | Branch Channel 17 | 7 | CT 17 |  | ■□
| 62085 | Branch Channel 18 | 6 | CT 19 | Logical Circuit 7
| 62086 | Branch Channel 19 | 7 | CT 21
| 62087 | Branch Channel 20 | 6 | CT 23 |  | ■□
| 62088 | Branch Channel 21 | 7 | CT 25 | Logical Circuit 9
| 62089 | Branch Channel 22 | 6 | CT 27
| 62090 | Branch Channel 23 | 9 | CT 29 |  | ■□
| 62091 | Branch Channel 24 | 8 | CT 31 | Logical Circuit 11
| 62092 | Branch Channel 25 | 9 | CT 33
| 62093 | Branch Channel 26 | 8 | CT 35 |  | ■□
| 62094 | Branch Channel 27 | 9 | CT 37 | Logical Circuit 13
| 62095 | Branch Channel 28 | 8 | CT 39
| 62096 | Branch Channel 29 | 11 | CT 41 |  | ■□
| 62097 | Branch Channel 30 | 10 | CT 2 | Logical Circuit 15
| 62098 | Branch Channel 31 | 11 | CT 4
| 62099 | Branch Channel 32 | 10 | CT 6 |  | ■□
| 62100 | Branch Channel 33 | 11 | CT 8 | Logical Circuit 2
| 62101 | Branch Channel 34 | 10 | CT 10
| 62102 | Branch Channel 35 | 13 | CT 12 |  | ■□
| 62103 | Branch Channel 36 | 12 | CT 14 | Logical Circuit 4
| 62104 | Branch Channel 37 | 13 | CT 16
| 62105 | Branch Channel 38 | 12 | CT 18 |  | ■□
| 62106 | Branch Channel 39 | 13 | CT 20 | Logical Circuit 6
| 62107 | Branch Channel 40 | 12 | CT 22
| 62108 | Branch Channel 41 | 15 | CT 24 |  | ■□
| 62109 | Branch Channel 42 | 14 | CT 26 | Logical Circuit 8
| 62110 | Aux Channel 1 | 16 | CT 28
| 62111 | Aux Channel 2 | 16 | CT 30 |  | ■□
| 62112 | Aux Channel 3 | 16 | CT 32 | Logical Circuit 10
| 62113 | Aux Channel 4 | 0 | CT 34
|  |  |  | CT 36 |  | ■□
|  |  |  | CT 38 | Logical Circuit 12
CT 40
|  |  |  | CT 42 | Logical Circuit 14 | ■□

## Logical Map by Circuit
[8 empty] | Modbus |  |  |  |  | BACnet
Channel | Model (A,B,C) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description | Object Name | Object ID | Units | COV Increment | BACnet Description | Range | Default
Panel & Branch Assignment
BACnet objets are incremented by 1 to get to the next Logical Circuit, Object ID listed is base value for Circuit #1
Logical Circuits are changed by incrementing by 1000, i.e. 10xxx is Circuit #1, 11xxx is Circuit #2, 12xxx is Circuit #3 etc.
| A,B,C | R | NV | 10001 |  |  |  | Number of Channels | Number of Channels Logical Circuit 1 | AI582 | No-Units | 0 | Number of Channels Assigned to Logical Circuit 1 | 0-3
1 | A,B,C | R | NV | 10002 |  |  |  | Panel & Channel | Logical Ckt 1: Phase 1 - Panel & Chan | AI628 | No-Units | 0 | 257-302=pnl1(1-46);512-558=pnl2;0=n/u | 0-2, 0-46
2 | A,B,C | R | NV | 10003 |  |  |  | Panel & Channel | Logical Ckt 1: Phase 2 - Panel & Chan | AI674 | No-Units | 0 | 257-302=pnl1(1-46);512-558=pnl2;0=n/u | 0-2, 0-46
3 | A,B,C | R | NV | 10004 |  |  |  | Panel & Channel | Logical Ckt 1: Phase 3 - Panel & Chan | AI720 | No-Units | 0 | 257-302=pnl1(1-46);512-558=pnl2;0=n/u | 0-2, 0-46
Circuits Inputs - Total
Total | A,B | R | NV | 10005 | 10101 | 10102 | 10049 | Total KWh (MSW) | kWh Logical Circuit 1 | AI766 | kWh | 1 | Real Energy - Circuit 1
Total | A,B | R | NV | 10006 |  |  |  | Total KWh (LSW)
Total | A,B | R |  | 10013 | 10109 | 10110 | 10051 | Total KW | kW Logical Circuit 1 | AI812 | kW | 1 | Instantaneous Real Power - Circuit 1
Total | A,B | R |  | 10015 | 10113 | 10114 | 10051 | Total KVA | kVA Logical Circuit 1 | AI858 | kVA | 1 | Instantaneous Apparent Power - Ckt 1
Total | A,B | R |  | 10016 | 10115 | 10116 | -3 | Total PF | Power Factor Logical Circuit 1 | AI904 | No-Units | 5 | Instantaneous Power Factor - Ckt 1 | 0.0 - 1.0
Total | A,B,C | R |  | 10018 | 10119 | 10120 | 10052 | Average Current | Amps (Average) Logical Circuit 1 | AI950 | Amperes | 5 | Instantaneous Current - Circuit 1
Total | A,B | R |  | 10019 | 10121 | 10122 | 10051 | Present KW Demand | kW Present Demand Logical Circuit 1 | AI996 | kW | 1 | Present Real Power Demand - Ckt 1
Total | A,B,C | R |  | 10022 | 10127 | 10128 | 10052 | Present Current Demand
Total | A,B | R | NV | 10023 | 10129 | 10130 | 10051 | Max KW Demand | kW Max Demand Logical Circuit 1 | AI1042 | kW | 1 | Max Real Power Demand - Circuit 1
Total | A,B,C | R |  | 10026 | 10135 | 10136 | 10052 | Max Current Demand
Total | A,B | R | NV | 10027 | 10137 | 10138 | 10051 | Max KW | kW Max Logical Circuit 1 | AI1088 | kW | 1 | Max Instantaneous Real Power - Ckt 1
Total | A,B,C | R |  | 10030 | 10143 | 10144 | 10052 | Max Current
Total | A,B | R |  | 10031 | 10145 | 10146 | 10053 | Voltage, L-L, Average of 3 Phases
Total | A,B | R |  | 10032 | 10147 | 10148 | 10053 | Voltage, L-N, Average of 3 Phases
Total | A,B | R |  | 10033 | 10149 | 10150 | -2 | Frequency (derived from Phase A) | [5 empty] | 40-70
Total | A,B | R | NV | 10037 | 10157 | 10158 | 10049 | Snapshot KWh (MSW) | kWh Snapshot Logical Circuit 1 | AI1134 | kWh | 0 | Energy Snapshot Logical Circuit 1
Total | A,B | R | NV | 10038 |  |  |  | Snapshot KWh (LSW)
Total | A,B | R | NV | 10049 |  |  |  | Energy Scale
Total | A,B | R | NV | 10051 |  |  |  | Power Scale
Total | A,B,C | R | NV | 10052 |  |  |  | Current Scale
Total | A,B | R | NV | 10053 |  |  |  | Voltage Scale Register
Circuit Resets
All | A,B,C | W |  | 10057 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset:
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps)
All | A,B,C | R/W | NV | 10058 |  |  |  | Circuit CT Size | [5 empty] | 0-32767 | 100
Breaker Sizes (Amps)
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
All | A,B,C | R/W | NV | 10059 |  |  |  | Circuit Breaker Size | [5 empty] | 0-32767 | 20
Circuit Alarm Status
All | A,B,C | R/W | NV | 10060 |  |  |  | Circuit Latching Alarm Status | Latching Alarm Status: Logical Meter 1 | AV255 | No-Units | 0 | Write 0 to alarm bits to clear alarms
Latching Alarms are cleared by writing a 0 to its alarm bit
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
All | A,B,C | R |  | 10061 |  |  |  | Circuit Non-Latching Alarm Status | Non-Latching Alarm Logical Circuit 1 | AI536 | No-Units | 0 | Status Bitmap
Bit 0: Reserved for High High Non-Latching Alarm (reads 0)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Panel & Branch Assignment - Phase 1
1 | A,B,C | R | NV | 10204 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 1
1 | A,B | R | NV | 10205 | 10301 | 10302 | 10249 | KWh (MSW)
1 | A,B | R | NV | 10206 |  |  |  | KWh (LSW)
1 | A,B | R |  | 10213 | 10309 | 10310 | 10251 | KW
1 | A,B | R |  | 10215 | 10313 | 10314 | 10251 | KVA
1 | A,B | R |  | 10216 | 10315 | 10316 | -3 | PF | [5 empty] | 0.0 - 1.0
1 | A,B |  |  | 10217 | 10317 | 10318 | -1 | Current Angle
1 | A,B,C | R |  | 10218 | 10319 | 10320 | 10252 | Current
1 | A,B | R |  | 10219 | 10321 | 10322 | 10251 | Present KW Demand
Total | A,B,C | R |  | 10222 | 10327 | 10328 | 10252 | Present Current Demand
Total | A,B | R | NV | 10223 | 10329 | 10330 | 10251 | Max KW Demand
Total | A,B,C | R | NV | 10226 | 10335 | 10336 | 10252 | Max Current Demand
1 | A,B | R | NV | 10227 | 10337 | 10338 | 10251 | Max KW
1 | A,B,C | R | NV | 10230 | 10343 | 10344 | 10252 | Max Current
1 | A,B | R |  | 10231 | 10345 | 10346 | 10253 | Voltage, L-L
1 | A,B | R |  | 10232 | 10347 | 10348 | 10253 | Voltage, L-N
1 | A,B | R |  | 10233 | 10349 | 10350 | -2 | Frequency (derived from Phase A) | [5 empty] | 40-70
1 | A,B | R |  | 10237 | 10357 | 10358 | 10249 | KWh Snapshot (MSW)
1 | A,B | R |  | 10238 |  |  |  | KWh Snapshot (LSW)
1 | A,B | R | NV | 10249 |  |  |  | Energy Scale
1 | A,B | R | NV | 10251 |  |  |  | Power Scale
1 | A,B,C | R | NV | 10252 |  |  |  | Current Scale
1 | A,B | R | NV | 10253 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 1
1 | A,B,C | W |  | 10257 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset:
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 1
All | A,B,C | R/W | NV | 10258 |  |  |  | Circuit CT Size | [5 empty] | 0-32767 | 100
Breaker Sizes (Amps) - Phase 1
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
1 | A,B,C | R/W | NV | 10259 |  |  |  | Chanel Breaker Size | [5 empty] | 0-32767 | 20
Circuit Alarm Status - Phase 1
1 | A,B,C | R/W | NV | 10260 |  |  |  | Channel Latching Alarm Status
Latching Alarms are cleared by writing a 0 to its alarm bit
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
1 | A,B,C | R |  | 10261 |  |  |  | Channel Non-Latching Alarm Status
Bit 0: Reserved for High High Non-Latching Alarm (reads 0)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 1
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
1 | A,B,C | R |  | 10262 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 10263 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 10264 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 10265 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | A,B,C | R |  | 10266 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
Panel & Branch Assignment - Phase 2
1 | A,B,C | R | NV | 10404 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 2
2 | A,B | R | NV | 10405 | 10501 | 10502 | 10449 | KWh (MSW)
2 | A,B | R | NV | 10406 |  |  |  | KWh (LSW)
2 | A,B | R |  | 10413 | 10509 | 10510 | 10451 | KW
2 | A,B | R |  | 10415 | 10513 | 10514 | 10451 | KVA
2 | A,B | R |  | 10416 | 10515 | 10516 | -3 | PF | [5 empty] | 0.0 - 1.0
2 | A,B |  |  | 10417 | 10517 | 10518 | -1 | Current Angle
2 | A,B,C | R |  | 10418 | 10519 | 10520 | 10452 | Current
2 | A,B | R |  | 10419 | 10521 | 10522 | 10451 | Present KW Demand
Total | A,B,C | R |  | 10422 | 10527 | 10528 | 10452 | Present Current Demand
Total | A,B | R | NV | 10423 | 10529 | 10530 | 10451 | Max KW Demand
Total | A,B,C | R | NV | 10426 | 10535 | 10536 | 10452 | Max Current Demand
2 | A,B | R | NV | 10427 | 10537 | 10538 | 10451 | Max KW
2 | A,B,C | R | NV | 10430 | 10543 | 10544 | 10452 | Max Current
2 | A,B | R |  | 10431 | 10545 | 10546 | 10453 | Voltage, L-L
2 | A,B | R |  | 10432 | 10547 | 10548 | 10453 | Voltage, L-N
2 | A,B | R |  | 10433 | 10549 | 10550 | -2 | Frequency (derived from Phase A) | [5 empty] | 40-70
2 | A,B | R |  | 10437 | 10557 | 10558 | 10449 | KWh Snapshot (MSW)
2 | A,B | R |  | 10438 |  |  |  | KWh Snapshot (LSW)
2 | A,B | R | NV | 10449 |  |  |  | Energy Scale
2 | A,B | R | NV | 10451 |  |  |  | Power Scale
2 | A,B,C | R | NV | 10452 |  |  |  | Current Scale
2 | A,B | R | NV | 10453 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 2
2 | A,B,C | W |  | 10457 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset:
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 2
All | A,B,C | R/W | NV | 10458 |  |  |  | Circuit CT Size | [5 empty] | 0-32767 | 100
Breaker Sizes (Amps) - Phase 2
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
2 | A,B,C | R/W | NV | 10459 |  |  |  | Chanel Breaker Size | [5 empty] | 0-32767 | 20
Circuit Alarm Status - Phase 2
2 | A,B,C | R/W | NV | 10460 |  |  |  | Channel Latching Alarm Status
Latching Alarms are cleared by writing a 0 to its alarm bit
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
2 | A,B,C | R |  | 10461 |  |  |  | Channel Non-Latching Alarm Status
Bit 0: Reserved for High High Non-Latching Alarm (reads 0)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 2
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
2 | A,B,C | R |  | 10462 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 10463 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 10464 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 10465 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | A,B,C | R |  | 10466 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
Panel & Branch Assignment - Phase 3
1 | A,B,C | R | NV | 10604 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 3
3 | A,B | R | NV | 10605 | 10701 | 10702 | 10649 | KWh (MSW)
3 | A,B | R | NV | 10606 |  |  |  | KWh (LSW)
3 | A,B | R |  | 10613 | 10709 | 10710 | 10651 | KW
3 | A,B | R |  | 10615 | 10713 | 10714 | 10651 | KVA
3 | A,B | R |  | 10616 | 10715 | 10716 | -3 | PF | [5 empty] | 0.0 - 1.0
3 | A,B |  |  | 10617 | 10717 | 10718 | -1 | Current Angle
3 | A,B,C | R |  | 10618 | 10719 | 10720 | 10652 | Current
3 | A,B | R |  | 10619 | 10721 | 10722 | 10651 | Present KW Demand
Total | A,B,C | R |  | 10622 | 10727 | 10728 | 10652 | Present Current Demand
Total | A,B | R | NV | 10623 | 10729 | 10730 | 10651 | Max KW Demand
Total | A,B,C | R | NV | 10626 | 10735 | 10736 | 10652 | Max Current Demand
3 | A,B | R | NV | 10627 | 10737 | 10738 | 10651 | Max KW
3 | A,B,C | R | NV | 10630 | 10743 | 10744 | 10652 | Max Current
3 | A,B | R |  | 10631 | 10745 | 10746 | 10653 | Voltage, L-L
3 | A,B | R |  | 10632 | 10747 | 10748 | 10653 | Voltage, L-N
3 | A,B | R |  | 10633 | 10749 | 10750 | -2 | Frequency (derived from Phase A) | [5 empty] | 40-70
3 | A,B | R |  | 10637 | 10757 | 10758 | 10649 | KWh Snapshot (MSW)
3 | A,B | R |  | 10638 |  |  |  | KWh Snapshot (LSW)
3 | A,B | R | NV | 10649 |  |  |  | Energy Scale
3 | A,B | R | NV | 10651 |  |  |  | Power Scale
3 | A,B,C | R | NV | 10652 |  |  |  | Current Scale
3 | A,B | R | NV | 10653 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 3
3 | A,B,C | W |  | 10657 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset:
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 3
All | A,B,C | R/W | NV | 10658 |  |  |  | Circuit CT Size | [5 empty] | 0-32767 | 100
Breaker Sizes (Amps) - Phase 3
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
3 | A,B,C | R/W | NV | 10659 |  |  |  | Chanel Breaker Size | [5 empty] | 0-32767 | 20
Circuit Alarm Status - Phase 3
3 | A,B,C | R/W | NV | 10660 |  |  |  | Channel Latching Alarm Status
Latching Alarms are cleared by writing a 0 to its alarm bit
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
3 | A,B,C | R |  | 10661 |  |  |  | Channel Non-Latching Alarm Status
Bit 0: Reserved for High High Non-Latching Alarm (reads 0)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 3
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
3 | A,B,C | R |  | 10662 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 10663 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 10664 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 10665 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | A,B,C | R |  | 10666 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
total registers in this section
482

## Logical Map by Type
Note: This map replaces the 2PH & 3PH Map and is enabled in User Setting Register 62017
[8 empty] | Modbus |  |  |  |  | BACnet
Group | Model (A,B,C) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description | Object Name | Object ID | Units | COV Increment | BACnet Description | Range | Default
SCALE REGISTERS
1 | A,B,C | R | NV | 4000 |  |  |  | Current Scale
2 | A,B,C | R | NV | 4001 |  |  |  | Current Scale
3 | A,B,C | R | NV | 4002 |  |  |  | Current Scale
4 | A,B,C | R | NV | 4003 |  |  |  | Current Scale
5 | A,B,C | R | NV | 4004 |  |  |  | Current Scale
6 | A,B,C | R | NV | 4005 |  |  |  | Current Scale
7 | A,B,C | R | NV | 4006 |  |  |  | Current Scale
8 | A,B,C | R | NV | 4007 |  |  |  | Current Scale
9 | A,B,C | R | NV | 4008 |  |  |  | Current Scale
10 | A,B,C | R | NV | 4009 |  |  |  | Current Scale
11 | A,B,C | R | NV | 4010 |  |  |  | Current Scale
12 | A,B,C | R | NV | 4011 |  |  |  | Current Scale
13 | A,B,C | R | NV | 4012 |  |  |  | Current Scale
14 | A,B,C | R | NV | 4013 |  |  |  | Current Scale
15 | A,B,C | R | NV | 4014 |  |  |  | Current Scale
16 | A,B,C | R | NV | 4015 |  |  |  | Current Scale
17 | A,B,C | R | NV | 4016 |  |  |  | Current Scale
18 | A,B,C | R | NV | 4017 |  |  |  | Current Scale
19 | A,B,C | R | NV | 4018 |  |  |  | Current Scale
20 | A,B,C | R | NV | 4019 |  |  |  | Current Scale
21 | A,B,C | R | NV | 4020 |  |  |  | Current Scale
22 | A,B,C | R | NV | 4021 |  |  |  | Current Scale
23 | A,B,C | R | NV | 4022 |  |  |  | Current Scale
24 | A,B,C | R | NV | 4023 |  |  |  | Current Scale
25 | A,B,C | R | NV | 4024 |  |  |  | Current Scale
26 | A,B,C | R | NV | 4025 |  |  |  | Current Scale
27 | A,B,C | R | NV | 4026 |  |  |  | Current Scale
28 | A,B,C | R | NV | 4027 |  |  |  | Current Scale
29 | A,B,C | R | NV | 4028 |  |  |  | Current Scale
30 | A,B,C | R | NV | 4029 |  |  |  | Current Scale
31 | A,B,C | R | NV | 4030 |  |  |  | Current Scale
32 | A,B,C | R | NV | 4031 |  |  |  | Current Scale
33 | A,B,C | R | NV | 4032 |  |  |  | Current Scale
34 | A,B,C | R | NV | 4033 |  |  |  | Current Scale
35 | A,B,C | R | NV | 4034 |  |  |  | Current Scale
36 | A,B,C | R | NV | 4035 |  |  |  | Current Scale
37 | A,B,C | R | NV | 4036 |  |  |  | Current Scale
38 | A,B,C | R | NV | 4037 |  |  |  | Current Scale
39 | A,B,C | R | NV | 4038 |  |  |  | Current Scale
40 | A,B,C | R | NV | 4039 |  |  |  | Current Scale
41 | A,B,C | R | NV | 4040 |  |  |  | Current Scale
42 | A,B,C | R | NV | 4041 |  |  |  | Current Scale
43 | A,B,C | R | NV | 4042 |  |  |  | Current Scale
44 | A,B,C | R | NV | 4043 |  |  |  | Current Scale
45 | A,B,C | R | NV | 4044 |  |  |  | Current Scale
46 | A,B,C | R | NV | 4045 |  |  |  | Current Scale
1 | A | R | NV | 4046 |  |  |  | Power Scale
2 | A | R | NV | 4047 |  |  |  | Power Scale
3 | A | R | NV | 4048 |  |  |  | Power Scale
4 | A | R | NV | 4049 |  |  |  | Power Scale
5 | A | R | NV | 4050 |  |  |  | Power Scale
6 | A | R | NV | 4051 |  |  |  | Power Scale
7 | A | R | NV | 4052 |  |  |  | Power Scale
8 | A | R | NV | 4053 |  |  |  | Power Scale
9 | A | R | NV | 4054 |  |  |  | Power Scale
10 | A | R | NV | 4055 |  |  |  | Power Scale
11 | A | R | NV | 4056 |  |  |  | Power Scale
12 | A | R | NV | 4057 |  |  |  | Power Scale
13 | A | R | NV | 4058 |  |  |  | Power Scale
14 | A | R | NV | 4059 |  |  |  | Power Scale
15 | A | R | NV | 4060 |  |  |  | Power Scale
16 | A | R | NV | 4061 |  |  |  | Power Scale
17 | A | R | NV | 4062 |  |  |  | Power Scale
18 | A | R | NV | 4063 |  |  |  | Power Scale
19 | A | R | NV | 4064 |  |  |  | Power Scale
20 | A | R | NV | 4065 |  |  |  | Power Scale
21 | A | R | NV | 4066 |  |  |  | Power Scale
22 | A | R | NV | 4067 |  |  |  | Power Scale
23 | A | R | NV | 4068 |  |  |  | Power Scale
24 | A | R | NV | 4069 |  |  |  | Power Scale
25 | A | R | NV | 4070 |  |  |  | Power Scale
26 | A | R | NV | 4071 |  |  |  | Power Scale
27 | A | R | NV | 4072 |  |  |  | Power Scale
28 | A | R | NV | 4073 |  |  |  | Power Scale
29 | A | R | NV | 4074 |  |  |  | Power Scale
30 | A | R | NV | 4075 |  |  |  | Power Scale
31 | A | R | NV | 4076 |  |  |  | Power Scale
32 | A | R | NV | 4077 |  |  |  | Power Scale
33 | A | R | NV | 4078 |  |  |  | Power Scale
34 | A | R | NV | 4079 |  |  |  | Power Scale
35 | A | R | NV | 4080 |  |  |  | Power Scale
36 | A | R | NV | 4081 |  |  |  | Power Scale
37 | A | R | NV | 4082 |  |  |  | Power Scale
38 | A | R | NV | 4083 |  |  |  | Power Scale
39 | A | R | NV | 4084 |  |  |  | Power Scale
40 | A | R | NV | 4085 |  |  |  | Power Scale
41 | A | R | NV | 4086 |  |  |  | Power Scale
42 | A | R | NV | 4087 |  |  |  | Power Scale
43 | A | R | NV | 4088 |  |  |  | Power Scale
44 | A | R | NV | 4089 |  |  |  | Power Scale
45 | A | R | NV | 4090 |  |  |  | Power Scale
46 | A | R | NV | 4091 |  |  |  | Power Scale
1 | A | R | NV | 4092 |  |  |  | Energy Scale
2 | A | R | NV | 4093 |  |  |  | Energy Scale
3 | A | R | NV | 4094 |  |  |  | Energy Scale
4 | A | R | NV | 4095 |  |  |  | Energy Scale
5 | A | R | NV | 4096 |  |  |  | Energy Scale
6 | A | R | NV | 4097 |  |  |  | Energy Scale
7 | A | R | NV | 4098 |  |  |  | Energy Scale
8 | A | R | NV | 4099 |  |  |  | Energy Scale
9 | A | R | NV | 4100 |  |  |  | Energy Scale
10 | A | R | NV | 4101 |  |  |  | Energy Scale
11 | A | R | NV | 4102 |  |  |  | Energy Scale
12 | A | R | NV | 4103 |  |  |  | Energy Scale
13 | A | R | NV | 4104 |  |  |  | Energy Scale
14 | A | R | NV | 4105 |  |  |  | Energy Scale
15 | A | R | NV | 4106 |  |  |  | Energy Scale
16 | A | R | NV | 4107 |  |  |  | Energy Scale
17 | A | R | NV | 4108 |  |  |  | Energy Scale
18 | A | R | NV | 4109 |  |  |  | Energy Scale
19 | A | R | NV | 4110 |  |  |  | Energy Scale
20 | A | R | NV | 4111 |  |  |  | Energy Scale
21 | A | R | NV | 4112 |  |  |  | Energy Scale
22 | A | R | NV | 4113 |  |  |  | Energy Scale
23 | A | R | NV | 4114 |  |  |  | Energy Scale
24 | A | R | NV | 4115 |  |  |  | Energy Scale
25 | A | R | NV | 4116 |  |  |  | Energy Scale
26 | A | R | NV | 4117 |  |  |  | Energy Scale
27 | A | R | NV | 4118 |  |  |  | Energy Scale
28 | A | R | NV | 4119 |  |  |  | Energy Scale
29 | A | R | NV | 4120 |  |  |  | Energy Scale
30 | A | R | NV | 4121 |  |  |  | Energy Scale
31 | A | R | NV | 4122 |  |  |  | Energy Scale
32 | A | R | NV | 4123 |  |  |  | Energy Scale
33 | A | R | NV | 4124 |  |  |  | Energy Scale
34 | A | R | NV | 4125 |  |  |  | Energy Scale
35 | A | R | NV | 4126 |  |  |  | Energy Scale
36 | A | R | NV | 4127 |  |  |  | Energy Scale
37 | A | R | NV | 4128 |  |  |  | Energy Scale
38 | A | R | NV | 4129 |  |  |  | Energy Scale
39 | A | R | NV | 4130 |  |  |  | Energy Scale
40 | A | R | NV | 4131 |  |  |  | Energy Scale
41 | A | R | NV | 4132 |  |  |  | Energy Scale
42 | A | R | NV | 4133 |  |  |  | Energy Scale
43 | A | R | NV | 4134 |  |  |  | Energy Scale
44 | A | R | NV | 4135 |  |  |  | Energy Scale
45 | A | R | NV | 4136 |  |  |  | Energy Scale
46 | A | R | NV | 4137 |  |  |  | Energy Scale
RESETS
Also resets corresponding registers in 2PH and 3PH point maps
1 | A,B,C | W |  | 4138 |  |  |  | Reset - Write the listed value to perform the listed reset: | Logical Ckt 1: Reset (1 of 6 values) | AO45 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
2 | A,B,C | W |  | 4139 |  |  |  | Reset | Logical Ckt 2: Reset (1 of 6 values) | AO46 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
3 | A,B,C | W |  | 4140 |  |  |  | Reset | Logical Ckt 3: Reset (1 of 6 values) | AO47 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
4 | A,B,C | W |  | 4141 |  |  |  | Reset | Logical Ckt 4: Reset (1 of 6 values) | AO48 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
5 | A,B,C | W |  | 4142 |  |  |  | Reset | Logical Ckt 5: Reset (1 of 6 values) | AO49 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
6 | A,B,C | W |  | 4143 |  |  |  | Reset | Logical Ckt 6: Reset (1 of 6 values) | AO50 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
7 | A,B,C | W |  | 4144 |  |  |  | Reset | Logical Ckt 7: Reset (1 of 6 values) | AO51 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
8 | A,B,C | W |  | 4145 |  |  |  | Reset | Logical Ckt 8: Reset (1 of 6 values) | AO52 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
9 | A,B,C | W |  | 4146 |  |  |  | Reset | Logical Ckt 9: Reset (1 of 6 values) | AO53 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
10 | A,B,C | W |  | 4147 |  |  |  | Reset | Logical Ckt 10: Reset (1 of 6 values) | AO54 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
11 | A,B,C | W |  | 4148 |  |  |  | Reset | Logical Ckt 11: Reset (1 of 6 values) | AO55 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
12 | A,B,C | W |  | 4149 |  |  |  | Reset | Logical Ckt 12: Reset (1 of 6 values) | AO56 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
13 | A,B,C | W |  | 4150 |  |  |  | Reset | Logical Ckt 13: Reset (1 of 6 values) | AO57 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
14 | A,B,C | W |  | 4151 |  |  |  | Reset | Logical Ckt 14: Reset (1 of 6 values) | AO58 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
15 | A,B,C | W |  | 4152 |  |  |  | Reset | Logical Ckt 15: Reset (1 of 6 values) | AO59 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
16 | A,B,C | W |  | 4153 |  |  |  | Reset | Logical Ckt 16: Reset (1 of 6 values) | AO60 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
17 | A,B,C | W |  | 4154 |  |  |  | Reset | Logical Ckt 17: Reset (1 of 6 values) | AO61 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
18 | A,B,C | W |  | 4155 |  |  |  | Reset | Logical Ckt 18: Reset (1 of 6 values) | AO62 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
19 | A,B,C | W |  | 4156 |  |  |  | Reset | Logical Ckt 19: Reset (1 of 6 values) | AO63 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
20 | A,B,C | W |  | 4157 |  |  |  | Reset | Logical Ckt 20: Reset (1 of 6 values) | AO64 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
21 | A,B,C | W |  | 4158 |  |  |  | Reset | Logical Ckt 21: Reset (1 of 6 values) | AO65 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
22 | A,B,C | W |  | 4159 |  |  |  | Reset | Logical Ckt 22: Reset (1 of 6 values) | AO66 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
23 | A,B,C | W |  | 4160 |  |  |  | Reset | Logical Ckt 23: Reset (1 of 6 values) | AO67 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
24 | A,B,C | W |  | 4161 |  |  |  | Reset | Logical Ckt 24: Reset (1 of 6 values) | AO68 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
25 | A,B,C | W |  | 4162 |  |  |  | Reset | Logical Ckt 25: Reset (1 of 6 values) | AO69 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
26 | A,B,C | W |  | 4163 |  |  |  | Reset | Logical Ckt 26: Reset (1 of 6 values) | AO70 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
27 | A,B,C | W |  | 4164 |  |  |  | Reset | Logical Ckt 27: Reset (1 of 6 values) | AO71 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
28 | A,B,C | W |  | 4165 |  |  |  | Reset | Logical Ckt 28: Reset (1 of 6 values) | AO72 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
29 | A,B,C | W |  | 4166 |  |  |  | Reset | Logical Ckt 29: Reset (1 of 6 values) | AO73 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
30 | A,B,C | W |  | 4167 |  |  |  | Reset | Logical Ckt 30: Reset (1 of 6 values) | AO74 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
31 | A,B,C | W |  | 4168 |  |  |  | Reset | Logical Ckt 31: Reset (1 of 6 values) | AO75 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
32 | A,B,C | W |  | 4169 |  |  |  | Reset | Logical Ckt 32: Reset (1 of 6 values) | AO76 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
33 | A,B,C | W |  | 4170 |  |  |  | Reset | Logical Ckt 33: Reset (1 of 6 values) | AO77 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
34 | A,B,C | W |  | 4171 |  |  |  | Reset | Logical Ckt 34: Reset (1 of 6 values) | AO78 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
35 | A,B,C | W |  | 4172 |  |  |  | Reset | Logical Ckt 35: Reset (1 of 6 values) | AO79 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
36 | A,B,C | W |  | 4173 |  |  |  | Reset | Logical Ckt 36: Reset (1 of 6 values) | AO80 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
37 | A,B,C | W |  | 4174 |  |  |  | Reset | Logical Ckt 37: Reset (1 of 6 values) | AO81 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
38 | A,B,C | W |  | 4175 |  |  |  | Reset | Logical Ckt 38: Reset (1 of 6 values) | AO82 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
39 | A,B,C | W |  | 4176 |  |  |  | Reset | Logical Ckt 39: Reset (1 of 6 values) | AO83 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
40 | A,B,C | W |  | 4177 |  |  |  | Reset | Logical Ckt 30: Reset (1 of 6 values) | AO84 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
41 | A,B,C | W |  | 4178 |  |  |  | Reset | Logical Ckt 41: Reset (1 of 6 values) | AO85 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
42 | A,B,C | W |  | 4179 |  |  |  | Reset | Logical Ckt 42: Reset (1 of 6 values) | AO86 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
43 | A,B,C | W |  | 4180 |  |  |  | Reset | Logical Ckt 43: Reset (1 of 6 values) | AO87 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
44 | A,B,C | W |  | 4181 |  |  |  | Reset | Logical Ckt 44: Reset (1 of 6 values) | AO88 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
45 | A,B,C | W |  | 4182 |  |  |  | Reset | Logical Ckt 45: Reset (1 of 6 values) | AO89 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
46 | A,B,C | W |  | 4183 |  |  |  | Reset | Logical Ckt 46: Reset (1 of 6 values) | AO90 | No-Units | 0 | Reset kWh; alarms; demand; max (6 val)
DATA
1 | A | R | NV | 4184 | 6000 | 6001 | 1084 | KWH (MSW) | kWh Logical Circuit 1 | AI766 | kWh | 1 | Real Energy - Circuit 1
1 | A | R | NV | 4185 |  |  |  | KWH (LSW)
2 | A | R | NV | 4186 | 6002 | 6003 | 1085 | KWH (MSW) | kWh Logical Circuit 2 | AI767 | kWh | 1 | Real Energy - Circuit 2
2 | A | R | NV | 4187 |  |  |  | KWH (LSW)
3 | A | R | NV | 4188 | 6004 | 6005 | 1086 | KWH (MSW) | kWh Logical Circuit 3 | AI768 | kWh | 1 | Real Energy - Circuit 3
3 | A | R | NV | 4189 |  |  |  | KWH (LSW)
4 | A | R | NV | 4190 | 6006 | 6007 | 1087 | KWH (MSW) | kWh Logical Circuit 4 | AI769 | kWh | 1 | Real Energy - Circuit 4
4 | A | R | NV | 4191 |  |  |  | KWH (LSW)
5 | A | R | NV | 4192 | 6008 | 6009 | 1088 | KWH (MSW) | kWh Logical Circuit 5 | AI770 | kWh | 1 | Real Energy - Circuit 5
5 | A | R | NV | 4193 |  |  |  | KWH (LSW)
6 | A | R | NV | 4194 | 6010 | 6011 | 1089 | KWH (MSW) | kWh Logical Circuit 6 | AI771 | kWh | 1 | Real Energy - Circuit 6
6 | A | R | NV | 4195 |  |  |  | KWH (LSW)
7 | A | R | NV | 4196 | 6012 | 6013 | 1090 | KWH (MSW) | kWh Logical Circuit 7 | AI772 | kWh | 1 | Real Energy - Circuit 7
7 | A | R | NV | 4197 |  |  |  | KWH (LSW)
8 | A | R | NV | 4198 | 6014 | 6015 | 1091 | KWH (MSW) | kWh Logical Circuit 8 | AI773 | kWh | 1 | Real Energy - Circuit 8
8 | A | R | NV | 4199 |  |  |  | KWH (LSW)
9 | A | R | NV | 4200 | 6016 | 6017 | 1092 | KWH (MSW) | kWh Logical Circuit 9 | AI774 | kWh | 1 | Real Energy - Circuit 9
9 | A | R | NV | 4201 |  |  |  | KWH (LSW)
10 | A | R | NV | 4202 | 6018 | 6019 | 1093 | KWH (MSW) | kWh Logical Circuit 10 | AI775 | kWh | 1 | Real Energy - Circuit 10
10 | A | R | NV | 4203 |  |  |  | KWH (LSW)
11 | A | R | NV | 4204 | 6020 | 6021 | 1094 | KWH (MSW) | kWh Logical Circuit 11 | AI776 | kWh | 1 | Real Energy - Circuit 11
11 | A | R | NV | 4205 |  |  |  | KWH (LSW)
12 | A | R | NV | 4206 | 6022 | 6023 | 1095 | KWH (MSW) | kWh Logical Circuit 12 | AI777 | kWh | 1 | Real Energy - Circuit 12
12 | A | R | NV | 4207 |  |  |  | KWH (LSW)
13 | A | R | NV | 4208 | 6024 | 6025 | 1096 | KWH (MSW) | kWh Logical Circuit 13 | AI778 | kWh | 1 | Real Energy - Circuit 13
13 | A | R | NV | 4209 |  |  |  | KWH (LSW)
14 | A | R | NV | 4210 | 6026 | 6027 | 1097 | KWH (MSW) | kWh Logical Circuit 14 | AI779 | kWh | 1 | Real Energy - Circuit 14
14 | A | R | NV | 4211 |  |  |  | KWH (LSW)
15 | A | R | NV | 4212 | 6028 | 6029 | 1098 | KWH (MSW) | kWh Logical Circuit 15 | AI780 | kWh | 1 | Real Energy - Circuit 15
15 | A | R | NV | 4213 |  |  |  | KWH (LSW)
16 | A | R | NV | 4214 | 6030 | 6031 | 1099 | KWH (MSW) | kWh Logical Circuit 16 | AI781 | kWh | 1 | Real Energy - Circuit 16
16 | A | R | NV | 4215 |  |  |  | KWH (LSW)
17 | A | R | NV | 4216 | 6032 | 6033 | 1100 | KWH (MSW) | kWh Logical Circuit 17 | AI782 | kWh | 1 | Real Energy - Circuit 17
17 | A | R | NV | 4217 |  |  |  | KWH (LSW)
18 | A | R | NV | 4218 | 6034 | 6035 | 1101 | KWH (MSW) | kWh Logical Circuit 18 | AI783 | kWh | 1 | Real Energy - Circuit 18
18 | A | R | NV | 4219 |  |  |  | KWH (LSW)
19 | A | R | NV | 4220 | 6036 | 6037 | 1102 | KWH (MSW) | kWh Logical Circuit 19 | AI784 | kWh | 1 | Real Energy - Circuit 19
19 | A | R | NV | 4221 |  |  |  | KWH (LSW)
20 | A | R | NV | 4222 | 6038 | 6039 | 1103 | KWH (MSW) | kWh Logical Circuit 20 | AI785 | kWh | 1 | Real Energy - Circuit 20
20 | A | R | NV | 4223 |  |  |  | KWH (LSW)
21 | A | R | NV | 4224 | 6040 | 6041 | 1104 | KWH (MSW) | kWh Logical Circuit 21 | AI786 | kWh | 1 | Real Energy - Circuit 21
21 | A | R | NV | 4225 |  |  |  | KWH (LSW)
22 | A | R | NV | 4226 | 6042 | 6043 | 1105 | KWH (MSW) | kWh Logical Circuit 22 | AI787 | kWh | 1 | Real Energy - Circuit 22
22 | A | R | NV | 4227 |  |  |  | KWH (LSW)
23 | A | R | NV | 4228 | 6044 | 6045 | 1106 | KWH (MSW) | kWh Logical Circuit 23 | AI788 | kWh | 1 | Real Energy - Circuit 23
23 | A | R | NV | 4229 |  |  |  | KWH (LSW)
24 | A | R | NV | 4230 | 6046 | 6047 | 1107 | KWH (MSW) | kWh Logical Circuit 24 | AI789 | kWh | 1 | Real Energy - Circuit 24
24 | A | R | NV | 4231 |  |  |  | KWH (LSW)
25 | A | R | NV | 4232 | 6048 | 6049 | 1108 | KWH (MSW) | kWh Logical Circuit 25 | AI790 | kWh | 1 | Real Energy - Circuit 25
25 | A | R | NV | 4233 |  |  |  | KWH (LSW)
26 | A | R | NV | 4234 | 6050 | 6051 | 1109 | KWH (MSW) | kWh Logical Circuit 26 | AI791 | kWh | 1 | Real Energy - Circuit 26
26 | A | R | NV | 4235 |  |  |  | KWH (LSW)
27 | A | R | NV | 4236 | 6052 | 6053 | 1110 | KWH (MSW) | kWh Logical Circuit 27 | AI792 | kWh | 1 | Real Energy - Circuit 27
27 | A | R | NV | 4237 |  |  |  | KWH (LSW)
28 | A | R | NV | 4238 | 6054 | 6055 | 1111 | KWH (MSW) | kWh Logical Circuit 28 | AI793 | kWh | 1 | Real Energy - Circuit 28
28 | A | R | NV | 4239 |  |  |  | KWH (LSW)
29 | A | R | NV | 4240 | 6056 | 6057 | 1112 | KWH (MSW) | kWh Logical Circuit 29 | AI794 | kWh | 1 | Real Energy - Circuit 29
29 | A | R | NV | 4241 |  |  |  | KWH (LSW)
30 | A | R | NV | 4242 | 6058 | 6059 | 1113 | KWH (MSW) | kWh Logical Circuit 30 | AI795 | kWh | 1 | Real Energy - Circuit 30
30 | A | R | NV | 4243 |  |  |  | KWH (LSW)
31 | A | R | NV | 4244 | 6060 | 6061 | 1114 | KWH (MSW) | kWh Logical Circuit 31 | AI796 | kWh | 1 | Real Energy - Circuit 31
31 | A | R | NV | 4245 |  |  |  | KWH (LSW)
32 | A | R | NV | 4246 | 6062 | 6063 | 1115 | KWH (MSW) | kWh Logical Circuit 32 | AI797 | kWh | 1 | Real Energy - Circuit 32
32 | A | R | NV | 4247 |  |  |  | KWH (LSW)
33 | A | R | NV | 4248 | 6064 | 6065 | 1116 | KWH (MSW) | kWh Logical Circuit 33 | AI798 | kWh | 1 | Real Energy - Circuit 33
33 | A | R | NV | 4249 |  |  |  | KWH (LSW)
34 | A | R | NV | 4250 | 6066 | 6067 | 1117 | KWH (MSW) | kWh Logical Circuit 34 | AI799 | kWh | 1 | Real Energy - Circuit 34
34 | A | R | NV | 4251 |  |  |  | KWH (LSW)
35 | A | R | NV | 4252 | 6068 | 6069 | 1118 | KWH (MSW) | kWh Logical Circuit 35 | AI800 | kWh | 1 | Real Energy - Circuit 35
35 | A | R | NV | 4253 |  |  |  | KWH (LSW)
36 | A | R | NV | 4254 | 6070 | 6071 | 1119 | KWH (MSW) | kWh Logical Circuit 36 | AI801 | kWh | 1 | Real Energy - Circuit 36
36 | A | R | NV | 4255 |  |  |  | KWH (LSW)
37 | A | R | NV | 4256 | 6072 | 6073 | 1120 | KWH (MSW) | kWh Logical Circuit 37 | AI802 | kWh | 1 | Real Energy - Circuit 37
37 | A | R | NV | 4257 |  |  |  | KWH (LSW)
38 | A | R | NV | 4258 | 6074 | 6075 | 1121 | KWH (MSW) | kWh Logical Circuit 38 | AI803 | kWh | 1 | Real Energy - Circuit 38
38 | A | R | NV | 4259 |  |  |  | KWH (LSW)
39 | A | R | NV | 4260 | 6076 | 6077 | 1122 | KWH (MSW) | kWh Logical Circuit 39 | AI804 | kWh | 1 | Real Energy - Circuit 39
39 | A | R | NV | 4261 |  |  |  | KWH (LSW)
40 | A | R | NV | 4262 | 6078 | 6079 | 1123 | KWH (MSW) | kWh Logical Circuit 40 | AI805 | kWh | 1 | Real Energy - Circuit 40
40 | A | R | NV | 4263 |  |  |  | KWH (LSW)
41 | A | R | NV | 4264 | 6080 | 6081 | 1124 | KWH (MSW) | kWh Logical Circuit 41 | AI806 | kWh | 1 | Real Energy - Circuit 41
41 | A | R | NV | 4265 |  |  |  | KWH (LSW)
42 | A | R | NV | 4266 | 6082 | 6083 | 1125 | KWH (MSW) | kWh Logical Circuit 42 | AI807 | kWh | 1 | Real Energy - Circuit 42
42 | A | R | NV | 4267 |  |  |  | KWH (LSW)
43 | A | R | NV | 4268 | 6084 | 6085 | 1126 | KWH (MSW) | kWh Logical Circuit 43 | AI808 | kWh | 1 | Real Energy - Circuit 43
43 | A | R | NV | 4269 |  |  |  | KWH (LSW)
44 | A | R | NV | 4270 | 6086 | 6087 | 1127 | KWH (MSW) | kWh Logical Circuit 44 | AI809 | kWh | 1 | Real Energy - Circuit 44
44 | A | R | NV | 4271 |  |  |  | KWH (LSW)
45 | A | R | NV | 4272 | 6088 | 6089 | 1128 | KWH (MSW) | kWh Logical Circuit 45 | AI810 | kWh | 1 | Real Energy - Circuit 45
45 | A | R | NV | 4273 |  |  |  | KWH (LSW)
46 | A | R | NV | 4274 | 6090 | 6091 | 1129 | KWH (MSW) | kWh Logical Circuit 46 | AI811 | kWh | 1 | Real Energy - Circuit 46
46 | A | R | NV | 4275 |  |  |  | KWH (LSW)
1 | A | R |  | 4276 | 6092 | 6093 | 1042 | KW | kW Logical Circuit 1 | AI812 | kW | 1 | Instantaneous Real Power - Circuit 1
2 | A | R |  | 4277 | 6094 | 6095 | 1043 | KW | kW Logical Circuit 2 | AI813 | kW | 1 | Instantaneous Real Power - Circuit 2
3 | A | R |  | 4278 | 6096 | 6097 | 1044 | KW | kW Logical Circuit 3 | AI814 | kW | 1 | Instantaneous Real Power - Circuit 3
4 | A | R |  | 4279 | 6098 | 6099 | 1045 | KW | kW Logical Circuit 4 | AI815 | kW | 1 | Instantaneous Real Power - Circuit 4
5 | A | R |  | 4280 | 6100 | 6101 | 1046 | KW | kW Logical Circuit 5 | AI816 | kW | 1 | Instantaneous Real Power - Circuit 5
6 | A | R |  | 4281 | 6102 | 6103 | 1047 | KW | kW Logical Circuit 6 | AI817 | kW | 1 | Instantaneous Real Power - Circuit 6
7 | A | R |  | 4282 | 6104 | 6105 | 1048 | KW | kW Logical Circuit 7 | AI818 | kW | 1 | Instantaneous Real Power - Circuit 7
8 | A | R |  | 4283 | 6106 | 6107 | 1049 | KW | kW Logical Circuit 8 | AI819 | kW | 1 | Instantaneous Real Power - Circuit 8
9 | A | R |  | 4284 | 6108 | 6109 | 1050 | KW | kW Logical Circuit 9 | AI820 | kW | 1 | Instantaneous Real Power - Circuit 9
10 | A | R |  | 4285 | 6110 | 6111 | 1051 | KW | kW Logical Circuit 10 | AI821 | kW | 1 | Instantaneous Real Power - Circuit 10
11 | A | R |  | 4286 | 6112 | 6113 | 1052 | KW | kW Logical Circuit 11 | AI822 | kW | 1 | Instantaneous Real Power - Circuit 11
12 | A | R |  | 4287 | 6114 | 6115 | 1053 | KW | kW Logical Circuit 12 | AI823 | kW | 1 | Instantaneous Real Power - Circuit 12
13 | A | R |  | 4288 | 6116 | 6117 | 1054 | KW | kW Logical Circuit 13 | AI824 | kW | 1 | Instantaneous Real Power - Circuit 13
14 | A | R |  | 4289 | 6118 | 6119 | 1055 | KW | kW Logical Circuit 14 | AI825 | kW | 1 | Instantaneous Real Power - Circuit 14
15 | A | R |  | 4290 | 6120 | 6121 | 1056 | KW | kW Logical Circuit 15 | AI826 | kW | 1 | Instantaneous Real Power - Circuit 15
16 | A | R |  | 4291 | 6122 | 6123 | 1057 | KW | kW Logical Circuit 16 | AI827 | kW | 1 | Instantaneous Real Power - Circuit 16
17 | A | R |  | 4292 | 6124 | 6125 | 1058 | KW | kW Logical Circuit 17 | AI828 | kW | 1 | Instantaneous Real Power - Circuit 17
18 | A | R |  | 4293 | 6126 | 6127 | 1059 | KW | kW Logical Circuit 18 | AI829 | kW | 1 | Instantaneous Real Power - Circuit 18
19 | A | R |  | 4294 | 6128 | 6129 | 1060 | KW | kW Logical Circuit 19 | AI830 | kW | 1 | Instantaneous Real Power - Circuit 19
20 | A | R |  | 4295 | 6130 | 6131 | 1061 | KW | kW Logical Circuit 20 | AI831 | kW | 1 | Instantaneous Real Power - Circuit 20
21 | A | R |  | 4296 | 6132 | 6133 | 1062 | KW | kW Logical Circuit 21 | AI832 | kW | 1 | Instantaneous Real Power - Circuit 21
22 | A | R |  | 4297 | 6134 | 6135 | 1063 | KW | kW Logical Circuit 22 | AI833 | kW | 1 | Instantaneous Real Power - Circuit 22
23 | A | R |  | 4298 | 6136 | 6137 | 1064 | KW | kW Logical Circuit 23 | AI834 | kW | 1 | Instantaneous Real Power - Circuit 23
24 | A | R |  | 4299 | 6138 | 6139 | 1065 | KW | kW Logical Circuit 24 | AI835 | kW | 1 | Instantaneous Real Power - Circuit 24
25 | A | R |  | 4300 | 6140 | 6141 | 1066 | KW | kW Logical Circuit 25 | AI836 | kW | 1 | Instantaneous Real Power - Circuit 25
26 | A | R |  | 4301 | 6142 | 6143 | 1067 | KW | kW Logical Circuit 26 | AI837 | kW | 1 | Instantaneous Real Power - Circuit 26
27 | A | R |  | 4302 | 6144 | 6145 | 1068 | KW | kW Logical Circuit 27 | AI838 | kW | 1 | Instantaneous Real Power - Circuit 27
28 | A | R |  | 4303 | 6146 | 6147 | 1069 | KW | kW Logical Circuit 28 | AI839 | kW | 1 | Instantaneous Real Power - Circuit 28
29 | A | R |  | 4304 | 6148 | 6149 | 1070 | KW | kW Logical Circuit 29 | AI840 | kW | 1 | Instantaneous Real Power - Circuit 29
30 | A | R |  | 4305 | 6150 | 6151 | 1071 | KW | kW Logical Circuit 30 | AI841 | kW | 1 | Instantaneous Real Power - Circuit 30
31 | A | R |  | 4306 | 6152 | 6153 | 1072 | KW | kW Logical Circuit 31 | AI842 | kW | 1 | Instantaneous Real Power - Circuit 31
32 | A | R |  | 4307 | 6154 | 6155 | 1073 | KW | kW Logical Circuit 32 | AI843 | kW | 1 | Instantaneous Real Power - Circuit 32
33 | A | R |  | 4308 | 6156 | 6157 | 1074 | KW | kW Logical Circuit 33 | AI844 | kW | 1 | Instantaneous Real Power - Circuit 33
34 | A | R |  | 4309 | 6158 | 6159 | 1075 | KW | kW Logical Circuit 34 | AI845 | kW | 1 | Instantaneous Real Power - Circuit 34
35 | A | R |  | 4310 | 6160 | 6161 | 1076 | KW | kW Logical Circuit 35 | AI846 | kW | 1 | Instantaneous Real Power - Circuit 35
36 | A | R |  | 4311 | 6162 | 6163 | 1077 | KW | kW Logical Circuit 36 | AI847 | kW | 1 | Instantaneous Real Power - Circuit 36
37 | A | R |  | 4312 | 6164 | 6165 | 1078 | KW | kW Logical Circuit 37 | AI848 | kW | 1 | Instantaneous Real Power - Circuit 37
38 | A | R |  | 4313 | 6166 | 6167 | 1079 | KW | kW Logical Circuit 38 | AI849 | kW | 1 | Instantaneous Real Power - Circuit 38
39 | A | R |  | 4314 | 6168 | 6169 | 1080 | KW | kW Logical Circuit 39 | AI850 | kW | 1 | Instantaneous Real Power - Circuit 39
40 | A | R |  | 4315 | 6170 | 6171 | 1081 | KW | kW Logical Circuit 40 | AI851 | kW | 1 | Instantaneous Real Power - Circuit 40
41 | A | R |  | 4316 | 6172 | 6173 | 1082 | KW | kW Logical Circuit 41 | AI852 | kW | 1 | Instantaneous Real Power - Circuit 41
42 | A | R |  | 4317 | 6174 | 6175 | 1083 | KW | kW Logical Circuit 42 | AI853 | kW | 1 | Instantaneous Real Power - Circuit 42
43 | A | R |  | 4318 | 6176 | 6177 | 1084 | KW | kW Logical Circuit 43 | AI854 | kW | 1 | Instantaneous Real Power - Circuit 43
44 | A | R |  | 4319 | 6178 | 6179 | 1085 | KW | kW Logical Circuit 44 | AI855 | kW | 1 | Instantaneous Real Power - Circuit 44
45 | A | R |  | 4320 | 6180 | 6181 | 1086 | KW | kW Logical Circuit 45 | AI856 | kW | 1 | Instantaneous Real Power - Circuit 45
46 | A | R |  | 4321 | 6182 | 6183 | 1087 | KW | kW Logical Circuit 46 | AI857 | kW | 1 | Instantaneous Real Power - Circuit 46
1 | A | R |  | 4322 | 6184 | 6185 | 1042 | KVA | kVA Logical Circuit 1 | AI858 | kVA | 1 | Instantaneous Apparent Power - Ckt 1
2 | A | R |  | 4323 | 6186 | 6187 | 1043 | KVA | kVA Logical Circuit 2 | AI859 | kVA | 1 | Instantaneous Apparent Power - Ckt 2
3 | A | R |  | 4324 | 6188 | 6189 | 1044 | KVA | kVA Logical Circuit 3 | AI860 | kVA | 1 | Instantaneous Apparent Power - Ckt 3
4 | A | R |  | 4325 | 6190 | 6191 | 1045 | KVA | kVA Logical Circuit 4 | AI861 | kVA | 1 | Instantaneous Apparent Power - Ckt 4
5 | A | R |  | 4326 | 6192 | 6193 | 1046 | KVA | kVA Logical Circuit 5 | AI862 | kVA | 1 | Instantaneous Apparent Power - Ckt 5
6 | A | R |  | 4327 | 6194 | 6195 | 1047 | KVA | kVA Logical Circuit 6 | AI863 | kVA | 1 | Instantaneous Apparent Power - Ckt 6
7 | A | R |  | 4328 | 6196 | 6197 | 1048 | KVA | kVA Logical Circuit 7 | AI864 | kVA | 1 | Instantaneous Apparent Power - Ckt 7
8 | A | R |  | 4329 | 6198 | 6199 | 1049 | KVA | kVA Logical Circuit 8 | AI865 | kVA | 1 | Instantaneous Apparent Power - Ckt 8
9 | A | R |  | 4330 | 6200 | 6201 | 1050 | KVA | kVA Logical Circuit 9 | AI866 | kVA | 1 | Instantaneous Apparent Power - Ckt 9
10 | A | R |  | 4331 | 6202 | 6203 | 1051 | KVA | kVA Logical Circuit 10 | AI867 | kVA | 1 | Instantaneous Apparent Power - Ckt 10
11 | A | R |  | 4332 | 6204 | 6205 | 1052 | KVA | kVA Logical Circuit 11 | AI868 | kVA | 1 | Instantaneous Apparent Power - Ckt 11
12 | A | R |  | 4333 | 6206 | 6207 | 1053 | KVA | kVA Logical Circuit 12 | AI869 | kVA | 1 | Instantaneous Apparent Power - Ckt 12
13 | A | R |  | 4334 | 6208 | 6209 | 1054 | KVA | kVA Logical Circuit 13 | AI870 | kVA | 1 | Instantaneous Apparent Power - Ckt 13
14 | A | R |  | 4335 | 6210 | 6211 | 1055 | KVA | kVA Logical Circuit 14 | AI871 | kVA | 1 | Instantaneous Apparent Power - Ckt 14
15 | A | R |  | 4336 | 6212 | 6213 | 1056 | KVA | kVA Logical Circuit 15 | AI872 | kVA | 1 | Instantaneous Apparent Power - Ckt 15
16 | A | R |  | 4337 | 6214 | 6215 | 1057 | KVA | kVA Logical Circuit 16 | AI873 | kVA | 1 | Instantaneous Apparent Power - Ckt 16
17 | A | R |  | 4338 | 6216 | 6217 | 1058 | KVA | kVA Logical Circuit 17 | AI874 | kVA | 1 | Instantaneous Apparent Power - Ckt 17
18 | A | R |  | 4339 | 6218 | 6219 | 1059 | KVA | kVA Logical Circuit 18 | AI875 | kVA | 1 | Instantaneous Apparent Power - Ckt 18
19 | A | R |  | 4340 | 6220 | 6221 | 1060 | KVA | kVA Logical Circuit 19 | AI876 | kVA | 1 | Instantaneous Apparent Power - Ckt 19
20 | A | R |  | 4341 | 6222 | 6223 | 1061 | KVA | kVA Logical Circuit 20 | AI877 | kVA | 1 | Instantaneous Apparent Power - Ckt 20
21 | A | R |  | 4342 | 6224 | 6225 | 1062 | KVA | kVA Logical Circuit 21 | AI878 | kVA | 1 | Instantaneous Apparent Power - Ckt 21
22 | A | R |  | 4343 | 6226 | 6227 | 1063 | KVA | kVA Logical Circuit 22 | AI879 | kVA | 1 | Instantaneous Apparent Power - Ckt 22
23 | A | R |  | 4344 | 6228 | 6229 | 1064 | KVA | kVA Logical Circuit 23 | AI880 | kVA | 1 | Instantaneous Apparent Power - Ckt 23
24 | A | R |  | 4345 | 6230 | 6231 | 1065 | KVA | kVA Logical Circuit 24 | AI881 | kVA | 1 | Instantaneous Apparent Power - Ckt 24
25 | A | R |  | 4346 | 6232 | 6233 | 1066 | KVA | kVA Logical Circuit 25 | AI882 | kVA | 1 | Instantaneous Apparent Power - Ckt 25
26 | A | R |  | 4347 | 6234 | 6235 | 1067 | KVA | kVA Logical Circuit 26 | AI883 | kVA | 1 | Instantaneous Apparent Power - Ckt 26
27 | A | R |  | 4348 | 6236 | 6237 | 1068 | KVA | kVA Logical Circuit 27 | AI884 | kVA | 1 | Instantaneous Apparent Power - Ckt 27
28 | A | R |  | 4349 | 6238 | 6239 | 1069 | KVA | kVA Logical Circuit 28 | AI885 | kVA | 1 | Instantaneous Apparent Power - Ckt 28
29 | A | R |  | 4350 | 6240 | 6241 | 1070 | KVA | kVA Logical Circuit 29 | AI886 | kVA | 1 | Instantaneous Apparent Power - Ckt 29
30 | A | R |  | 4351 | 6242 | 6243 | 1071 | KVA | kVA Logical Circuit 30 | AI887 | kVA | 1 | Instantaneous Apparent Power - Ckt 30
31 | A | R |  | 4352 | 6244 | 6245 | 1072 | KVA | kVA Logical Circuit 31 | AI888 | kVA | 1 | Instantaneous Apparent Power - Ckt 31
32 | A | R |  | 4353 | 6246 | 6247 | 1073 | KVA | kVA Logical Circuit 32 | AI889 | kVA | 1 | Instantaneous Apparent Power - Ckt 32
33 | A | R |  | 4354 | 6248 | 6249 | 1074 | KVA | kVA Logical Circuit 33 | AI890 | kVA | 1 | Instantaneous Apparent Power - Ckt 33
34 | A | R |  | 4355 | 6250 | 6251 | 1075 | KVA | kVA Logical Circuit 34 | AI891 | kVA | 1 | Instantaneous Apparent Power - Ckt 34
35 | A | R |  | 4356 | 6252 | 6253 | 1076 | KVA | kVA Logical Circuit 35 | AI892 | kVA | 1 | Instantaneous Apparent Power - Ckt 35
36 | A | R |  | 4357 | 6254 | 6255 | 1077 | KVA | kVA Logical Circuit 36 | AI893 | kVA | 1 | Instantaneous Apparent Power - Ckt 36
37 | A | R |  | 4358 | 6256 | 6257 | 1078 | KVA | kVA Logical Circuit 37 | AI894 | kVA | 1 | Instantaneous Apparent Power - Ckt 37
38 | A | R |  | 4359 | 6258 | 6259 | 1079 | KVA | kVA Logical Circuit 38 | AI895 | kVA | 1 | Instantaneous Apparent Power - Ckt 38
39 | A | R |  | 4360 | 6260 | 6261 | 1080 | KVA | kVA Logical Circuit 39 | AI896 | kVA | 1 | Instantaneous Apparent Power - Ckt 39
40 | A | R |  | 4361 | 6262 | 6263 | 1081 | KVA | kVA Logical Circuit 40 | AI897 | kVA | 1 | Instantaneous Apparent Power - Ckt 40
41 | A | R |  | 4362 | 6264 | 6265 | 1082 | KVA | kVA Logical Circuit 41 | AI898 | kVA | 1 | Instantaneous Apparent Power - Ckt 41
42 | A | R |  | 4363 | 6266 | 6267 | 1083 | KVA | kVA Logical Circuit 42 | AI899 | kVA | 1 | Instantaneous Apparent Power - Ckt 42
43 | A | R |  | 4364 | 6268 | 6269 | 1084 | KVA | kVA Logical Circuit 43 | AI900 | kVA | 1 | Instantaneous Apparent Power - Ckt 43
44 | A | R |  | 4365 | 6270 | 6271 | 1085 | KVA | kVA Logical Circuit 44 | AI901 | kVA | 1 | Instantaneous Apparent Power - Ckt 44
45 | A | R |  | 4366 | 6272 | 6273 | 1086 | KVA | kVA Logical Circuit 45 | AI902 | kVA | 1 | Instantaneous Apparent Power - Ckt 45
46 | A | R |  | 4367 | 6274 | 6275 | 1087 | KVA | kVA Logical Circuit 46 | AI903 | kVA | 1 | Instantaneous Apparent Power - Ckt 46
1 | A | R |  | 4368 | 6276 | 6277 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 1 | AI904 | No-Units | 5 | Instantaneous Power Factor - Ckt 1
2 | A | R |  | 4369 | 6278 | 6279 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 2 | AI905 | No-Units | 5 | Instantaneous Power Factor - Ckt 2
3 | A | R |  | 4370 | 6280 | 6281 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 3 | AI906 | No-Units | 5 | Instantaneous Power Factor - Ckt 3
4 | A | R |  | 4371 | 6282 | 6283 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 4 | AI907 | No-Units | 5 | Instantaneous Power Factor - Ckt 4
5 | A | R |  | 4372 | 6284 | 6285 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 5 | AI908 | No-Units | 5 | Instantaneous Power Factor - Ckt 5
6 | A | R |  | 4373 | 6286 | 6287 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 6 | AI909 | No-Units | 5 | Instantaneous Power Factor - Ckt 6
7 | A | R |  | 4374 | 6288 | 6289 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 7 | AI910 | No-Units | 5 | Instantaneous Power Factor - Ckt 7
8 | A | R |  | 4375 | 6290 | 6291 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 8 | AI911 | No-Units | 5 | Instantaneous Power Factor - Ckt 8
9 | A | R |  | 4376 | 6292 | 6293 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 9 | AI912 | No-Units | 5 | Instantaneous Power Factor - Ckt 9
10 | A | R |  | 4377 | 6294 | 6295 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 10 | AI913 | No-Units | 5 | Instantaneous Power Factor - Ckt 10
11 | A | R |  | 4378 | 6296 | 6297 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 11 | AI914 | No-Units | 5 | Instantaneous Power Factor - Ckt 11
12 | A | R |  | 4379 | 6298 | 6299 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 12 | AI915 | No-Units | 5 | Instantaneous Power Factor - Ckt 12
13 | A | R |  | 4380 | 6300 | 6301 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 13 | AI916 | No-Units | 5 | Instantaneous Power Factor - Ckt 13
14 | A | R |  | 4381 | 6302 | 6303 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 14 | AI917 | No-Units | 5 | Instantaneous Power Factor - Ckt 14
15 | A | R |  | 4382 | 6304 | 6305 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 15 | AI918 | No-Units | 5 | Instantaneous Power Factor - Ckt 15
16 | A | R |  | 4383 | 6306 | 6307 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 16 | AI919 | No-Units | 5 | Instantaneous Power Factor - Ckt 16
17 | A | R |  | 4384 | 6308 | 6309 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 17 | AI920 | No-Units | 5 | Instantaneous Power Factor - Ckt 17
18 | A | R |  | 4385 | 6310 | 6311 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 18 | AI921 | No-Units | 5 | Instantaneous Power Factor - Ckt 18
19 | A | R |  | 4386 | 6312 | 6313 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 19 | AI922 | No-Units | 5 | Instantaneous Power Factor - Ckt 19
20 | A | R |  | 4387 | 6314 | 6315 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 20 | AI923 | No-Units | 5 | Instantaneous Power Factor - Ckt 20
21 | A | R |  | 4388 | 6316 | 6317 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 21 | AI924 | No-Units | 5 | Instantaneous Power Factor - Ckt 21
22 | A | R |  | 4389 | 6318 | 6319 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 22 | AI925 | No-Units | 5 | Instantaneous Power Factor - Ckt 22
23 | A | R |  | 4390 | 6320 | 6321 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 23 | AI926 | No-Units | 5 | Instantaneous Power Factor - Ckt 23
24 | A | R |  | 4391 | 6322 | 6323 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 24 | AI927 | No-Units | 5 | Instantaneous Power Factor - Ckt 24
25 | A | R |  | 4392 | 6324 | 6325 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 25 | AI928 | No-Units | 5 | Instantaneous Power Factor - Ckt 25
26 | A | R |  | 4393 | 6326 | 6327 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 26 | AI929 | No-Units | 5 | Instantaneous Power Factor - Ckt 26
27 | A | R |  | 4394 | 6328 | 6329 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 27 | AI930 | No-Units | 5 | Instantaneous Power Factor - Ckt 27
28 | A | R |  | 4395 | 6330 | 6331 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 28 | AI931 | No-Units | 5 | Instantaneous Power Factor - Ckt 28
29 | A | R |  | 4396 | 6332 | 6333 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 29 | AI932 | No-Units | 5 | Instantaneous Power Factor - Ckt 29
30 | A | R |  | 4397 | 6334 | 6335 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 30 | AI933 | No-Units | 5 | Instantaneous Power Factor - Ckt 30
31 | A | R |  | 4398 | 6336 | 6337 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 31 | AI934 | No-Units | 5 | Instantaneous Power Factor - Ckt 31
32 | A | R |  | 4399 | 6338 | 6339 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 32 | AI935 | No-Units | 5 | Instantaneous Power Factor - Ckt 32
33 | A | R |  | 4400 | 6340 | 6341 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 33 | AI936 | No-Units | 5 | Instantaneous Power Factor - Ckt 33
34 | A | R |  | 4401 | 6342 | 6343 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 34 | AI937 | No-Units | 5 | Instantaneous Power Factor - Ckt 34
35 | A | R |  | 4402 | 6344 | 6345 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 35 | AI938 | No-Units | 5 | Instantaneous Power Factor - Ckt 35
36 | A | R |  | 4403 | 6346 | 6347 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 36 | AI939 | No-Units | 5 | Instantaneous Power Factor - Ckt 36
37 | A | R |  | 4404 | 6348 | 6349 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 37 | AI940 | No-Units | 5 | Instantaneous Power Factor - Ckt 37
38 | A | R |  | 4405 | 6350 | 6351 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 38 | AI941 | No-Units | 5 | Instantaneous Power Factor - Ckt 38
39 | A | R |  | 4406 | 6352 | 6353 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 39 | AI942 | No-Units | 5 | Instantaneous Power Factor - Ckt 39
40 | A | R |  | 4407 | 6354 | 6355 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 40 | AI943 | No-Units | 5 | Instantaneous Power Factor - Ckt 40
41 | A | R |  | 4408 | 6356 | 6357 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 41 | AI944 | No-Units | 5 | Instantaneous Power Factor - Ckt 41
42 | A | R |  | 4409 | 6358 | 6359 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 42 | AI945 | No-Units | 5 | Instantaneous Power Factor - Ckt 42
43 | A | R |  | 4410 | 6360 | 6361 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 43 | AI946 | No-Units | 5 | Instantaneous Power Factor - Ckt 43
44 | A | R |  | 4411 | 6362 | 6363 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 44 | AI947 | No-Units | 5 | Instantaneous Power Factor - Ckt 44
45 | A | R |  | 4412 | 6364 | 6365 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 45 | AI948 | No-Units | 5 | Instantaneous Power Factor - Ckt 45
46 | A | R |  | 4413 | 6366 | 6367 | -3 | PF (+ for leading, - for lagging) | Power Factor Logical Circuit 46 | AI949 | No-Units | 5 | Instantaneous Power Factor - Ckt 46
1 | A,B,C | R |  | 4414 | 6368 | 6369 | 1000 | Current | Amps (Average) Logical Circuit 1 | AI950 | Amperes | 5 | Instantaneous Current - Circuit 1
2 | A,B,C | R |  | 4415 | 6370 | 6371 | 1001 | Current | Amps (Average) Logical Circuit 2 | AI951 | Amperes | 5 | Instantaneous Current - Circuit 2
3 | A,B,C | R |  | 4416 | 6372 | 6373 | 1002 | Current | Amps (Average) Logical Circuit 3 | AI952 | Amperes | 5 | Instantaneous Current - Circuit 3
4 | A,B,C | R |  | 4417 | 6374 | 6375 | 1003 | Current | Amps (Average) Logical Circuit 4 | AI953 | Amperes | 5 | Instantaneous Current - Circuit 4
5 | A,B,C | R |  | 4418 | 6376 | 6377 | 1004 | Current | Amps (Average) Logical Circuit 5 | AI954 | Amperes | 5 | Instantaneous Current - Circuit 5
6 | A,B,C | R |  | 4419 | 6378 | 6379 | 1005 | Current | Amps (Average) Logical Circuit 6 | AI955 | Amperes | 5 | Instantaneous Current - Circuit 6
7 | A,B,C | R |  | 4420 | 6380 | 6381 | 1006 | Current | Amps (Average) Logical Circuit 7 | AI956 | Amperes | 5 | Instantaneous Current - Circuit 7
8 | A,B,C | R |  | 4421 | 6382 | 6383 | 1007 | Current | Amps (Average) Logical Circuit 8 | AI957 | Amperes | 5 | Instantaneous Current - Circuit 8
9 | A,B,C | R |  | 4422 | 6384 | 6385 | 1008 | Current | Amps (Average) Logical Circuit 9 | AI958 | Amperes | 5 | Instantaneous Current - Circuit 9
10 | A,B,C | R |  | 4423 | 6386 | 6387 | 1009 | Current | Amps (Average) Logical Circuit 10 | AI959 | Amperes | 5 | Instantaneous Current - Circuit 10
11 | A,B,C | R |  | 4424 | 6388 | 6389 | 1010 | Current | Amps (Average) Logical Circuit 11 | AI960 | Amperes | 5 | Instantaneous Current - Circuit 11
12 | A,B,C | R |  | 4425 | 6390 | 6391 | 1011 | Current | Amps (Average) Logical Circuit 12 | AI961 | Amperes | 5 | Instantaneous Current - Circuit 12
13 | A,B,C | R |  | 4426 | 6392 | 6393 | 1012 | Current | Amps (Average) Logical Circuit 13 | AI962 | Amperes | 5 | Instantaneous Current - Circuit 13
14 | A,B,C | R |  | 4427 | 6394 | 6395 | 1013 | Current | Amps (Average) Logical Circuit 14 | AI963 | Amperes | 5 | Instantaneous Current - Circuit 14
15 | A,B,C | R |  | 4428 | 6396 | 6397 | 1014 | Current | Amps (Average) Logical Circuit 15 | AI964 | Amperes | 5 | Instantaneous Current - Circuit 15
16 | A,B,C | R |  | 4429 | 6398 | 6399 | 1015 | Current | Amps (Average) Logical Circuit 16 | AI965 | Amperes | 5 | Instantaneous Current - Circuit 16
17 | A,B,C | R |  | 4430 | 6400 | 6401 | 1016 | Current | Amps (Average) Logical Circuit 17 | AI966 | Amperes | 5 | Instantaneous Current - Circuit 17
18 | A,B,C | R |  | 4431 | 6402 | 6403 | 1017 | Current | Amps (Average) Logical Circuit 18 | AI967 | Amperes | 5 | Instantaneous Current - Circuit 18
19 | A,B,C | R |  | 4432 | 6404 | 6405 | 1018 | Current | Amps (Average) Logical Circuit 19 | AI968 | Amperes | 5 | Instantaneous Current - Circuit 19
20 | A,B,C | R |  | 4433 | 6406 | 6407 | 1019 | Current | Amps (Average) Logical Circuit 20 | AI969 | Amperes | 5 | Instantaneous Current - Circuit 20
21 | A,B,C | R |  | 4434 | 6408 | 6409 | 1020 | Current | Amps (Average) Logical Circuit 21 | AI970 | Amperes | 5 | Instantaneous Current - Circuit 21
22 | A,B,C | R |  | 4435 | 6410 | 6411 | 1021 | Current | Amps (Average) Logical Circuit 22 | AI971 | Amperes | 5 | Instantaneous Current - Circuit 22
23 | A,B,C | R |  | 4436 | 6412 | 6413 | 1022 | Current | Amps (Average) Logical Circuit 23 | AI972 | Amperes | 5 | Instantaneous Current - Circuit 23
24 | A,B,C | R |  | 4437 | 6414 | 6415 | 1023 | Current | Amps (Average) Logical Circuit 24 | AI973 | Amperes | 5 | Instantaneous Current - Circuit 24
25 | A,B,C | R |  | 4438 | 6416 | 6417 | 1024 | Current | Amps (Average) Logical Circuit 25 | AI974 | Amperes | 5 | Instantaneous Current - Circuit 25
26 | A,B,C | R |  | 4439 | 6418 | 6419 | 1025 | Current | Amps (Average) Logical Circuit 26 | AI975 | Amperes | 5 | Instantaneous Current - Circuit 26
27 | A,B,C | R |  | 4440 | 6420 | 6421 | 1026 | Current | Amps (Average) Logical Circuit 27 | AI976 | Amperes | 5 | Instantaneous Current - Circuit 27
28 | A,B,C | R |  | 4441 | 6422 | 6423 | 1027 | Current | Amps (Average) Logical Circuit 28 | AI977 | Amperes | 5 | Instantaneous Current - Circuit 28
29 | A,B,C | R |  | 4442 | 6424 | 6425 | 1028 | Current | Amps (Average) Logical Circuit 29 | AI978 | Amperes | 5 | Instantaneous Current - Circuit 29
30 | A,B,C | R |  | 4443 | 6426 | 6427 | 1029 | Current | Amps (Average) Logical Circuit 30 | AI979 | Amperes | 5 | Instantaneous Current - Circuit 30
31 | A,B,C | R |  | 4444 | 6428 | 6429 | 1030 | Current | Amps (Average) Logical Circuit 31 | AI980 | Amperes | 5 | Instantaneous Current - Circuit 31
32 | A,B,C | R |  | 4445 | 6430 | 6431 | 1031 | Current | Amps (Average) Logical Circuit 32 | AI981 | Amperes | 5 | Instantaneous Current - Circuit 32
33 | A,B,C | R |  | 4446 | 6432 | 6433 | 1032 | Current | Amps (Average) Logical Circuit 33 | AI982 | Amperes | 5 | Instantaneous Current - Circuit 33
34 | A,B,C | R |  | 4447 | 6434 | 6435 | 1033 | Current | Amps (Average) Logical Circuit 34 | AI983 | Amperes | 5 | Instantaneous Current - Circuit 34
35 | A,B,C | R |  | 4448 | 6436 | 6437 | 1034 | Current | Amps (Average) Logical Circuit 35 | AI984 | Amperes | 5 | Instantaneous Current - Circuit 35
36 | A,B,C | R |  | 4449 | 6438 | 6439 | 1035 | Current | Amps (Average) Logical Circuit 36 | AI985 | Amperes | 5 | Instantaneous Current - Circuit 36
37 | A,B,C | R |  | 4450 | 6440 | 6441 | 1036 | Current | Amps (Average) Logical Circuit 37 | AI986 | Amperes | 5 | Instantaneous Current - Circuit 37
38 | A,B,C | R |  | 4451 | 6442 | 6443 | 1037 | Current | Amps (Average) Logical Circuit 38 | AI987 | Amperes | 5 | Instantaneous Current - Circuit 38
39 | A,B,C | R |  | 4452 | 6444 | 6445 | 1038 | Current | Amps (Average) Logical Circuit 39 | AI988 | Amperes | 5 | Instantaneous Current - Circuit 39
40 | A,B,C | R |  | 4453 | 6446 | 6447 | 1039 | Current | Amps (Average) Logical Circuit 40 | AI989 | Amperes | 5 | Instantaneous Current - Circuit 40
41 | A,B,C | R |  | 4454 | 6448 | 6449 | 1040 | Current | Amps (Average) Logical Circuit 41 | AI990 | Amperes | 5 | Instantaneous Current - Circuit 41
42 | A,B,C | R |  | 4455 | 6450 | 6451 | 1041 | Current | Amps (Average) Logical Circuit 42 | AI991 | Amperes | 5 | Instantaneous Current - Circuit 42
43 | A,B,C | R |  | 4456 | 6452 | 6453 | 1042 | Current | Amps (Average) Logical Circuit 43 | AI992 | Amperes | 5 | Instantaneous Current - Circuit 43
44 | A,B,C | R |  | 4457 | 6454 | 6455 | 1043 | Current | Amps (Average) Logical Circuit 44 | AI993 | Amperes | 5 | Instantaneous Current - Circuit 44
45 | A,B,C | R |  | 4458 | 6456 | 6457 | 1044 | Current | Amps (Average) Logical Circuit 45 | AI994 | Amperes | 5 | Instantaneous Current - Circuit 45
46 | A,B,C | R |  | 4459 | 6458 | 6459 | 1045 | Current | Amps (Average) Logical Circuit 46 | AI995 | Amperes | 5 | Instantaneous Current - Circuit 46
1 | A | R |  | 4460 | 6460 | 6461 | 1042 | Present KW Demand | kW Present Demand Logical Circuit 1 | AI996 | kW | 1 | Present Real Power Demand - Ckt 1
2 | A | R |  | 4461 | 6462 | 6463 | 1043 | Present KW Demand | kW Present Demand Logical Circuit 2 | AI997 | kW | 1 | Present Real Power Demand - Ckt 2
3 | A | R |  | 4462 | 6464 | 6465 | 1044 | Present KW Demand | kW Present Demand Logical Circuit 3 | AI998 | kW | 1 | Present Real Power Demand - Ckt 3
4 | A | R |  | 4463 | 6466 | 6467 | 1045 | Present KW Demand | kW Present Demand Logical Circuit 4 | AI999 | kW | 1 | Present Real Power Demand - Ckt 4
5 | A | R |  | 4464 | 6468 | 6469 | 1046 | Present KW Demand | kW Present Demand Logical Circuit 5 | AI1000 | kW | 1 | Present Real Power Demand - Ckt 5
6 | A | R |  | 4465 | 6470 | 6471 | 1047 | Present KW Demand | kW Present Demand Logical Circuit 6 | AI1001 | kW | 1 | Present Real Power Demand - Ckt 6
7 | A | R |  | 4466 | 6472 | 6473 | 1048 | Present KW Demand | kW Present Demand Logical Circuit 7 | AI1002 | kW | 1 | Present Real Power Demand - Ckt 7
8 | A | R |  | 4467 | 6474 | 6475 | 1049 | Present KW Demand | kW Present Demand Logical Circuit 8 | AI1003 | kW | 1 | Present Real Power Demand - Ckt 8
9 | A | R |  | 4468 | 6476 | 6477 | 1050 | Present KW Demand | kW Present Demand Logical Circuit 9 | AI1004 | kW | 1 | Present Real Power Demand - Ckt 9
10 | A | R |  | 4469 | 6478 | 6479 | 1051 | Present KW Demand | kW Present Demand Logical Circuit 10 | AI1005 | kW | 1 | Present Real Power Demand - Ckt 10
11 | A | R |  | 4470 | 6480 | 6481 | 1052 | Present KW Demand | kW Present Demand Logical Circuit 11 | AI1006 | kW | 1 | Present Real Power Demand - Ckt 11
12 | A | R |  | 4471 | 6482 | 6483 | 1053 | Present KW Demand | kW Present Demand Logical Circuit 12 | AI1007 | kW | 1 | Present Real Power Demand - Ckt 12
13 | A | R |  | 4472 | 6484 | 6485 | 1054 | Present KW Demand | kW Present Demand Logical Circuit 13 | AI1008 | kW | 1 | Present Real Power Demand - Ckt 13
14 | A | R |  | 4473 | 6486 | 6487 | 1055 | Present KW Demand | kW Present Demand Logical Circuit 14 | AI1009 | kW | 1 | Present Real Power Demand - Ckt 14
15 | A | R |  | 4474 | 6488 | 6489 | 1056 | Present KW Demand | kW Present Demand Logical Circuit 15 | AI1010 | kW | 1 | Present Real Power Demand - Ckt 15
16 | A | R |  | 4475 | 6490 | 6491 | 1057 | Present KW Demand | kW Present Demand Logical Circuit 16 | AI1011 | kW | 1 | Present Real Power Demand - Ckt 16
17 | A | R |  | 4476 | 6492 | 6493 | 1058 | Present KW Demand | kW Present Demand Logical Circuit 17 | AI1012 | kW | 1 | Present Real Power Demand - Ckt 17
18 | A | R |  | 4477 | 6494 | 6495 | 1059 | Present KW Demand | kW Present Demand Logical Circuit 18 | AI1013 | kW | 1 | Present Real Power Demand - Ckt 18
19 | A | R |  | 4478 | 6496 | 6497 | 1060 | Present KW Demand | kW Present Demand Logical Circuit 19 | AI1014 | kW | 1 | Present Real Power Demand - Ckt 19
20 | A | R |  | 4479 | 6498 | 6499 | 1061 | Present KW Demand | kW Present Demand Logical Circuit 20 | AI1015 | kW | 1 | Present Real Power Demand - Ckt 20
21 | A | R |  | 4480 | 6500 | 6501 | 1062 | Present KW Demand | kW Present Demand Logical Circuit 21 | AI1016 | kW | 1 | Present Real Power Demand - Ckt 21
22 | A | R |  | 4481 | 6502 | 6503 | 1063 | Present KW Demand | kW Present Demand Logical Circuit 22 | AI1017 | kW | 1 | Present Real Power Demand - Ckt 22
23 | A | R |  | 4482 | 6504 | 6505 | 1064 | Present KW Demand | kW Present Demand Logical Circuit 23 | AI1018 | kW | 1 | Present Real Power Demand - Ckt 23
24 | A | R |  | 4483 | 6506 | 6507 | 1065 | Present KW Demand | kW Present Demand Logical Circuit 24 | AI1019 | kW | 1 | Present Real Power Demand - Ckt 24
25 | A | R |  | 4484 | 6508 | 6509 | 1066 | Present KW Demand | kW Present Demand Logical Circuit 25 | AI1020 | kW | 1 | Present Real Power Demand - Ckt 25
26 | A | R |  | 4485 | 6510 | 6511 | 1067 | Present KW Demand | kW Present Demand Logical Circuit 26 | AI1021 | kW | 1 | Present Real Power Demand - Ckt 26
27 | A | R |  | 4486 | 6512 | 6513 | 1068 | Present KW Demand | kW Present Demand Logical Circuit 27 | AI1022 | kW | 1 | Present Real Power Demand - Ckt 27
28 | A | R |  | 4487 | 6514 | 6515 | 1069 | Present KW Demand | kW Present Demand Logical Circuit 28 | AI1023 | kW | 1 | Present Real Power Demand - Ckt 28
29 | A | R |  | 4488 | 6516 | 6517 | 1070 | Present KW Demand | kW Present Demand Logical Circuit 29 | AI1024 | kW | 1 | Present Real Power Demand - Ckt 29
30 | A | R |  | 4489 | 6518 | 6519 | 1071 | Present KW Demand | kW Present Demand Logical Circuit 30 | AI1025 | kW | 1 | Present Real Power Demand - Ckt 30
31 | A | R |  | 4490 | 6520 | 6521 | 1072 | Present KW Demand | kW Present Demand Logical Circuit 31 | AI1026 | kW | 1 | Present Real Power Demand - Ckt 31
32 | A | R |  | 4491 | 6522 | 6523 | 1073 | Present KW Demand | kW Present Demand Logical Circuit 32 | AI1027 | kW | 1 | Present Real Power Demand - Ckt 32
33 | A | R |  | 4492 | 6524 | 6525 | 1074 | Present KW Demand | kW Present Demand Logical Circuit 33 | AI1028 | kW | 1 | Present Real Power Demand - Ckt 33
34 | A | R |  | 4493 | 6526 | 6527 | 1075 | Present KW Demand | kW Present Demand Logical Circuit 34 | AI1029 | kW | 1 | Present Real Power Demand - Ckt 34
35 | A | R |  | 4494 | 6528 | 6529 | 1076 | Present KW Demand | kW Present Demand Logical Circuit 35 | AI1030 | kW | 1 | Present Real Power Demand - Ckt 35
36 | A | R |  | 4495 | 6530 | 6531 | 1077 | Present KW Demand | kW Present Demand Logical Circuit 36 | AI1031 | kW | 1 | Present Real Power Demand - Ckt 36
37 | A | R |  | 4496 | 6532 | 6533 | 1078 | Present KW Demand | kW Present Demand Logical Circuit 37 | AI1032 | kW | 1 | Present Real Power Demand - Ckt 37
38 | A | R |  | 4497 | 6534 | 6535 | 1079 | Present KW Demand | kW Present Demand Logical Circuit 38 | AI1033 | kW | 1 | Present Real Power Demand - Ckt 38
39 | A | R |  | 4498 | 6536 | 6537 | 1080 | Present KW Demand | kW Present Demand Logical Circuit 39 | AI1034 | kW | 1 | Present Real Power Demand - Ckt 39
40 | A | R |  | 4499 | 6538 | 6539 | 1081 | Present KW Demand | kW Present Demand Logical Circuit 40 | AI1035 | kW | 1 | Present Real Power Demand - Ckt 40
41 | A | R |  | 4500 | 6540 | 6541 | 1082 | Present KW Demand | kW Present Demand Logical Circuit 41 | AI1036 | kW | 1 | Present Real Power Demand - Ckt 41
42 | A | R |  | 4501 | 6542 | 6543 | 1083 | Present KW Demand | kW Present Demand Logical Circuit 42 | AI1037 | kW | 1 | Present Real Power Demand - Ckt 42
43 | A | R |  | 4502 | 6544 | 6545 | 1084 | Present KW Demand | kW Present Demand Logical Circuit 43 | AI1038 | kW | 1 | Present Real Power Demand - Ckt 43
44 | A | R |  | 4503 | 6546 | 6547 | 1085 | Present KW Demand | kW Present Demand Logical Circuit 44 | AI1039 | kW | 1 | Present Real Power Demand - Ckt 44
45 | A | R |  | 4504 | 6548 | 6549 | 1086 | Present KW Demand | kW Present Demand Logical Circuit 45 | AI1040 | kW | 1 | Present Real Power Demand - Ckt 45
46 | A | R |  | 4505 | 6550 | 6551 | 1087 | Present KW Demand | kW Present Demand Logical Circuit 46 | AI1041 | kW | 1 | Present Real Power Demand - Ckt 46
1 | A | R | NV | 4506 | 6552 | 6553 | 1042 | Max KW Demand | kW Max Demand Logical Circuit 1 | AI1042 | kW | 1 | Max Real Power Demand - Circuit 1
2 | A | R | NV | 4507 | 6554 | 6555 | 1043 | Max KW Demand | kW Max Demand Logical Circuit 2 | AI1043 | kW | 1 | Max Real Power Demand - Circuit 2
3 | A | R | NV | 4508 | 6556 | 6557 | 1044 | Max KW Demand | kW Max Demand Logical Circuit 3 | AI1044 | kW | 1 | Max Real Power Demand - Circuit 3
4 | A | R | NV | 4509 | 6558 | 6559 | 1045 | Max KW Demand | kW Max Demand Logical Circuit 4 | AI1045 | kW | 1 | Max Real Power Demand - Circuit 4
5 | A | R | NV | 4510 | 6560 | 6561 | 1046 | Max KW Demand | kW Max Demand Logical Circuit 5 | AI1046 | kW | 1 | Max Real Power Demand - Circuit 5
6 | A | R | NV | 4511 | 6562 | 6563 | 1047 | Max KW Demand | kW Max Demand Logical Circuit 6 | AI1047 | kW | 1 | Max Real Power Demand - Circuit 6
7 | A | R | NV | 4512 | 6564 | 6565 | 1048 | Max KW Demand | kW Max Demand Logical Circuit 7 | AI1048 | kW | 1 | Max Real Power Demand - Circuit 7
8 | A | R | NV | 4513 | 6566 | 6567 | 1049 | Max KW Demand | kW Max Demand Logical Circuit 8 | AI1049 | kW | 1 | Max Real Power Demand - Circuit 8
9 | A | R | NV | 4514 | 6568 | 6569 | 1050 | Max KW Demand | kW Max Demand Logical Circuit 9 | AI1050 | kW | 1 | Max Real Power Demand - Circuit 9
10 | A | R | NV | 4515 | 6570 | 6571 | 1051 | Max KW Demand | kW Max Demand Logical Circuit 10 | AI1051 | kW | 1 | Max Real Power Demand - Circuit 10
11 | A | R | NV | 4516 | 6572 | 6573 | 1052 | Max KW Demand | kW Max Demand Logical Circuit 11 | AI1052 | kW | 1 | Max Real Power Demand - Circuit 11
12 | A | R | NV | 4517 | 6574 | 6575 | 1053 | Max KW Demand | kW Max Demand Logical Circuit 12 | AI1053 | kW | 1 | Max Real Power Demand - Circuit 12
13 | A | R | NV | 4518 | 6576 | 6577 | 1054 | Max KW Demand | kW Max Demand Logical Circuit 13 | AI1054 | kW | 1 | Max Real Power Demand - Circuit 13
14 | A | R | NV | 4519 | 6578 | 6579 | 1055 | Max KW Demand | kW Max Demand Logical Circuit 14 | AI1055 | kW | 1 | Max Real Power Demand - Circuit 14
15 | A | R | NV | 4520 | 6580 | 6581 | 1056 | Max KW Demand | kW Max Demand Logical Circuit 15 | AI1056 | kW | 1 | Max Real Power Demand - Circuit 15
16 | A | R | NV | 4521 | 6582 | 6583 | 1057 | Max KW Demand | kW Max Demand Logical Circuit 16 | AI1057 | kW | 1 | Max Real Power Demand - Circuit 16
17 | A | R | NV | 4522 | 6584 | 6585 | 1058 | Max KW Demand | kW Max Demand Logical Circuit 17 | AI1058 | kW | 1 | Max Real Power Demand - Circuit 17
18 | A | R | NV | 4523 | 6586 | 6587 | 1059 | Max KW Demand | kW Max Demand Logical Circuit 18 | AI1059 | kW | 1 | Max Real Power Demand - Circuit 18
19 | A | R | NV | 4524 | 6588 | 6589 | 1060 | Max KW Demand | kW Max Demand Logical Circuit 19 | AI1060 | kW | 1 | Max Real Power Demand - Circuit 19
20 | A | R | NV | 4525 | 6590 | 6591 | 1061 | Max KW Demand | kW Max Demand Logical Circuit 20 | AI1061 | kW | 1 | Max Real Power Demand - Circuit 20
21 | A | R | NV | 4526 | 6592 | 6593 | 1062 | Max KW Demand | kW Max Demand Logical Circuit 21 | AI1062 | kW | 1 | Max Real Power Demand - Circuit 21
22 | A | R | NV | 4527 | 6594 | 6595 | 1063 | Max KW Demand | kW Max Demand Logical Circuit 22 | AI1063 | kW | 1 | Max Real Power Demand - Circuit 22
23 | A | R | NV | 4528 | 6596 | 6597 | 1064 | Max KW Demand | kW Max Demand Logical Circuit 23 | AI1064 | kW | 1 | Max Real Power Demand - Circuit 23
24 | A | R | NV | 4529 | 6598 | 6599 | 1065 | Max KW Demand | kW Max Demand Logical Circuit 24 | AI1065 | kW | 1 | Max Real Power Demand - Circuit 24
25 | A | R | NV | 4530 | 6600 | 6601 | 1066 | Max KW Demand | kW Max Demand Logical Circuit 25 | AI1066 | kW | 1 | Max Real Power Demand - Circuit 25
26 | A | R | NV | 4531 | 6602 | 6603 | 1067 | Max KW Demand | kW Max Demand Logical Circuit 26 | AI1067 | kW | 1 | Max Real Power Demand - Circuit 26
27 | A | R | NV | 4532 | 6604 | 6605 | 1068 | Max KW Demand | kW Max Demand Logical Circuit 27 | AI1068 | kW | 1 | Max Real Power Demand - Circuit 27
28 | A | R | NV | 4533 | 6606 | 6607 | 1069 | Max KW Demand | kW Max Demand Logical Circuit 28 | AI1069 | kW | 1 | Max Real Power Demand - Circuit 28
29 | A | R | NV | 4534 | 6608 | 6609 | 1070 | Max KW Demand | kW Max Demand Logical Circuit 29 | AI1070 | kW | 1 | Max Real Power Demand - Circuit 29
30 | A | R | NV | 4535 | 6610 | 6611 | 1071 | Max KW Demand | kW Max Demand Logical Circuit 30 | AI1071 | kW | 1 | Max Real Power Demand - Circuit 30
31 | A | R | NV | 4536 | 6612 | 6613 | 1072 | Max KW Demand | kW Max Demand Logical Circuit 31 | AI1072 | kW | 1 | Max Real Power Demand - Circuit 31
32 | A | R | NV | 4537 | 6614 | 6615 | 1073 | Max KW Demand | kW Max Demand Logical Circuit 32 | AI1073 | kW | 1 | Max Real Power Demand - Circuit 32
33 | A | R | NV | 4538 | 6616 | 6617 | 1074 | Max KW Demand | kW Max Demand Logical Circuit 33 | AI1074 | kW | 1 | Max Real Power Demand - Circuit 33
34 | A | R | NV | 4539 | 6618 | 6619 | 1075 | Max KW Demand | kW Max Demand Logical Circuit 34 | AI1075 | kW | 1 | Max Real Power Demand - Circuit 34
35 | A | R | NV | 4540 | 6620 | 6621 | 1076 | Max KW Demand | kW Max Demand Logical Circuit 35 | AI1076 | kW | 1 | Max Real Power Demand - Circuit 35
36 | A | R | NV | 4541 | 6622 | 6623 | 1077 | Max KW Demand | kW Max Demand Logical Circuit 36 | AI1077 | kW | 1 | Max Real Power Demand - Circuit 36
37 | A | R | NV | 4542 | 6624 | 6625 | 1078 | Max KW Demand | kW Max Demand Logical Circuit 37 | AI1078 | kW | 1 | Max Real Power Demand - Circuit 37
38 | A | R | NV | 4543 | 6626 | 6627 | 1079 | Max KW Demand | kW Max Demand Logical Circuit 38 | AI1079 | kW | 1 | Max Real Power Demand - Circuit 38
39 | A | R | NV | 4544 | 6628 | 6629 | 1080 | Max KW Demand | kW Max Demand Logical Circuit 39 | AI1080 | kW | 1 | Max Real Power Demand - Circuit 39
40 | A | R | NV | 4545 | 6630 | 6631 | 1081 | Max KW Demand | kW Max Demand Logical Circuit 40 | AI1081 | kW | 1 | Max Real Power Demand - Circuit 40
41 | A | R | NV | 4546 | 6632 | 6633 | 1082 | Max KW Demand | kW Max Demand Logical Circuit 41 | AI1082 | kW | 1 | Max Real Power Demand - Circuit 41
42 | A | R | NV | 4547 | 6634 | 6635 | 1083 | Max KW Demand | kW Max Demand Logical Circuit 42 | AI1083 | kW | 1 | Max Real Power Demand - Circuit 42
43 | A | R | NV | 4548 | 6636 | 6637 | 1084 | Max KW Demand | kW Max Demand Logical Circuit 43 | AI1084 | kW | 1 | Max Real Power Demand - Circuit 43
44 | A | R | NV | 4549 | 6638 | 6639 | 1085 | Max KW Demand | kW Max Demand Logical Circuit 44 | AI1085 | kW | 1 | Max Real Power Demand - Circuit 44
45 | A | R | NV | 4550 | 6640 | 6641 | 1086 | Max KW Demand | kW Max Demand Logical Circuit 45 | AI1086 | kW | 1 | Max Real Power Demand - Circuit 45
46 | A | R | NV | 4551 | 6642 | 6643 | 1087 | Max KW Demand | kW Max Demand Logical Circuit 46 | AI1087 | kW | 1 | Max Real Power Demand - Circuit 46
1 | A,B,C | R |  | 4552 | 6644 | 6645 | 1000 | Present Current Demand
2 | A,B,C | R |  | 4553 | 6646 | 6647 | 1001 | Present Current Demand
3 | A,B,C | R |  | 4554 | 6648 | 6649 | 1002 | Present Current Demand
4 | A,B,C | R |  | 4555 | 6650 | 6651 | 1003 | Present Current Demand
5 | A,B,C | R |  | 4556 | 6652 | 6653 | 1004 | Present Current Demand
6 | A,B,C | R |  | 4557 | 6654 | 6655 | 1005 | Present Current Demand
7 | A,B,C | R |  | 4558 | 6656 | 6657 | 1006 | Present Current Demand
8 | A,B,C | R |  | 4559 | 6658 | 6659 | 1007 | Present Current Demand
9 | A,B,C | R |  | 4560 | 6660 | 6661 | 1008 | Present Current Demand
10 | A,B,C | R |  | 4561 | 6662 | 6663 | 1009 | Present Current Demand
11 | A,B,C | R |  | 4562 | 6664 | 6665 | 1010 | Present Current Demand
12 | A,B,C | R |  | 4563 | 6666 | 6667 | 1011 | Present Current Demand
13 | A,B,C | R |  | 4564 | 6668 | 6669 | 1012 | Present Current Demand
14 | A,B,C | R |  | 4565 | 6670 | 6671 | 1013 | Present Current Demand
15 | A,B,C | R |  | 4566 | 6672 | 6673 | 1014 | Present Current Demand
16 | A,B,C | R |  | 4567 | 6674 | 6675 | 1015 | Present Current Demand
17 | A,B,C | R |  | 4568 | 6676 | 6677 | 1016 | Present Current Demand
18 | A,B,C | R |  | 4569 | 6678 | 6679 | 1017 | Present Current Demand
19 | A,B,C | R |  | 4570 | 6680 | 6681 | 1018 | Present Current Demand
20 | A,B,C | R |  | 4571 | 6682 | 6683 | 1019 | Present Current Demand
21 | A,B,C | R |  | 4572 | 6684 | 6685 | 1020 | Present Current Demand
22 | A,B,C | R |  | 4573 | 6686 | 6687 | 1021 | Present Current Demand
23 | A,B,C | R |  | 4574 | 6688 | 6689 | 1022 | Present Current Demand
24 | A,B,C | R |  | 4575 | 6690 | 6691 | 1023 | Present Current Demand
25 | A,B,C | R |  | 4576 | 6692 | 6693 | 1024 | Present Current Demand
26 | A,B,C | R |  | 4577 | 6694 | 6695 | 1025 | Present Current Demand
27 | A,B,C | R |  | 4578 | 6696 | 6697 | 1026 | Present Current Demand
28 | A,B,C | R |  | 4579 | 6698 | 6699 | 1027 | Present Current Demand
29 | A,B,C | R |  | 4580 | 6700 | 6701 | 1028 | Present Current Demand
30 | A,B,C | R |  | 4581 | 6702 | 6703 | 1029 | Present Current Demand
31 | A,B,C | R |  | 4582 | 6704 | 6705 | 1030 | Present Current Demand
32 | A,B,C | R |  | 4583 | 6706 | 6707 | 1031 | Present Current Demand
33 | A,B,C | R |  | 4584 | 6708 | 6709 | 1032 | Present Current Demand
34 | A,B,C | R |  | 4585 | 6710 | 6711 | 1033 | Present Current Demand
35 | A,B,C | R |  | 4586 | 6712 | 6713 | 1034 | Present Current Demand
36 | A,B,C | R |  | 4587 | 6714 | 6715 | 1035 | Present Current Demand
37 | A,B,C | R |  | 4588 | 6716 | 6717 | 1036 | Present Current Demand
38 | A,B,C | R |  | 4589 | 6718 | 6719 | 1037 | Present Current Demand
39 | A,B,C | R |  | 4590 | 6720 | 6721 | 1038 | Present Current Demand
40 | A,B,C | R |  | 4591 | 6722 | 6723 | 1039 | Present Current Demand
41 | A,B,C | R |  | 4592 | 6724 | 6725 | 1040 | Present Current Demand
42 | A,B,C | R |  | 4593 | 6726 | 6727 | 1041 | Present Current Demand
43 | A,B,C | R |  | 4594 | 6728 | 6729 | 1042 | Present Current Demand
44 | A,B,C | R |  | 4595 | 6730 | 6731 | 1043 | Present Current Demand
45 | A,B,C | R |  | 4596 | 6732 | 6733 | 1044 | Present Current Demand
46 | A,B,C | R |  | 4597 | 6734 | 6735 | 1045 | Present Current Demand
1 | A,B,C | R | NV | 4598 | 6736 | 6737 | 1000 | Max Current Demand
2 | A,B,C | R | NV | 4599 | 6738 | 6739 | 1001 | Max Current Demand
3 | A,B,C | R | NV | 4600 | 6740 | 6741 | 1002 | Max Current Demand
4 | A,B,C | R | NV | 4601 | 6742 | 6743 | 1003 | Max Current Demand
5 | A,B,C | R | NV | 4602 | 6744 | 6745 | 1004 | Max Current Demand
6 | A,B,C | R | NV | 4603 | 6746 | 6747 | 1005 | Max Current Demand
7 | A,B,C | R | NV | 4604 | 6748 | 6749 | 1006 | Max Current Demand
8 | A,B,C | R | NV | 4605 | 6750 | 6751 | 1007 | Max Current Demand
9 | A,B,C | R | NV | 4606 | 6752 | 6753 | 1008 | Max Current Demand
10 | A,B,C | R | NV | 4607 | 6754 | 6755 | 1009 | Max Current Demand
11 | A,B,C | R | NV | 4608 | 6756 | 6757 | 1010 | Max Current Demand
12 | A,B,C | R | NV | 4609 | 6758 | 6759 | 1011 | Max Current Demand
13 | A,B,C | R | NV | 4610 | 6760 | 6761 | 1012 | Max Current Demand
14 | A,B,C | R | NV | 4611 | 6762 | 6763 | 1013 | Max Current Demand
15 | A,B,C | R | NV | 4612 | 6764 | 6765 | 1014 | Max Current Demand
16 | A,B,C | R | NV | 4613 | 6766 | 6767 | 1015 | Max Current Demand
17 | A,B,C | R | NV | 4614 | 6768 | 6769 | 1016 | Max Current Demand
18 | A,B,C | R | NV | 4615 | 6770 | 6771 | 1017 | Max Current Demand
19 | A,B,C | R | NV | 4616 | 6772 | 6773 | 1018 | Max Current Demand
20 | A,B,C | R | NV | 4617 | 6774 | 6775 | 1019 | Max Current Demand
21 | A,B,C | R | NV | 4618 | 6776 | 6777 | 1020 | Max Current Demand
22 | A,B,C | R | NV | 4619 | 6778 | 6779 | 1021 | Max Current Demand
23 | A,B,C | R | NV | 4620 | 6780 | 6781 | 1022 | Max Current Demand
24 | A,B,C | R | NV | 4621 | 6782 | 6783 | 1023 | Max Current Demand
25 | A,B,C | R | NV | 4622 | 6784 | 6785 | 1024 | Max Current Demand
26 | A,B,C | R | NV | 4623 | 6786 | 6787 | 1025 | Max Current Demand
27 | A,B,C | R | NV | 4624 | 6788 | 6789 | 1026 | Max Current Demand
28 | A,B,C | R | NV | 4625 | 6790 | 6791 | 1027 | Max Current Demand
29 | A,B,C | R | NV | 4626 | 6792 | 6793 | 1028 | Max Current Demand
30 | A,B,C | R | NV | 4627 | 6794 | 6795 | 1029 | Max Current Demand
31 | A,B,C | R | NV | 4628 | 6796 | 6797 | 1030 | Max Current Demand
32 | A,B,C | R | NV | 4629 | 6798 | 6799 | 1031 | Max Current Demand
33 | A,B,C | R | NV | 4630 | 6800 | 6801 | 1032 | Max Current Demand
34 | A,B,C | R | NV | 4631 | 6802 | 6803 | 1033 | Max Current Demand
35 | A,B,C | R | NV | 4632 | 6804 | 6805 | 1034 | Max Current Demand
36 | A,B,C | R | NV | 4633 | 6806 | 6807 | 1035 | Max Current Demand
37 | A,B,C | R | NV | 4634 | 6808 | 6809 | 1036 | Max Current Demand
38 | A,B,C | R | NV | 4635 | 6810 | 6811 | 1037 | Max Current Demand
39 | A,B,C | R | NV | 4636 | 6812 | 6813 | 1038 | Max Current Demand
40 | A,B,C | R | NV | 4637 | 6814 | 6815 | 1039 | Max Current Demand
41 | A,B,C | R | NV | 4638 | 6816 | 6817 | 1040 | Max Current Demand
42 | A,B,C | R | NV | 4639 | 6818 | 6819 | 1041 | Max Current Demand
43 | A,B,C | R | NV | 4640 | 6820 | 6821 | 1042 | Max Current Demand
44 | A,B,C | R | NV | 4641 | 6822 | 6823 | 1043 | Max Current Demand
45 | A,B,C | R | NV | 4642 | 6824 | 6825 | 1044 | Max Current Demand
46 | A,B,C | R | NV | 4643 | 6826 | 6827 | 1045 | Max Current Demand
1 | A | R | NV | 4644 | 6828 | 6829 | 1042 | Max KW | kW Max Logical Circuit 1 | AI1088 | kW | 1 | Max Instantaneous Real Power - Ckt 1
2 | A | R | NV | 4645 | 6830 | 6831 | 1043 | Max KW | kW Max Logical Circuit 2 | AI1089 | kW | 1 | Max Instantaneous Real Power - Ckt 2
3 | A | R | NV | 4646 | 6832 | 6833 | 1044 | Max KW | kW Max Logical Circuit 3 | AI1090 | kW | 1 | Max Instantaneous Real Power - Ckt 3
4 | A | R | NV | 4647 | 6834 | 6835 | 1045 | Max KW | kW Max Logical Circuit 4 | AI1091 | kW | 1 | Max Instantaneous Real Power - Ckt 4
5 | A | R | NV | 4648 | 6836 | 6837 | 1046 | Max KW | kW Max Logical Circuit 5 | AI1092 | kW | 1 | Max Instantaneous Real Power - Ckt 5
6 | A | R | NV | 4649 | 6838 | 6839 | 1047 | Max KW | kW Max Logical Circuit 6 | AI1093 | kW | 1 | Max Instantaneous Real Power - Ckt 6
7 | A | R | NV | 4650 | 6840 | 6841 | 1048 | Max KW | kW Max Logical Circuit 7 | AI1094 | kW | 1 | Max Instantaneous Real Power - Ckt 7
8 | A | R | NV | 4651 | 6842 | 6843 | 1049 | Max KW | kW Max Logical Circuit 8 | AI1095 | kW | 1 | Max Instantaneous Real Power - Ckt 8
9 | A | R | NV | 4652 | 6844 | 6845 | 1050 | Max KW | kW Max Logical Circuit 9 | AI1096 | kW | 1 | Max Instantaneous Real Power - Ckt 9
10 | A | R | NV | 4653 | 6846 | 6847 | 1051 | Max KW | kW Max Logical Circuit 10 | AI1097 | kW | 1 | Max Instantaneous Real Power - Ckt 10
11 | A | R | NV | 4654 | 6848 | 6849 | 1052 | Max KW | kW Max Logical Circuit 11 | AI1098 | kW | 1 | Max Instantaneous Real Power - Ckt 11
12 | A | R | NV | 4655 | 6850 | 6851 | 1053 | Max KW | kW Max Logical Circuit 12 | AI1099 | kW | 1 | Max Instantaneous Real Power - Ckt 12
13 | A | R | NV | 4656 | 6852 | 6853 | 1054 | Max KW | kW Max Logical Circuit 13 | AI1100 | kW | 1 | Max Instantaneous Real Power - Ckt 13
14 | A | R | NV | 4657 | 6854 | 6855 | 1055 | Max KW | kW Max Logical Circuit 14 | AI1101 | kW | 1 | Max Instantaneous Real Power - Ckt 14
15 | A | R | NV | 4658 | 6856 | 6857 | 1056 | Max KW | kW Max Logical Circuit 15 | AI1102 | kW | 1 | Max Instantaneous Real Power - Ckt 15
16 | A | R | NV | 4659 | 6858 | 6859 | 1057 | Max KW | kW Max Logical Circuit 16 | AI1103 | kW | 1 | Max Instantaneous Real Power - Ckt 16
17 | A | R | NV | 4660 | 6860 | 6861 | 1058 | Max KW | kW Max Logical Circuit 17 | AI1104 | kW | 1 | Max Instantaneous Real Power - Ckt 17
18 | A | R | NV | 4661 | 6862 | 6863 | 1059 | Max KW | kW Max Logical Circuit 18 | AI1105 | kW | 1 | Max Instantaneous Real Power - Ckt 18
19 | A | R | NV | 4662 | 6864 | 6865 | 1060 | Max KW | kW Max Logical Circuit 19 | AI1106 | kW | 1 | Max Instantaneous Real Power - Ckt 19
20 | A | R | NV | 4663 | 6866 | 6867 | 1061 | Max KW | kW Max Logical Circuit 20 | AI1107 | kW | 1 | Max Instantaneous Real Power - Ckt 20
21 | A | R | NV | 4664 | 6868 | 6869 | 1062 | Max KW | kW Max Logical Circuit 21 | AI1108 | kW | 1 | Max Instantaneous Real Power - Ckt 21
22 | A | R | NV | 4665 | 6870 | 6871 | 1063 | Max KW | kW Max Logical Circuit 22 | AI1109 | kW | 1 | Max Instantaneous Real Power - Ckt 22
23 | A | R | NV | 4666 | 6872 | 6873 | 1064 | Max KW | kW Max Logical Circuit 23 | AI1110 | kW | 1 | Max Instantaneous Real Power - Ckt 23
24 | A | R | NV | 4667 | 6874 | 6875 | 1065 | Max KW | kW Max Logical Circuit 24 | AI1111 | kW | 1 | Max Instantaneous Real Power - Ckt 24
25 | A | R | NV | 4668 | 6876 | 6877 | 1066 | Max KW | kW Max Logical Circuit 25 | AI1112 | kW | 1 | Max Instantaneous Real Power - Ckt 25
26 | A | R | NV | 4669 | 6878 | 6879 | 1067 | Max KW | kW Max Logical Circuit 26 | AI1113 | kW | 1 | Max Instantaneous Real Power - Ckt 26
27 | A | R | NV | 4670 | 6880 | 6881 | 1068 | Max KW | kW Max Logical Circuit 27 | AI1114 | kW | 1 | Max Instantaneous Real Power - Ckt 27
28 | A | R | NV | 4671 | 6882 | 6883 | 1069 | Max KW | kW Max Logical Circuit 28 | AI1115 | kW | 1 | Max Instantaneous Real Power - Ckt 28
29 | A | R | NV | 4672 | 6884 | 6885 | 1070 | Max KW | kW Max Logical Circuit 29 | AI1116 | kW | 1 | Max Instantaneous Real Power - Ckt 29
30 | A | R | NV | 4673 | 6886 | 6887 | 1071 | Max KW | kW Max Logical Circuit 30 | AI1117 | kW | 1 | Max Instantaneous Real Power - Ckt 30
31 | A | R | NV | 4674 | 6888 | 6889 | 1072 | Max KW | kW Max Logical Circuit 31 | AI1118 | kW | 1 | Max Instantaneous Real Power - Ckt 31
32 | A | R | NV | 4675 | 6890 | 6891 | 1073 | Max KW | kW Max Logical Circuit 32 | AI1119 | kW | 1 | Max Instantaneous Real Power - Ckt 32
33 | A | R | NV | 4676 | 6892 | 6893 | 1074 | Max KW | kW Max Logical Circuit 33 | AI1120 | kW | 1 | Max Instantaneous Real Power - Ckt 33
34 | A | R | NV | 4677 | 6894 | 6895 | 1075 | Max KW | kW Max Logical Circuit 34 | AI1121 | kW | 1 | Max Instantaneous Real Power - Ckt 34
35 | A | R | NV | 4678 | 6896 | 6897 | 1076 | Max KW | kW Max Logical Circuit 35 | AI1122 | kW | 1 | Max Instantaneous Real Power - Ckt 35
36 | A | R | NV | 4679 | 6898 | 6899 | 1077 | Max KW | kW Max Logical Circuit 36 | AI1123 | kW | 1 | Max Instantaneous Real Power - Ckt 36
37 | A | R | NV | 4680 | 6900 | 6901 | 1078 | Max KW | kW Max Logical Circuit 37 | AI1124 | kW | 1 | Max Instantaneous Real Power - Ckt 37
38 | A | R | NV | 4681 | 6902 | 6903 | 1079 | Max KW | kW Max Logical Circuit 38 | AI1125 | kW | 1 | Max Instantaneous Real Power - Ckt 38
39 | A | R | NV | 4682 | 6904 | 6905 | 1080 | Max KW | kW Max Logical Circuit 39 | AI1126 | kW | 1 | Max Instantaneous Real Power - Ckt 39
40 | A | R | NV | 4683 | 6906 | 6907 | 1081 | Max KW | kW Max Logical Circuit 40 | AI1127 | kW | 1 | Max Instantaneous Real Power - Ckt 40
41 | A | R | NV | 4684 | 6908 | 6909 | 1082 | Max KW | kW Max Logical Circuit 41 | AI1128 | kW | 1 | Max Instantaneous Real Power - Ckt 41
42 | A | R | NV | 4685 | 6910 | 6911 | 1083 | Max KW | kW Max Logical Circuit 42 | AI1129 | kW | 1 | Max Instantaneous Real Power - Ckt 42
43 | A | R | NV | 4686 | 6912 | 6913 | 1084 | Max KW | kW Max Logical Circuit 43 | AI1130 | kW | 1 | Max Instantaneous Real Power - Ckt 43
44 | A | R | NV | 4687 | 6914 | 6915 | 1085 | Max KW | kW Max Logical Circuit 44 | AI1131 | kW | 1 | Max Instantaneous Real Power - Ckt 44
45 | A | R | NV | 4688 | 6916 | 6917 | 1086 | Max KW | kW Max Logical Circuit 45 | AI1132 | kW | 1 | Max Instantaneous Real Power - Ckt 45
46 | A | R | NV | 4689 | 6918 | 6919 | 1087 | Max KW | kW Max Logical Circuit 46 | AI1133 | kW | 1 | Max Instantaneous Real Power - Ckt 46
1 | A,B,C | R | NV | 4690 | 6920 | 6921 | 1000 | Max Current
2 | A,B,C | R | NV | 4691 | 6922 | 6923 | 1001 | Max Current
3 | A,B,C | R | NV | 4692 | 6924 | 6925 | 1002 | Max Current
4 | A,B,C | R | NV | 4693 | 6926 | 6927 | 1003 | Max Current
5 | A,B,C | R | NV | 4694 | 6928 | 6929 | 1004 | Max Current
6 | A,B,C | R | NV | 4695 | 6930 | 6931 | 1005 | Max Current
7 | A,B,C | R | NV | 4696 | 6932 | 6933 | 1006 | Max Current
8 | A,B,C | R | NV | 4697 | 6934 | 6935 | 1007 | Max Current
9 | A,B,C | R | NV | 4698 | 6936 | 6937 | 1008 | Max Current
10 | A,B,C | R | NV | 4699 | 6938 | 6939 | 1009 | Max Current
11 | A,B,C | R | NV | 4700 | 6940 | 6941 | 1010 | Max Current
12 | A,B,C | R | NV | 4701 | 6942 | 6943 | 1011 | Max Current
13 | A,B,C | R | NV | 4702 | 6944 | 6945 | 1012 | Max Current
14 | A,B,C | R | NV | 4703 | 6946 | 6947 | 1013 | Max Current
15 | A,B,C | R | NV | 4704 | 6948 | 6949 | 1014 | Max Current
16 | A,B,C | R | NV | 4705 | 6950 | 6951 | 1015 | Max Current
17 | A,B,C | R | NV | 4706 | 6952 | 6953 | 1016 | Max Current
18 | A,B,C | R | NV | 4707 | 6954 | 6955 | 1017 | Max Current
19 | A,B,C | R | NV | 4708 | 6956 | 6957 | 1018 | Max Current
20 | A,B,C | R | NV | 4709 | 6958 | 6959 | 1019 | Max Current
21 | A,B,C | R | NV | 4710 | 6960 | 6961 | 1020 | Max Current
22 | A,B,C | R | NV | 4711 | 6962 | 6963 | 1021 | Max Current
23 | A,B,C | R | NV | 4712 | 6964 | 6965 | 1022 | Max Current
24 | A,B,C | R | NV | 4713 | 6966 | 6967 | 1023 | Max Current
25 | A,B,C | R | NV | 4714 | 6968 | 6969 | 1024 | Max Current
26 | A,B,C | R | NV | 4715 | 6970 | 6971 | 1025 | Max Current
27 | A,B,C | R | NV | 4716 | 6972 | 6973 | 1026 | Max Current
28 | A,B,C | R | NV | 4717 | 6974 | 6975 | 1027 | Max Current
29 | A,B,C | R | NV | 4718 | 6976 | 6977 | 1028 | Max Current
30 | A,B,C | R | NV | 4719 | 6978 | 6979 | 1029 | Max Current
31 | A,B,C | R | NV | 4720 | 6980 | 6981 | 1030 | Max Current
32 | A,B,C | R | NV | 4721 | 6982 | 6983 | 1031 | Max Current
33 | A,B,C | R | NV | 4722 | 6984 | 6985 | 1032 | Max Current
34 | A,B,C | R | NV | 4723 | 6986 | 6987 | 1033 | Max Current
35 | A,B,C | R | NV | 4724 | 6988 | 6989 | 1034 | Max Current
36 | A,B,C | R | NV | 4725 | 6990 | 6991 | 1035 | Max Current
37 | A,B,C | R | NV | 4726 | 6992 | 6993 | 1036 | Max Current
38 | A,B,C | R | NV | 4727 | 6994 | 6995 | 1037 | Max Current
39 | A,B,C | R | NV | 4728 | 6996 | 6997 | 1038 | Max Current
40 | A,B,C | R | NV | 4729 | 6998 | 6999 | 1039 | Max Current
41 | A,B,C | R | NV | 4730 | 7000 | 7001 | 1040 | Max Current
42 | A,B,C | R | NV | 4731 | 7002 | 7003 | 1041 | Max Current
43 | A,B,C | R | NV | 4732 | 7004 | 7005 | 1042 | Max Current
44 | A,B,C | R | NV | 4733 | 7006 | 7007 | 1043 | Max Current
45 | A,B,C | R | NV | 4734 | 7008 | 7009 | 1044 | Max Current
46 | A,B,C | R | NV | 4735 | 7010 | 7011 | 1045 | Max Current
1 | A,B,C | R |  | 4736 | 7012 | 7013 |  | Reserved for future use
2 | A,B,C | R |  | 4737 | 7014 | 7015 |  | Reserved for future use
3 | A,B,C | R |  | 4738 | 7016 | 7017 |  | Reserved for future use
4 | A,B,C | R |  | 4739 | 7018 | 7019 |  | Reserved for future use
5 | A,B,C | R |  | 4740 | 7020 | 7021 |  | Reserved for future use
6 | A,B,C | R |  | 4741 | 7022 | 7023 |  | Reserved for future use
7 | A,B,C | R |  | 4742 | 7024 | 7025 |  | Reserved for future use
8 | A,B,C | R |  | 4743 | 7026 | 7027 |  | Reserved for future use
9 | A,B,C | R |  | 4744 | 7028 | 7029 |  | Reserved for future use
10 | A,B,C | R |  | 4745 | 7030 | 7031 |  | Reserved for future use
11 | A,B,C | R |  | 4746 | 7032 | 7033 |  | Reserved for future use
12 | A,B,C | R |  | 4747 | 7034 | 7035 |  | Reserved for future use
13 | A,B,C | R |  | 4748 | 7036 | 7037 |  | Reserved for future use
14 | A,B,C | R |  | 4749 | 7038 | 7039 |  | Reserved for future use
15 | A,B,C | R |  | 4750 | 7040 | 7041 |  | Reserved for future use
16 | A,B,C | R |  | 4751 | 7042 | 7043 |  | Reserved for future use
17 | A,B,C | R |  | 4752 | 7044 | 7045 |  | Reserved for future use
18 | A,B,C | R |  | 4753 | 7046 | 7047 |  | Reserved for future use
19 | A,B,C | R |  | 4754 | 7048 | 7049 |  | Reserved for future use
20 | A,B,C | R |  | 4755 | 7050 | 7051 |  | Reserved for future use
21 | A,B,C | R |  | 4756 | 7052 | 7053 |  | Reserved for future use
22 | A,B,C | R |  | 4757 | 7054 | 7055 |  | Reserved for future use
23 | A,B,C | R |  | 4758 | 7056 | 7057 |  | Reserved for future use
24 | A,B,C | R |  | 4759 | 7058 | 7059 |  | Reserved for future use
25 | A,B,C | R |  | 4760 | 7060 | 7061 |  | Reserved for future use
26 | A,B,C | R |  | 4761 | 7062 | 7063 |  | Reserved for future use
27 | A,B,C | R |  | 4762 | 7064 | 7065 |  | Reserved for future use
28 | A,B,C | R |  | 4763 | 7066 | 7067 |  | Reserved for future use
29 | A,B,C | R |  | 4764 | 7068 | 7069 |  | Reserved for future use
30 | A,B,C | R |  | 4765 | 7070 | 7071 |  | Reserved for future use
31 | A,B,C | R |  | 4766 | 7072 | 7073 |  | Reserved for future use
32 | A,B,C | R |  | 4767 | 7074 | 7075 |  | Reserved for future use
33 | A,B,C | R |  | 4768 | 7076 | 7077 |  | Reserved for future use
34 | A,B,C | R |  | 4769 | 7078 | 7079 |  | Reserved for future use
35 | A,B,C | R |  | 4770 | 7080 | 7081 |  | Reserved for future use
36 | A,B,C | R |  | 4771 | 7082 | 7083 |  | Reserved for future use
37 | A,B,C | R |  | 4772 | 7084 | 7085 |  | Reserved for future use
38 | A,B,C | R |  | 4773 | 7086 | 7087 |  | Reserved for future use
39 | A,B,C | R |  | 4774 | 7088 | 7089 |  | Reserved for future use
40 | A,B,C | R |  | 4775 | 7090 | 7091 |  | Reserved for future use
41 | A,B,C | R |  | 4776 | 7092 | 7093 |  | Reserved for future use
42 | A,B,C | R |  | 4777 | 7094 | 7095 |  | Reserved for future use
43 | A,B,C | R |  | 4778 | 7096 | 7097 |  | Reserved for future use
44 | A,B,C | R |  | 4779 | 7098 | 7099 |  | Reserved for future use
45 | A,B,C | R |  | 4780 | 7100 | 7101 |  | Reserved for future use
46 | A,B,C | R |  | 4781 | 7102 | 7103 |  | Reserved for future use
1 | A | R |  | 4782 | 7104 | 7105 | 1084 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 1 | AI1134 | kWh | 0 | Energy Snapshot Logical Circuit 1
1 | A | R |  | 4783 |  |  |  | KWH Snapshot (LSW)
2 | A | R |  | 4784 | 7106 | 7107 | 1085 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 2 | AI1135 | kWh | 0 | Energy Snapshot Logical Circuit 2
2 | A | R |  | 4785 |  |  |  | KWH Snapshot (LSW)
3 | A | R |  | 4786 | 7108 | 7109 | 1086 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 3 | AI1136 | kWh | 0 | Energy Snapshot Logical Circuit 3
3 | A | R |  | 4787 |  |  |  | KWH Snapshot (LSW)
4 | A | R |  | 4788 | 7110 | 7111 | 1087 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 4 | AI1137 | kWh | 0 | Energy Snapshot Logical Circuit 4
4 | A | R |  | 4789 |  |  |  | KWH Snapshot (LSW)
5 | A | R |  | 4790 | 7112 | 7113 | 1088 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 5 | AI1138 | kWh | 0 | Energy Snapshot Logical Circuit 5
5 | A | R |  | 4791 |  |  |  | KWH Snapshot (LSW)
6 | A | R |  | 4792 | 7114 | 7115 | 1089 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 6 | AI1139 | kWh | 0 | Energy Snapshot Logical Circuit 6
6 | A | R |  | 4793 |  |  |  | KWH Snapshot (LSW)
7 | A | R |  | 4794 | 7116 | 7117 | 1090 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 7 | AI1140 | kWh | 0 | Energy Snapshot Logical Circuit 7
7 | A | R |  | 4795 |  |  |  | KWH Snapshot (LSW)
8 | A | R |  | 4796 | 7118 | 7119 | 1091 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 8 | AI1141 | kWh | 0 | Energy Snapshot Logical Circuit 8
8 | A | R |  | 4797 |  |  |  | KWH Snapshot (LSW)
9 | A | R |  | 4798 | 7120 | 7121 | 1092 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 9 | AI1142 | kWh | 0 | Energy Snapshot Logical Circuit 9
9 | A | R |  | 4799 |  |  |  | KWH Snapshot (LSW)
10 | A | R |  | 4800 | 7122 | 7123 | 1093 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 10 | AI1143 | kWh | 0 | Energy Snapshot Logical Circuit 10
10 | A | R |  | 4801 |  |  |  | KWH Snapshot (LSW)
11 | A | R |  | 4802 | 7124 | 7125 | 1094 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 11 | AI1144 | kWh | 0 | Energy Snapshot Logical Circuit 11
11 | A | R |  | 4803 |  |  |  | KWH Snapshot (LSW)
12 | A | R |  | 4804 | 7126 | 7127 | 1095 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 12 | AI1145 | kWh | 0 | Energy Snapshot Logical Circuit 12
12 | A | R |  | 4805 |  |  |  | KWH Snapshot (LSW)
13 | A | R |  | 4806 | 7128 | 7129 | 1096 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 13 | AI1146 | kWh | 0 | Energy Snapshot Logical Circuit 13
13 | A | R |  | 4807 |  |  |  | KWH Snapshot (LSW)
14 | A | R |  | 4808 | 7130 | 7131 | 1097 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 14 | AI1147 | kWh | 0 | Energy Snapshot Logical Circuit 14
14 | A | R |  | 4809 |  |  |  | KWH Snapshot (LSW)
15 | A | R |  | 4810 | 7132 | 7133 | 1098 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 15 | AI1148 | kWh | 0 | Energy Snapshot Logical Circuit 15
15 | A | R |  | 4811 |  |  |  | KWH Snapshot (LSW)
16 | A | R |  | 4812 | 7134 | 7135 | 1099 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 16 | AI1149 | kWh | 0 | Energy Snapshot Logical Circuit 16
16 | A | R |  | 4813 |  |  |  | KWH Snapshot (LSW)
17 | A | R |  | 4814 | 7136 | 7137 | 1100 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 17 | AI1150 | kWh | 0 | Energy Snapshot Logical Circuit 17
17 | A | R |  | 4815 |  |  |  | KWH Snapshot (LSW)
18 | A | R |  | 4816 | 7138 | 7139 | 1101 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 18 | AI1151 | kWh | 0 | Energy Snapshot Logical Circuit 18
18 | A | R |  | 4817 |  |  |  | KWH Snapshot (LSW)
19 | A | R |  | 4818 | 7140 | 7141 | 1102 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 19 | AI1152 | kWh | 0 | Energy Snapshot Logical Circuit 19
19 | A | R |  | 4819 |  |  |  | KWH Snapshot (LSW)
20 | A | R |  | 4820 | 7142 | 7143 | 1103 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 20 | AI1153 | kWh | 0 | Energy Snapshot Logical Circuit 20
20 | A | R |  | 4821 |  |  |  | KWH Snapshot (LSW)
21 | A | R |  | 4822 | 7144 | 7145 | 1104 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 21 | AI1154 | kWh | 0 | Energy Snapshot Logical Circuit 21
21 | A | R |  | 4823 |  |  |  | KWH Snapshot (LSW)
22 | A | R |  | 4824 | 7146 | 7147 | 1105 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 22 | AI1155 | kWh | 0 | Energy Snapshot Logical Circuit 22
22 | A | R |  | 4825 |  |  |  | KWH Snapshot (LSW)
23 | A | R |  | 4826 | 7148 | 7149 | 1106 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 23 | AI1156 | kWh | 0 | Energy Snapshot Logical Circuit 23
23 | A | R |  | 4827 |  |  |  | KWH Snapshot (LSW)
24 | A | R |  | 4828 | 7150 | 7151 | 1107 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 24 | AI1157 | kWh | 0 | Energy Snapshot Logical Circuit 24
24 | A | R |  | 4829 |  |  |  | KWH Snapshot (LSW)
25 | A | R |  | 4830 | 7152 | 7153 | 1108 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 25 | AI1158 | kWh | 0 | Energy Snapshot Logical Circuit 25
25 | A | R |  | 4831 |  |  |  | KWH Snapshot (LSW)
26 | A | R |  | 4832 | 7154 | 7155 | 1109 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 26 | AI1159 | kWh | 0 | Energy Snapshot Logical Circuit 26
26 | A | R |  | 4833 |  |  |  | KWH Snapshot (LSW)
27 | A | R |  | 4834 | 7156 | 7157 | 1110 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 27 | AI1160 | kWh | 0 | Energy Snapshot Logical Circuit 27
27 | A | R |  | 4835 |  |  |  | KWH Snapshot (LSW)
28 | A | R |  | 4836 | 7158 | 7159 | 1111 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 28 | AI1161 | kWh | 0 | Energy Snapshot Logical Circuit 28
28 | A | R |  | 4837 |  |  |  | KWH Snapshot (LSW)
29 | A | R |  | 4838 | 7160 | 7161 | 1112 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 29 | AI1162 | kWh | 0 | Energy Snapshot Logical Circuit 29
29 | A | R |  | 4839 |  |  |  | KWH Snapshot (LSW)
30 | A | R |  | 4840 | 7162 | 7163 | 1113 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 30 | AI1163 | kWh | 0 | Energy Snapshot Logical Circuit 30
30 | A | R |  | 4841 |  |  |  | KWH Snapshot (LSW)
31 | A | R |  | 4842 | 7164 | 7165 | 1114 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 31 | AI1164 | kWh | 0 | Energy Snapshot Logical Circuit 31
31 | A | R |  | 4843 |  |  |  | KWH Snapshot (LSW)
32 | A | R |  | 4844 | 7166 | 7167 | 1115 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 32 | AI1165 | kWh | 0 | Energy Snapshot Logical Circuit 32
32 | A | R |  | 4845 |  |  |  | KWH Snapshot (LSW)
33 | A | R |  | 4846 | 7168 | 7169 | 1116 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 33 | AI1166 | kWh | 0 | Energy Snapshot Logical Circuit 33
33 | A | R |  | 4847 |  |  |  | KWH Snapshot (LSW)
34 | A | R |  | 4848 | 7170 | 7171 | 1117 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 34 | AI1167 | kWh | 0 | Energy Snapshot Logical Circuit 34
34 | A | R |  | 4849 |  |  |  | KWH Snapshot (LSW)
35 | A | R |  | 4850 | 7172 | 7173 | 1118 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 35 | AI1168 | kWh | 0 | Energy Snapshot Logical Circuit 35
35 | A | R |  | 4851 |  |  |  | KWH Snapshot (LSW)
36 | A | R |  | 4852 | 7174 | 7175 | 1119 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 36 | AI1169 | kWh | 0 | Energy Snapshot Logical Circuit 36
36 | A | R |  | 4853 |  |  |  | KWH Snapshot (LSW)
37 | A | R |  | 4854 | 7176 | 7177 | 1120 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 37 | AI1170 | kWh | 0 | Energy Snapshot Logical Circuit 37
37 | A | R |  | 4855 |  |  |  | KWH Snapshot (LSW)
38 | A | R |  | 4856 | 7178 | 7179 | 1121 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 38 | AI1171 | kWh | 0 | Energy Snapshot Logical Circuit 38
38 | A | R |  | 4857 |  |  |  | KWH Snapshot (LSW)
39 | A | R |  | 4858 | 7180 | 7181 | 1122 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 39 | AI1172 | kWh | 0 | Energy Snapshot Logical Circuit 39
39 | A | R |  | 4859 |  |  |  | KWH Snapshot (LSW)
40 | A | R |  | 4860 | 7182 | 7183 | 1123 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 40 | AI1173 | kWh | 0 | Energy Snapshot Logical Circuit 40
40 | A | R |  | 4861 |  |  |  | KWH Snapshot (LSW)
41 | A | R |  | 4862 | 7184 | 7185 | 1124 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 41 | AI1174 | kWh | 0 | Energy Snapshot Logical Circuit 41
41 | A | R |  | 4863 |  |  |  | KWH Snapshot (LSW)
42 | A | R |  | 4864 | 7186 | 7187 | 1125 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 42 | AI1175 | kWh | 0 | Energy Snapshot Logical Circuit 42
42 | A | R |  | 4865 |  |  |  | KWH Snapshot (LSW)
43 | A | R |  | 4866 | 7188 | 7189 | 1126 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 43 | AI1176 | kWh | 0 | Energy Snapshot Logical Circuit 43
43 | A | R |  | 4867 |  |  |  | KWH Snapshot (LSW)
44 | A | R |  | 4868 | 7190 | 7191 | 1127 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 44 | AI1177 | kWh | 0 | Energy Snapshot Logical Circuit 44
44 | A | R |  | 4869 |  |  |  | KWH Snapshot (LSW)
45 | A | R |  | 4870 | 7192 | 7193 | 1128 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 45 | AI1178 | kWh | 0 | Energy Snapshot Logical Circuit 45
45 | A | R |  | 4871 |  |  |  | KWH Snapshot (LSW)
46 | A | R |  | 4872 | 7194 | 7195 | 1129 | KWH Snapshot (MSW) | kWh Snapshot Logical Circuit 46 | AI1179 | kWh | 0 | Energy Snapshot Logical Circuit 46
46 | A | R |  | 4873 |  |  |  | KWH Snapshot (LSW)
1 | A,B,C | R/W | NV | 4874 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 1 | AV255 | No-Units | 0 | Write 0 to alarm bits to clear alarms
Latching Alarms are cleared by writing a 0 to it's alarm bit.
A write to a Non-Latching alarm is ignored
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
2 | A,B,C | R/W | NV | 4875 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 2 | AV256 | No-Units | 0 | Write 0 to alarm bits to clear alarms
3 | A,B,C | R/W | NV | 4876 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 3 | AV257 | No-Units | 0 | Write 0 to alarm bits to clear alarms
4 | A,B,C | R/W | NV | 4877 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 4 | AV258 | No-Units | 0 | Write 0 to alarm bits to clear alarms
5 | A,B,C | R/W | NV | 4878 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 5 | AV259 | No-Units | 0 | Write 0 to alarm bits to clear alarms
6 | A,B,C | R/W | NV | 4879 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 6 | AV260 | No-Units | 0 | Write 0 to alarm bits to clear alarms
7 | A,B,C | R/W | NV | 4880 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 7 | AV261 | No-Units | 0 | Write 0 to alarm bits to clear alarms
8 | A,B,C | R/W | NV | 4881 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 8 | AV262 | No-Units | 0 | Write 0 to alarm bits to clear alarms
9 | A,B,C | R/W | NV | 4882 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 9 | AV263 | No-Units | 0 | Write 0 to alarm bits to clear alarms
10 | A,B,C | R/W | NV | 4883 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 10 | AV264 | No-Units | 0 | Write 0 to alarm bits to clear alarms
11 | A,B,C | R/W | NV | 4884 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 11 | AV265 | No-Units | 0 | Write 0 to alarm bits to clear alarms
12 | A,B,C | R/W | NV | 4885 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 12 | AV266 | No-Units | 0 | Write 0 to alarm bits to clear alarms
13 | A,B,C | R/W | NV | 4886 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 13 | AV267 | No-Units | 0 | Write 0 to alarm bits to clear alarms
14 | A,B,C | R/W | NV | 4887 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 14 | AV268 | No-Units | 0 | Write 0 to alarm bits to clear alarms
15 | A,B,C | R/W | NV | 4888 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 15 | AV269 | No-Units | 0 | Write 0 to alarm bits to clear alarms
16 | A,B,C | R/W | NV | 4889 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 16 | AV270 | No-Units | 0 | Write 0 to alarm bits to clear alarms
17 | A,B,C | R/W | NV | 4890 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 17 | AV271 | No-Units | 0 | Write 0 to alarm bits to clear alarms
18 | A,B,C | R/W | NV | 4891 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 18 | AV272 | No-Units | 0 | Write 0 to alarm bits to clear alarms
19 | A,B,C | R/W | NV | 4892 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 19 | AV273 | No-Units | 0 | Write 0 to alarm bits to clear alarms
20 | A,B,C | R/W | NV | 4893 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 20 | AV274 | No-Units | 0 | Write 0 to alarm bits to clear alarms
21 | A,B,C | R/W | NV | 4894 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 21 | AV275 | No-Units | 0 | Write 0 to alarm bits to clear alarms
22 | A,B,C | R/W | NV | 4895 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 22 | AV276 | No-Units | 0 | Write 0 to alarm bits to clear alarms
23 | A,B,C | R/W | NV | 4896 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 23 | AV277 | No-Units | 0 | Write 0 to alarm bits to clear alarms
24 | A,B,C | R/W | NV | 4897 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 24 | AV278 | No-Units | 0 | Write 0 to alarm bits to clear alarms
25 | A,B,C | R/W | NV | 4898 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 25 | AV279 | No-Units | 0 | Write 0 to alarm bits to clear alarms
26 | A,B,C | R/W | NV | 4899 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 26 | AV280 | No-Units | 0 | Write 0 to alarm bits to clear alarms
27 | A,B,C | R/W | NV | 4900 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 27 | AV281 | No-Units | 0 | Write 0 to alarm bits to clear alarms
28 | A,B,C | R/W | NV | 4901 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 28 | AV282 | No-Units | 0 | Write 0 to alarm bits to clear alarms
29 | A,B,C | R/W | NV | 4902 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 29 | AV283 | No-Units | 0 | Write 0 to alarm bits to clear alarms
30 | A,B,C | R/W | NV | 4903 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 30 | AV284 | No-Units | 0 | Write 0 to alarm bits to clear alarms
31 | A,B,C | R/W | NV | 4904 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 31 | AV285 | No-Units | 0 | Write 0 to alarm bits to clear alarms
32 | A,B,C | R/W | NV | 4905 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 32 | AV286 | No-Units | 0 | Write 0 to alarm bits to clear alarms
33 | A,B,C | R/W | NV | 4906 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 33 | AV287 | No-Units | 0 | Write 0 to alarm bits to clear alarms
34 | A,B,C | R/W | NV | 4907 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 34 | AV288 | No-Units | 0 | Write 0 to alarm bits to clear alarms
35 | A,B,C | R/W | NV | 4908 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 35 | AV289 | No-Units | 0 | Write 0 to alarm bits to clear alarms
36 | A,B,C | R/W | NV | 4909 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 36 | AV290 | No-Units | 0 | Write 0 to alarm bits to clear alarms
37 | A,B,C | R/W | NV | 4910 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 37 | AV291 | No-Units | 0 | Write 0 to alarm bits to clear alarms
38 | A,B,C | R/W | NV | 4911 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 38 | AV292 | No-Units | 0 | Write 0 to alarm bits to clear alarms
39 | A,B,C | R/W | NV | 4912 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 39 | AV293 | No-Units | 0 | Write 0 to alarm bits to clear alarms
40 | A,B,C | R/W | NV | 4913 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 30 | AV294 | No-Units | 0 | Write 0 to alarm bits to clear alarms
41 | A,B,C | R/W | NV | 4914 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 41 | AV295 | No-Units | 0 | Write 0 to alarm bits to clear alarms
42 | A,B,C | R/W | NV | 4915 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 42 | AV296 | No-Units | 0 | Write 0 to alarm bits to clear alarms
43 | A,B,C | R/W | NV | 4916 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 43 | AV297 | No-Units | 0 | Write 0 to alarm bits to clear alarms
44 | A,B,C | R/W | NV | 4917 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 44 | AV298 | No-Units | 0 | Write 0 to alarm bits to clear alarms
45 | A,B,C | R/W | NV | 4918 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 45 | AV299 | No-Units | 0 | Write 0 to alarm bits to clear alarms
46 | A,B,C | R/W | NV | 4919 |  |  |  | Alarm Status Latching | Latching Alarm Status: Logical Ckt 46 | AV300 | No-Units | 0 | Write 0 to alarm bits to clear alarms
1 | A,B,C | R/W | NV | 4920 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 1 | AI536 | No-Units | 0 | Status Bitmap
Latching Alarms are cleared by writing a 0 to it's alarm bit.
A write to a Non-Latching alarm is ignored
Bit 0: Reserved for High High Non-Latching Alarm (reads 0)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
2 | A,B,C | R/W | NV | 4921 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 2 | AI537 | No-Units | 0 | Status Bitmap
3 | A,B,C | R/W | NV | 4922 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 3 | AI538 | No-Units | 0 | Status Bitmap
4 | A,B,C | R/W | NV | 4923 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 4 | AI539 | No-Units | 0 | Status Bitmap
5 | A,B,C | R/W | NV | 4924 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 5 | AI540 | No-Units | 0 | Status Bitmap
6 | A,B,C | R/W | NV | 4925 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 6 | AI541 | No-Units | 0 | Status Bitmap
7 | A,B,C | R/W | NV | 4926 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 7 | AI542 | No-Units | 0 | Status Bitmap
8 | A,B,C | R/W | NV | 4927 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 8 | AI543 | No-Units | 0 | Status Bitmap
9 | A,B,C | R/W | NV | 4928 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 9 | AI544 | No-Units | 0 | Status Bitmap
10 | A,B,C | R/W | NV | 4929 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 10 | AI545 | No-Units | 0 | Status Bitmap
11 | A,B,C | R/W | NV | 4930 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 11 | AI546 | No-Units | 0 | Status Bitmap
12 | A,B,C | R/W | NV | 4931 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 12 | AI547 | No-Units | 0 | Status Bitmap
13 | A,B,C | R/W | NV | 4932 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 13 | AI548 | No-Units | 0 | Status Bitmap
14 | A,B,C | R/W | NV | 4933 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 14 | AI549 | No-Units | 0 | Status Bitmap
15 | A,B,C | R/W | NV | 4934 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 15 | AI550 | No-Units | 0 | Status Bitmap
16 | A,B,C | R/W | NV | 4935 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 16 | AI551 | No-Units | 0 | Status Bitmap
17 | A,B,C | R/W | NV | 4936 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 17 | AI552 | No-Units | 0 | Status Bitmap
18 | A,B,C | R/W | NV | 4937 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 18 | AI553 | No-Units | 0 | Status Bitmap
19 | A,B,C | R/W | NV | 4938 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 19 | AI554 | No-Units | 0 | Status Bitmap
20 | A,B,C | R/W | NV | 4939 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 20 | AI555 | No-Units | 0 | Status Bitmap
21 | A,B,C | R/W | NV | 4940 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 21 | AI556 | No-Units | 0 | Status Bitmap
22 | A,B,C | R/W | NV | 4941 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 22 | AI557 | No-Units | 0 | Status Bitmap
23 | A,B,C | R/W | NV | 4942 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 23 | AI558 | No-Units | 0 | Status Bitmap
24 | A,B,C | R/W | NV | 4943 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 24 | AI559 | No-Units | 0 | Status Bitmap
25 | A,B,C | R/W | NV | 4944 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 25 | AI560 | No-Units | 0 | Status Bitmap
26 | A,B,C | R/W | NV | 4945 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 26 | AI561 | No-Units | 0 | Status Bitmap
27 | A,B,C | R/W | NV | 4946 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 27 | AI562 | No-Units | 0 | Status Bitmap
28 | A,B,C | R/W | NV | 4947 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 28 | AI563 | No-Units | 0 | Status Bitmap
29 | A,B,C | R/W | NV | 4948 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 29 | AI564 | No-Units | 0 | Status Bitmap
30 | A,B,C | R/W | NV | 4949 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 30 | AI565 | No-Units | 0 | Status Bitmap
31 | A,B,C | R/W | NV | 4950 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 31 | AI566 | No-Units | 0 | Status Bitmap
32 | A,B,C | R/W | NV | 4951 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 32 | AI567 | No-Units | 0 | Status Bitmap
33 | A,B,C | R/W | NV | 4952 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 33 | AI568 | No-Units | 0 | Status Bitmap
34 | A,B,C | R/W | NV | 4953 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 34 | AI569 | No-Units | 0 | Status Bitmap
35 | A,B,C | R/W | NV | 4954 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 35 | AI570 | No-Units | 0 | Status Bitmap
36 | A,B,C | R/W | NV | 4955 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 36 | AI571 | No-Units | 0 | Status Bitmap
37 | A,B,C | R/W | NV | 4956 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 37 | AI572 | No-Units | 0 | Status Bitmap
38 | A,B,C | R/W | NV | 4957 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 38 | AI573 | No-Units | 0 | Status Bitmap
39 | A,B,C | R/W | NV | 4958 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 39 | AI574 | No-Units | 0 | Status Bitmap
40 | A,B,C | R/W | NV | 4959 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 30 | AI575 | No-Units | 0 | Status Bitmap
41 | A,B,C | R/W | NV | 4960 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 41 | AI576 | No-Units | 0 | Status Bitmap
42 | A,B,C | R/W | NV | 4961 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 42 | AI577 | No-Units | 0 | Status Bitmap
43 | A,B,C | R/W | NV | 4962 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 43 | AI578 | No-Units | 0 | Status Bitmap
44 | A,B,C | R/W | NV | 4963 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 44 | AI579 | No-Units | 0 | Status Bitmap
45 | A,B,C | R/W | NV | 4964 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 45 | AI580 | No-Units | 0 | Status Bitmap
46 | A,B,C | R/W | NV | 4965 |  |  |  | Alarm Status Non-Latching | Non-Latching Alarm Logical Circuit 46 | AI581 | No-Units | 0 | Status Bitmap
total registers in this section
2070

## -=E30 2PH Circuits=-
21 DUAL-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed, Bottom Feed configuration
[6 empty] | Top Feed | Bottom Feed
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 3 | 2 | B
| 2 | 2 | 1 | A
|  | 4 | 2 | B
| 3 | 5 | 1 | C
|  | 7 | 2 | A
| 4 | 6 | 1 | C
|  | 8 | 2 | A
| 5 | 9 | 1 | B
|  | 11 | 2 | C
| 6 | 10 | 1 | B
|  | 12 | 2 | C
| 7 | 13 | 1 | A
|  | 15 | 2 | B
| 8 | 14 | 1 | A
|  | 16 | 2 | B
| 9 | 17 | 1 | C
|  | 19 | 2 | A
| 10 | 18 | 1 | C
|  | 20 | 2 | A
| 11 | 21 | 1 | B
|  | 23 | 2 | C
| 12 | 22 | 1 | B
|  | 24 | 2 | C
| 13 | 25 | 1 | A
|  | 27 | 2 | B
| 14 | 26 | 1 | A
|  | 28 | 2 | B
| 15 | 29 | 1 | C
|  | 31 | 2 | A
| 16 | 30 | 1 | C
|  | 32 | 2 | A
| 17 | 33 | 1 | B
|  | 35 | 2 | C
| 18 | 34 | 1 | B
|  | 36 | 2 | C
| 19 | 37 | 1 | A
|  | 39 | 2 | B
| 20 | 38 | 1 | A
|  | 40 | 2 | B
| 21 | 41 | 1 | C | *Circuit 21 will not produce meaningful data for Top Feed 2-phase
|  | 42 | 2 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A |  | Sequential
|  | 2 | 2 | B
| 2 | 3 | 1 | C
|  | 4 | 2 | A
| 3 | 5 | 1 | B
|  | 6 | 2 | C
| 4 | 7 | 1 | A
|  | 8 | 2 | B
| 5 | 9 | 1 | C
|  | 10 | 2 | A
| 6 | 11 | 1 | B
|  | 12 | 2 | C
| 7 | 13 | 1 | A
|  | 14 | 2 | B
| 8 | 15 | 1 | C
|  | 16 | 2 | A
| 9 | 17 | 1 | B
|  | 18 | 2 | C
| 10 | 19 | 1 | A
|  | 20 | 2 | B
| 11 | 21 | 1 | C
|  | 22 | 2 | A
| 12 | 23 | 1 | B
|  | 24 | 2 | C
| 13 | 25 | 1 | A
|  | 26 | 2 | B
| 14 | 27 | 1 | C
|  | 28 | 2 | A
| 15 | 29 | 1 | B
|  | 30 | 2 | C
| 16 | 31 | 1 | A
|  | 32 | 2 | B
| 17 | 33 | 1 | C
|  | 34 | 2 | A
| 18 | 35 | 1 | B
|  | 36 | 2 | C
| 19 | 37 | 1 | A
|  | 38 | 2 | B
| 20 | 39 | 1 | C
|  | 40 | 2 | A
| 21 | 41 | 1 | B
|  | 42 | 2 | C
Voltage/Current Phasing for Single Row: Odd / Even configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A |  | Odd / Even
|  | 3 | 2 | B
| 2 | 5 | 1 | C
|  | 7 | 2 | A
| 3 | 9 | 1 | B
|  | 11 | 2 | C
| 4 | 13 | 1 | A
|  | 15 | 2 | B
| 5 | 17 | 1 | C
|  | 19 | 2 | A
| 6 | 21 | 1 | B
|  | 23 | 2 | C
| 7 | 25 | 1 | A
|  | 27 | 2 | B
| 8 | 29 | 1 | C
|  | 31 | 2 | A
| 9 | 33 | 1 | B
|  | 35 | 2 | C
| 10 | 37 | 1 | A
|  | 39 | 2 | B
| 11 | 41 | 1 | C
|  | 2 | 2 | A
| 12 | 4 | 1 | B
|  | 6 | 2 | C
| 13 | 8 | 1 | A
|  | 10 | 2 | B
| 14 | 12 | 1 | C
|  | 14 | 2 | A
| 15 | 16 | 1 | B
|  | 18 | 2 | C
| 16 | 20 | 1 | A
|  | 22 | 2 | B
| 17 | 24 | 1 | C
|  | 26 | 2 | A
| 18 | 28 | 1 | B
|  | 30 | 2 | C
| 19 | 32 | 1 | A
|  | 34 | 2 | B
| 20 | 36 | 1 | C
|  | 38 | 2 | A
| 21 | 40 | 1 | B
|  | 42 | 2 | C

## -=E31 2PH Circuits=-
21 DUAL-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 3 | 2 | B
| 2 | 2 | 1 | A
|  | 4 | 2 | B
| 3 | 5 | 1 | C
|  | 7 | 2 | A
| 4 | 6 | 1 | C
|  | 8 | 2 | A
| 5 | 9 | 1 | B
|  | 11 | 2 | C
| 6 | 10 | 1 | B
|  | 12 | 2 | C
| 7 | 13 | 1 | A
|  | 15 | 2 | B
| 8 | 14 | 1 | A
|  | 16 | 2 | B
| 9 | 17 | 1 | C
|  | 19 | 2 | A
| 10 | 18 | 1 | C
|  | 20 | 2 | A
| 11 | 21 | 1 | B
|  | 23 | 2 | C
| 12 | 22 | 1 | B
|  | 24 | 2 | C
| 13 | 25 | 1 | A
|  | 27 | 2 | B
| 14 | 26 | 1 | A
|  | 28 | 2 | B
| 15 | 29 | 1 | C
|  | 31 | 2 | A
| 16 | 30 | 1 | C
|  | 32 | 2 | A
| 17 | 33 | 1 | B
|  | 35 | 2 | C
| 18 | 34 | 1 | B
|  | 36 | 2 | C
| 19 | 37 | 1 | A
|  | 39 | 2 | B
| 20 | 38 | 1 | A
|  | 40 | 2 | B
| 21 | 41 | 1 | C | *Circuit 21 will not produce meaningful data for Top Feed 2-phase
|  | 42 | 2 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 2 | 2 | B
| 2 | 3 | 1 | C
|  | 4 | 2 | A
| 3 | 5 | 1 | B
|  | 6 | 2 | C
| 4 | 7 | 1 | A
|  | 8 | 2 | B
| 5 | 9 | 1 | C
|  | 10 | 2 | A
| 6 | 11 | 1 | B
|  | 12 | 2 | C
| 7 | 13 | 1 | A
|  | 14 | 2 | B
| 8 | 15 | 1 | C
|  | 16 | 2 | A
| 9 | 17 | 1 | B
|  | 18 | 2 | C
| 10 | 19 | 1 | A
|  | 20 | 2 | B
| 11 | 21 | 1 | C
|  | 22 | 2 | A
| 12 | 23 | 1 | B
|  | 24 | 2 | C
| 13 | 25 | 1 | A
|  | 26 | 2 | B
| 14 | 27 | 1 | C
|  | 28 | 2 | A
| 15 | 29 | 1 | B
|  | 30 | 2 | C
| 16 | 31 | 1 | A
|  | 32 | 2 | B
| 17 | 33 | 1 | C
|  | 34 | 2 | A
| 18 | 35 | 1 | B
|  | 36 | 2 | C
| 19 | 37 | 1 | A
|  | 38 | 2 | B
| 20 | 39 | 1 | C
|  | 40 | 2 | A
| 21 | 41 | 1 | B
|  | 42 | 2 | C

## 2PH Point Map
Note: This map assumes that all pairs of branch CT's are identical
Modbus
Circuit | Model (A,B,C) | R/W | NV | Integer Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description
SCALE REGISTERS
1 | A,B,C | R | NV | 4000 |  |  |  | Current Scale
2 | A,B,C | R | NV | 4001 |  |  |  | Current Scale
3 | A,B,C | R | NV | 4002 |  |  |  | Current Scale
4 | A,B,C | R | NV | 4003 |  |  |  | Current Scale
5 | A,B,C | R | NV | 4004 |  |  |  | Current Scale
6 | A,B,C | R | NV | 4005 |  |  |  | Current Scale
7 | A,B,C | R | NV | 4006 |  |  |  | Current Scale
8 | A,B,C | R | NV | 4007 |  |  |  | Current Scale
9 | A,B,C | R | NV | 4008 |  |  |  | Current Scale
10 | A,B,C | R | NV | 4009 |  |  |  | Current Scale
11 | A,B,C | R | NV | 4010 |  |  |  | Current Scale
12 | A,B,C | R | NV | 4011 |  |  |  | Current Scale
13 | A,B,C | R | NV | 4012 |  |  |  | Current Scale
14 | A,B,C | R | NV | 4013 |  |  |  | Current Scale
15 | A,B,C | R | NV | 4014 |  |  |  | Current Scale
16 | A,B,C | R | NV | 4015 |  |  |  | Current Scale
17 | A,B,C | R | NV | 4016 |  |  |  | Current Scale
18 | A,B,C | R | NV | 4017 |  |  |  | Current Scale
19 | A,B,C | R | NV | 4018 |  |  |  | Current Scale
20 | A,B,C | R | NV | 4019 |  |  |  | Current Scale
21 | A,B,C | R | NV | 4020 |  |  |  | Current Scale
1 | A | R | NV | 4021 |  |  |  | Power Scale
2 | A | R | NV | 4022 |  |  |  | Power Scale
3 | A | R | NV | 4023 |  |  |  | Power Scale
4 | A | R | NV | 4024 |  |  |  | Power Scale
5 | A | R | NV | 4025 |  |  |  | Power Scale
6 | A | R | NV | 4026 |  |  |  | Power Scale
7 | A | R | NV | 4027 |  |  |  | Power Scale
8 | A | R | NV | 4028 |  |  |  | Power Scale
9 | A | R | NV | 4029 |  |  |  | Power Scale
10 | A | R | NV | 4030 |  |  |  | Power Scale
11 | A | R | NV | 4031 |  |  |  | Power Scale
12 | A | R | NV | 4032 |  |  |  | Power Scale
13 | A | R | NV | 4033 |  |  |  | Power Scale
14 | A | R | NV | 4034 |  |  |  | Power Scale
15 | A | R | NV | 4035 |  |  |  | Power Scale
16 | A | R | NV | 4036 |  |  |  | Power Scale
17 | A | R | NV | 4037 |  |  |  | Power Scale
18 | A | R | NV | 4038 |  |  |  | Power Scale
19 | A | R | NV | 4039 |  |  |  | Power Scale
20 | A | R | NV | 4040 |  |  |  | Power Scale
21 | A | R | NV | 4041 |  |  |  | Power Scale
1 | A | R | NV | 4042 |  |  |  | Energy Scale
2 | A | R | NV | 4043 |  |  |  | Energy Scale
3 | A | R | NV | 4044 |  |  |  | Energy Scale
4 | A | R | NV | 4045 |  |  |  | Energy Scale
5 | A | R | NV | 4046 |  |  |  | Energy Scale
6 | A | R | NV | 4047 |  |  |  | Energy Scale
7 | A | R | NV | 4048 |  |  |  | Energy Scale
8 | A | R | NV | 4049 |  |  |  | Energy Scale
9 | A | R | NV | 4050 |  |  |  | Energy Scale
10 | A | R | NV | 4051 |  |  |  | Energy Scale
11 | A | R | NV | 4052 |  |  |  | Energy Scale
12 | A | R | NV | 4053 |  |  |  | Energy Scale
13 | A | R | NV | 4054 |  |  |  | Energy Scale
14 | A | R | NV | 4055 |  |  |  | Energy Scale
15 | A | R | NV | 4056 |  |  |  | Energy Scale
16 | A | R | NV | 4057 |  |  |  | Energy Scale
17 | A | R | NV | 4058 |  |  |  | Energy Scale
18 | A | R | NV | 4059 |  |  |  | Energy Scale
19 | A | R | NV | 4060 |  |  |  | Energy Scale
20 | A | R | NV | 4061 |  |  |  | Energy Scale
21 | A | R | NV | 4062 |  |  |  | Energy Scale
RESETS
Also resets corresponding registers in 1PH and 3PH maps
1 | A,B,C | W |  | 4063 |  |  |  | Reset - Write the listed value to perform the listed reset:
10203 = Clear KWH value to zero
29877 = Clear all Max Current and Max KW values to zero
2 | A,B,C | W |  | 4064 |  |  |  | Reset
3 | A,B,C | W |  | 4065 |  |  |  | Reset
4 | A,B,C | W |  | 4066 |  |  |  | Reset
5 | A,B,C | W |  | 4067 |  |  |  | Reset
6 | A,B,C | W |  | 4068 |  |  |  | Reset
7 | A,B,C | W |  | 4069 |  |  |  | Reset
8 | A,B,C | W |  | 4070 |  |  |  | Reset
9 | A,B,C | W |  | 4071 |  |  |  | Reset
10 | A,B,C | W |  | 4072 |  |  |  | Reset
11 | A,B,C | W |  | 4073 |  |  |  | Reset
12 | A,B,C | W |  | 4074 |  |  |  | Reset
13 | A,B,C | W |  | 4075 |  |  |  | Reset
14 | A,B,C | W |  | 4076 |  |  |  | Reset
15 | A,B,C | W |  | 4077 |  |  |  | Reset
16 | A,B,C | W |  | 4078 |  |  |  | Reset
17 | A,B,C | W |  | 4079 |  |  |  | Reset
18 | A,B,C | W |  | 4080 |  |  |  | Reset
19 | A,B,C | W |  | 4081 |  |  |  | Reset
20 | A,B,C | W |  | 4082 |  |  |  | Reset
21 | A,B,C | W |  | 4083 |  |  |  | Reset
DATA
1 | A | R | NV | 4084 | 5000 | 5001 | 4042 | KWH (MSW)
1 | A | R | NV | 4085 |  |  |  | KWH (LSW)
2 | A | R | NV | 4086 | 5002 | 5003 | 4043 | KWH (MSW)
2 | A | R | NV | 4087 |  |  |  | KWH (LSW)
3 | A | R | NV | 4088 | 5004 | 5005 | 4044 | KWH (MSW)
3 | A | R | NV | 4089 |  |  |  | KWH (LSW)
4 | A | R | NV | 4090 | 5006 | 5007 | 4045 | KWH (MSW)
4 | A | R | NV | 4091 |  |  |  | KWH (LSW)
5 | A | R | NV | 4092 | 5008 | 5009 | 4046 | KWH (MSW)
5 | A | R | NV | 4093 |  |  |  | KWH (LSW)
6 | A | R | NV | 4094 | 5010 | 5011 | 4047 | KWH (MSW)
6 | A | R | NV | 4095 |  |  |  | KWH (LSW)
7 | A | R | NV | 4096 | 5012 | 5013 | 4048 | KWH (MSW)
7 | A | R | NV | 4097 |  |  |  | KWH (LSW)
8 | A | R | NV | 4098 | 5014 | 5015 | 4049 | KWH (MSW)
8 | A | R | NV | 4099 |  |  |  | KWH (LSW)
9 | A | R | NV | 4100 | 5016 | 5017 | 4050 | KWH (MSW)
9 | A | R | NV | 4101 |  |  |  | KWH (LSW)
10 | A | R | NV | 4102 | 5018 | 5019 | 4051 | KWH (MSW)
10 | A | R | NV | 4103 |  |  |  | KWH (LSW)
11 | A | R | NV | 4104 | 5020 | 5021 | 4052 | KWH (MSW)
11 | A | R | NV | 4105 |  |  |  | KWH (LSW)
12 | A | R | NV | 4106 | 5022 | 5023 | 4053 | KWH (MSW)
12 | A | R | NV | 4107 |  |  |  | KWH (LSW)
13 | A | R | NV | 4108 | 5024 | 5025 | 4054 | KWH (MSW)
13 | A | R | NV | 4109 |  |  |  | KWH (LSW)
14 | A | R | NV | 4110 | 5026 | 5027 | 4055 | KWH (MSW)
14 | A | R | NV | 4111 |  |  |  | KWH (LSW)
15 | A | R | NV | 4112 | 5028 | 5029 | 4056 | KWH (MSW)
15 | A | R | NV | 4113 |  |  |  | KWH (LSW)
16 | A | R | NV | 4114 | 5030 | 5031 | 4057 | KWH (MSW)
16 | A | R | NV | 4115 |  |  |  | KWH (LSW)
17 | A | R | NV | 4116 | 5032 | 5033 | 4058 | KWH (MSW)
17 | A | R | NV | 4117 |  |  |  | KWH (LSW)
18 | A | R | NV | 4118 | 5034 | 5035 | 4059 | KWH (MSW)
18 | A | R | NV | 4119 |  |  |  | KWH (LSW)
19 | A | R | NV | 4120 | 5036 | 5037 | 4060 | KWH (MSW)
19 | A | R | NV | 4121 |  |  |  | KWH (LSW)
20 | A | R | NV | 4122 | 5038 | 5039 | 4061 | KWH (MSW)
20 | A | R | NV | 4123 |  |  |  | KWH (LSW)
21 | A | R | NV | 4124 | 5040 | 5041 | 4062 | KWH (MSW)
21 | A | R | NV | 4125 |  |  |  | KWH (LSW)
1 | A | R |  | 4126 | 5042 | 5043 | 4021 | KW Total
2 | A | R |  | 4127 | 5044 | 5045 | 4022 | KW Total
3 | A | R |  | 4128 | 5046 | 5047 | 4023 | KW Total
4 | A | R |  | 4129 | 5048 | 5049 | 4024 | KW Total
5 | A | R |  | 4130 | 5050 | 5051 | 4025 | KW Total
6 | A | R |  | 4131 | 5052 | 5053 | 4026 | KW Total
7 | A | R |  | 4132 | 5054 | 5055 | 4027 | KW Total
8 | A | R |  | 4133 | 5056 | 5057 | 4028 | KW Total
9 | A | R |  | 4134 | 5058 | 5059 | 4029 | KW Total
10 | A | R |  | 4135 | 5060 | 5061 | 4030 | KW Total
11 | A | R |  | 4136 | 5062 | 5063 | 4031 | KW Total
12 | A | R |  | 4137 | 5064 | 5065 | 4032 | KW Total
13 | A | R |  | 4138 | 5066 | 5067 | 4033 | KW Total
14 | A | R |  | 4139 | 5068 | 5069 | 4034 | KW Total
15 | A | R |  | 4140 | 5070 | 5071 | 4035 | KW Total
16 | A | R |  | 4141 | 5072 | 5073 | 4036 | KW Total
17 | A | R |  | 4142 | 5074 | 5075 | 4037 | KW Total
18 | A | R |  | 4143 | 5076 | 5077 | 4038 | KW Total
19 | A | R |  | 4144 | 5078 | 5079 | 4039 | KW Total
20 | A | R |  | 4145 | 5080 | 5081 | 4040 | KW Total
21 | A | R |  | 4146 | 5082 | 5083 | 4041 | KW Total
1 | A | R |  | 4147 | 5084 | 5085 | -3 | PF Total
2 | A | R |  | 4148 | 5086 | 5087 | -3 | PF Total
3 | A | R |  | 4149 | 5088 | 5089 | -3 | PF Total
4 | A | R |  | 4150 | 5090 | 5091 | -3 | PF Total
5 | A | R |  | 4151 | 5092 | 5093 | -3 | PF Total
6 | A | R |  | 4152 | 5094 | 5095 | -3 | PF Total
7 | A | R |  | 4153 | 5096 | 5097 | -3 | PF Total
8 | A | R |  | 4154 | 5098 | 5099 | -3 | PF Total
9 | A | R |  | 4155 | 5100 | 5101 | -3 | PF Total
10 | A | R |  | 4156 | 5102 | 5103 | -3 | PF Total
11 | A | R |  | 4157 | 5104 | 5105 | -3 | PF Total
12 | A | R |  | 4158 | 5106 | 5107 | -3 | PF Total
13 | A | R |  | 4159 | 5108 | 5109 | -3 | PF Total
14 | A | R |  | 4160 | 5110 | 5111 | -3 | PF Total
15 | A | R |  | 4161 | 5112 | 5113 | -3 | PF Total
16 | A | R |  | 4162 | 5114 | 5115 | -3 | PF Total
17 | A | R |  | 4163 | 5116 | 5117 | -3 | PF Total
18 | A | R |  | 4164 | 5118 | 5119 | -3 | PF Total
19 | A | R |  | 4165 | 5120 | 5121 | -3 | PF Total
20 | A | R |  | 4166 | 5122 | 5123 | -3 | PF Total
21 | A | R |  | 4167 | 5124 | 5125 | -3 | PF Total
1 | A,B,C | R |  | 4168 | 5126 | 5127 | 4000 | Current Average of 2 phases
2 | A,B,C | R |  | 4169 | 5128 | 5129 | 4001 | Current Average of 2 phases
3 | A,B,C | R |  | 4170 | 5130 | 5131 | 4002 | Current Average of 2 phases
4 | A,B,C | R |  | 4171 | 5132 | 5133 | 4003 | Current Average of 2 phases
5 | A,B,C | R |  | 4172 | 5134 | 5135 | 4004 | Current Average of 2 phases
6 | A,B,C | R |  | 4173 | 5136 | 5137 | 4005 | Current Average of 2 phases
7 | A,B,C | R |  | 4174 | 5138 | 5139 | 4006 | Current Average of 2 phases
8 | A,B,C | R |  | 4175 | 5140 | 5141 | 4007 | Current Average of 2 phases
9 | A,B,C | R |  | 4176 | 5142 | 5143 | 4008 | Current Average of 2 phases
10 | A,B,C | R |  | 4177 | 5144 | 5145 | 4009 | Current Average of 2 phases
11 | A,B,C | R |  | 4178 | 5146 | 5147 | 4010 | Current Average of 2 phases
12 | A,B,C | R |  | 4179 | 5148 | 5149 | 4011 | Current Average of 2 phases
13 | A,B,C | R |  | 4180 | 5150 | 5151 | 4012 | Current Average of 2 phases
14 | A,B,C | R |  | 4181 | 5152 | 5153 | 4013 | Current Average of 2 phases
15 | A,B,C | R |  | 4182 | 5154 | 5155 | 4014 | Current Average of 2 phases
16 | A,B,C | R |  | 4183 | 5156 | 5157 | 4015 | Current Average of 2 phases
17 | A,B,C | R |  | 4184 | 5158 | 5159 | 4016 | Current Average of 2 phases
18 | A,B,C | R |  | 4185 | 5160 | 5161 | 4017 | Current Average of 2 phases
19 | A,B,C | R |  | 4186 | 5162 | 5163 | 4018 | Current Average of 2 phases
20 | A,B,C | R |  | 4187 | 5164 | 5165 | 4019 | Current Average of 2 phases
21 | A,B,C | R |  | 4188 | 5166 | 5167 | 4020 | Current Average of 2 phases
1 | A | R |  | 4189 | 5168 | 5169 | 4021 | KW Phase 1
2 | A | R |  | 4190 | 5170 | 5171 | 4022 | KW Phase 1
3 | A | R |  | 4191 | 5172 | 5173 | 4023 | KW Phase 1
4 | A | R |  | 4192 | 5174 | 5175 | 4024 | KW Phase 1
5 | A | R |  | 4193 | 5176 | 5177 | 4025 | KW Phase 1
6 | A | R |  | 4194 | 5178 | 5179 | 4026 | KW Phase 1
7 | A | R |  | 4195 | 5180 | 5181 | 4027 | KW Phase 1
8 | A | R |  | 4196 | 5182 | 5183 | 4028 | KW Phase 1
9 | A | R |  | 4197 | 5184 | 5185 | 4029 | KW Phase 1
10 | A | R |  | 4198 | 5186 | 5187 | 4030 | KW Phase 1
11 | A | R |  | 4199 | 5188 | 5189 | 4031 | KW Phase 1
12 | A | R |  | 4200 | 5190 | 5191 | 4032 | KW Phase 1
13 | A | R |  | 4201 | 5192 | 5193 | 4033 | KW Phase 1
14 | A | R |  | 4202 | 5194 | 5195 | 4034 | KW Phase 1
15 | A | R |  | 4203 | 5196 | 5197 | 4035 | KW Phase 1
16 | A | R |  | 4204 | 5198 | 5199 | 4036 | KW Phase 1
17 | A | R |  | 4205 | 5200 | 5201 | 4037 | KW Phase 1
18 | A | R |  | 4206 | 5202 | 5203 | 4038 | KW Phase 1
19 | A | R |  | 4207 | 5204 | 5205 | 4039 | KW Phase 1
20 | A | R |  | 4208 | 5206 | 5207 | 4040 | KW Phase 1
21 | A | R |  | 4209 | 5208 | 5209 | 4041 | KW Phase 1
1 | A | R |  | 4210 | 5210 | 5211 | 4021 | KW Phase 2
2 | A | R |  | 4211 | 5212 | 5213 | 4022 | KW Phase 2
3 | A | R |  | 4212 | 5214 | 5215 | 4023 | KW Phase 2
4 | A | R |  | 4213 | 5216 | 5217 | 4024 | KW Phase 2
5 | A | R |  | 4214 | 5218 | 5219 | 4025 | KW Phase 2
6 | A | R |  | 4215 | 5220 | 5221 | 4026 | KW Phase 2
7 | A | R |  | 4216 | 5222 | 5223 | 4027 | KW Phase 2
8 | A | R |  | 4217 | 5224 | 5225 | 4028 | KW Phase 2
9 | A | R |  | 4218 | 5226 | 5227 | 4029 | KW Phase 2
10 | A | R |  | 4219 | 5228 | 5229 | 4030 | KW Phase 2
11 | A | R |  | 4220 | 5230 | 5231 | 4031 | KW Phase 2
12 | A | R |  | 4221 | 5232 | 5233 | 4032 | KW Phase 2
13 | A | R |  | 4222 | 5234 | 5235 | 4033 | KW Phase 2
14 | A | R |  | 4223 | 5236 | 5237 | 4034 | KW Phase 2
15 | A | R |  | 4224 | 5238 | 5239 | 4035 | KW Phase 2
16 | A | R |  | 4225 | 5240 | 5241 | 4036 | KW Phase 2
17 | A | R |  | 4226 | 5242 | 5243 | 4037 | KW Phase 2
18 | A | R |  | 4227 | 5244 | 5245 | 4038 | KW Phase 2
19 | A | R |  | 4228 | 5246 | 5247 | 4039 | KW Phase 2
20 | A | R |  | 4229 | 5248 | 5249 | 4040 | KW Phase 2
21 | A | R |  | 4230 | 5250 | 5251 | 4041 | KW Phase 2
1 | A | R |  | 4231 | 5252 | 5253 | -3 | PF Phase 1
2 | A | R |  | 4232 | 5254 | 5255 | -3 | PF Phase 1
3 | A | R |  | 4233 | 5256 | 5257 | -3 | PF Phase 1
4 | A | R |  | 4234 | 5258 | 5259 | -3 | PF Phase 1
5 | A | R |  | 4235 | 5260 | 5261 | -3 | PF Phase 1
6 | A | R |  | 4236 | 5262 | 5263 | -3 | PF Phase 1
7 | A | R |  | 4237 | 5264 | 5265 | -3 | PF Phase 1
8 | A | R |  | 4238 | 5266 | 5267 | -3 | PF Phase 1
9 | A | R |  | 4239 | 5268 | 5269 | -3 | PF Phase 1
10 | A | R |  | 4240 | 5270 | 5271 | -3 | PF Phase 1
11 | A | R |  | 4241 | 5272 | 5273 | -3 | PF Phase 1
12 | A | R |  | 4242 | 5274 | 5275 | -3 | PF Phase 1
13 | A | R |  | 4243 | 5276 | 5277 | -3 | PF Phase 1
14 | A | R |  | 4244 | 5278 | 5279 | -3 | PF Phase 1
15 | A | R |  | 4245 | 5280 | 5281 | -3 | PF Phase 1
16 | A | R |  | 4246 | 5282 | 5283 | -3 | PF Phase 1
17 | A | R |  | 4247 | 5284 | 5285 | -3 | PF Phase 1
18 | A | R |  | 4248 | 5286 | 5287 | -3 | PF Phase 1
19 | A | R |  | 4249 | 5288 | 5289 | -3 | PF Phase 1
20 | A | R |  | 4250 | 5290 | 5291 | -3 | PF Phase 1
21 | A | R |  | 4251 | 5292 | 5293 | -3 | PF Phase 1
1 | A | R |  | 4252 | 5294 | 5295 | -3 | PF Phase 2
2 | A | R |  | 4253 | 5296 | 5297 | -3 | PF Phase 2
3 | A | R |  | 4254 | 5298 | 5299 | -3 | PF Phase 2
4 | A | R |  | 4255 | 5300 | 5301 | -3 | PF Phase 2
5 | A | R |  | 4256 | 5302 | 5303 | -3 | PF Phase 2
6 | A | R |  | 4257 | 5304 | 5305 | -3 | PF Phase 2
7 | A | R |  | 4258 | 5306 | 5307 | -3 | PF Phase 2
8 | A | R |  | 4259 | 5308 | 5309 | -3 | PF Phase 2
9 | A | R |  | 4260 | 5310 | 5311 | -3 | PF Phase 2
10 | A | R |  | 4261 | 5312 | 5313 | -3 | PF Phase 2
11 | A | R |  | 4262 | 5314 | 5315 | -3 | PF Phase 2
12 | A | R |  | 4263 | 5316 | 5317 | -3 | PF Phase 2
13 | A | R |  | 4264 | 5318 | 5319 | -3 | PF Phase 2
14 | A | R |  | 4265 | 5320 | 5321 | -3 | PF Phase 2
15 | A | R |  | 4266 | 5322 | 5323 | -3 | PF Phase 2
16 | A | R |  | 4267 | 5324 | 5325 | -3 | PF Phase 2
17 | A | R |  | 4268 | 5326 | 5327 | -3 | PF Phase 2
18 | A | R |  | 4269 | 5328 | 5329 | -3 | PF Phase 2
19 | A | R |  | 4270 | 5330 | 5331 | -3 | PF Phase 2
20 | A | R |  | 4271 | 5332 | 5333 | -3 | PF Phase 2
21 | A | R |  | 4272 | 5334 | 5335 | -3 | PF Phase 2
1 | A,B,C | R |  | 4273 | 5336 | 5337 | 4000 | Current Phase 1
2 | A,B,C | R |  | 4274 | 5338 | 5339 | 4001 | Current Phase 1
3 | A,B,C | R |  | 4275 | 5340 | 5341 | 4002 | Current Phase 1
4 | A,B,C | R |  | 4276 | 5342 | 5343 | 4003 | Current Phase 1
5 | A,B,C | R |  | 4277 | 5344 | 5345 | 4004 | Current Phase 1
6 | A,B,C | R |  | 4278 | 5346 | 5347 | 4005 | Current Phase 1
7 | A,B,C | R |  | 4279 | 5348 | 5349 | 4006 | Current Phase 1
8 | A,B,C | R |  | 4280 | 5350 | 5351 | 4007 | Current Phase 1
9 | A,B,C | R |  | 4281 | 5352 | 5353 | 4008 | Current Phase 1
10 | A,B,C | R |  | 4282 | 5354 | 5355 | 4009 | Current Phase 1
11 | A,B,C | R |  | 4283 | 5356 | 5357 | 4010 | Current Phase 1
12 | A,B,C | R |  | 4284 | 5358 | 5359 | 4011 | Current Phase 1
13 | A,B,C | R |  | 4285 | 5360 | 5361 | 4012 | Current Phase 1
14 | A,B,C | R |  | 4286 | 5362 | 5363 | 4013 | Current Phase 1
15 | A,B,C | R |  | 4287 | 5364 | 5365 | 4014 | Current Phase 1
16 | A,B,C | R |  | 4288 | 5366 | 5367 | 4015 | Current Phase 1
17 | A,B,C | R |  | 4289 | 5368 | 5369 | 4016 | Current Phase 1
18 | A,B,C | R |  | 4290 | 5370 | 5371 | 4017 | Current Phase 1
19 | A,B,C | R |  | 4291 | 5372 | 5373 | 4018 | Current Phase 1
20 | A,B,C | R |  | 4292 | 5374 | 5375 | 4019 | Current Phase 1
21 | A,B,C | R |  | 4293 | 5376 | 5377 | 4020 | Current Phase 1
1 | A,B,C | R |  | 4294 | 5378 | 5379 | 4000 | Current Phase 2
2 | A,B,C | R |  | 4295 | 5380 | 5381 | 4001 | Current Phase 2
3 | A,B,C | R |  | 4296 | 5382 | 5383 | 4002 | Current Phase 2
4 | A,B,C | R |  | 4297 | 5384 | 5385 | 4003 | Current Phase 2
5 | A,B,C | R |  | 4298 | 5386 | 5387 | 4004 | Current Phase 2
6 | A,B,C | R |  | 4299 | 5388 | 5389 | 4005 | Current Phase 2
7 | A,B,C | R |  | 4300 | 5390 | 5391 | 4006 | Current Phase 2
8 | A,B,C | R |  | 4301 | 5392 | 5393 | 4007 | Current Phase 2
9 | A,B,C | R |  | 4302 | 5394 | 5395 | 4008 | Current Phase 2
10 | A,B,C | R |  | 4303 | 5396 | 5397 | 4009 | Current Phase 2
11 | A,B,C | R |  | 4304 | 5398 | 5399 | 4010 | Current Phase 2
12 | A,B,C | R |  | 4305 | 5400 | 5401 | 4011 | Current Phase 2
13 | A,B,C | R |  | 4306 | 5402 | 5403 | 4012 | Current Phase 2
14 | A,B,C | R |  | 4307 | 5404 | 5405 | 4013 | Current Phase 2
15 | A,B,C | R |  | 4308 | 5406 | 5407 | 4014 | Current Phase 2
16 | A,B,C | R |  | 4309 | 5408 | 5409 | 4015 | Current Phase 2
17 | A,B,C | R |  | 4310 | 5410 | 5411 | 4016 | Current Phase 2
18 | A,B,C | R |  | 4311 | 5412 | 5413 | 4017 | Current Phase 2
19 | A,B,C | R |  | 4312 | 5414 | 5415 | 4018 | Current Phase 2
20 | A,B,C | R |  | 4313 | 5416 | 5417 | 4019 | Current Phase 2
21 | A,B,C | R |  | 4314 | 5418 | 5419 | 4020 | Current Phase 2
1 | A | R |  | 4315 | 5420 | 5421 | 4021 | Present KW-Total Demand
2 | A | R |  | 4316 | 5422 | 5423 | 4022 | Present KW-Total Demand
3 | A | R |  | 4317 | 5424 | 5425 | 4023 | Present KW-Total Demand
4 | A | R |  | 4318 | 5426 | 5427 | 4024 | Present KW-Total Demand
5 | A | R |  | 4319 | 5428 | 5429 | 4025 | Present KW-Total Demand
6 | A | R |  | 4320 | 5430 | 5431 | 4026 | Present KW-Total Demand
7 | A | R |  | 4321 | 5432 | 5433 | 4027 | Present KW-Total Demand
8 | A | R |  | 4322 | 5434 | 5435 | 4028 | Present KW-Total Demand
9 | A | R |  | 4323 | 5436 | 5437 | 4029 | Present KW-Total Demand
10 | A | R |  | 4324 | 5438 | 5439 | 4030 | Present KW-Total Demand
11 | A | R |  | 4325 | 5440 | 5441 | 4031 | Present KW-Total Demand
12 | A | R |  | 4326 | 5442 | 5443 | 4032 | Present KW-Total Demand
13 | A | R |  | 4327 | 5444 | 5445 | 4033 | Present KW-Total Demand
14 | A | R |  | 4328 | 5446 | 5447 | 4034 | Present KW-Total Demand
15 | A | R |  | 4329 | 5448 | 5449 | 4035 | Present KW-Total Demand
16 | A | R |  | 4330 | 5450 | 5451 | 4036 | Present KW-Total Demand
17 | A | R |  | 4331 | 5452 | 5453 | 4037 | Present KW-Total Demand
18 | A | R |  | 4332 | 5454 | 5455 | 4038 | Present KW-Total Demand
19 | A | R |  | 4333 | 5456 | 5457 | 4039 | Present KW-Total Demand
20 | A | R |  | 4334 | 5458 | 5459 | 4040 | Present KW-Total Demand
21 | A | R |  | 4335 | 5460 | 5461 | 4041 | Present KW-Total Demand
1 | A | R | NV | 4336 | 5462 | 5463 | 4021 | Max KW-Total Demand
2 | A | R | NV | 4337 | 5464 | 5465 | 4022 | Max KW-Total Demand
3 | A | R | NV | 4338 | 5466 | 5467 | 4023 | Max KW-Total Demand
4 | A | R | NV | 4339 | 5468 | 5469 | 4024 | Max KW-Total Demand
5 | A | R | NV | 4340 | 5470 | 5471 | 4025 | Max KW-Total Demand
6 | A | R | NV | 4341 | 5472 | 5473 | 4026 | Max KW-Total Demand
7 | A | R | NV | 4342 | 5474 | 5475 | 4027 | Max KW-Total Demand
8 | A | R | NV | 4343 | 5476 | 5477 | 4028 | Max KW-Total Demand
9 | A | R | NV | 4344 | 5478 | 5479 | 4029 | Max KW-Total Demand
10 | A | R | NV | 4345 | 5480 | 5481 | 4030 | Max KW-Total Demand
11 | A | R | NV | 4346 | 5482 | 5483 | 4031 | Max KW-Total Demand
12 | A | R | NV | 4347 | 5484 | 5485 | 4032 | Max KW-Total Demand
13 | A | R | NV | 4348 | 5486 | 5487 | 4033 | Max KW-Total Demand
14 | A | R | NV | 4349 | 5488 | 5489 | 4034 | Max KW-Total Demand
15 | A | R | NV | 4350 | 5490 | 5491 | 4035 | Max KW-Total Demand
16 | A | R | NV | 4351 | 5492 | 5493 | 4036 | Max KW-Total Demand
17 | A | R | NV | 4352 | 5494 | 5495 | 4037 | Max KW-Total Demand
18 | A | R | NV | 4353 | 5496 | 5497 | 4038 | Max KW-Total Demand
19 | A | R | NV | 4354 | 5498 | 5499 | 4039 | Max KW-Total Demand
20 | A | R | NV | 4355 | 5500 | 5501 | 4040 | Max KW-Total Demand
21 | A | R | NV | 4356 | 5502 | 5503 | 4041 | Max KW-Total Demand
1 | A,B,C | R |  | 4357 | 5504 | 5505 | 4000 | Present Current Demand Phase 1
2 | A,B,C | R |  | 4358 | 5506 | 5507 | 4001 | Present Current Demand Phase 1
3 | A,B,C | R |  | 4359 | 5508 | 5509 | 4002 | Present Current Demand Phase 1
4 | A,B,C | R |  | 4360 | 5510 | 5511 | 4003 | Present Current Demand Phase 1
5 | A,B,C | R |  | 4361 | 5512 | 5513 | 4004 | Present Current Demand Phase 1
6 | A,B,C | R |  | 4362 | 5514 | 5515 | 4005 | Present Current Demand Phase 1
7 | A,B,C | R |  | 4363 | 5516 | 5517 | 4006 | Present Current Demand Phase 1
8 | A,B,C | R |  | 4364 | 5518 | 5519 | 4007 | Present Current Demand Phase 1
9 | A,B,C | R |  | 4365 | 5520 | 5521 | 4008 | Present Current Demand Phase 1
10 | A,B,C | R |  | 4366 | 5522 | 5523 | 4009 | Present Current Demand Phase 1
11 | A,B,C | R |  | 4367 | 5524 | 5525 | 4010 | Present Current Demand Phase 1
12 | A,B,C | R |  | 4368 | 5526 | 5527 | 4011 | Present Current Demand Phase 1
13 | A,B,C | R |  | 4369 | 5528 | 5529 | 4012 | Present Current Demand Phase 1
14 | A,B,C | R |  | 4370 | 5530 | 5531 | 4013 | Present Current Demand Phase 1
15 | A,B,C | R |  | 4371 | 5532 | 5533 | 4014 | Present Current Demand Phase 1
16 | A,B,C | R |  | 4372 | 5534 | 5535 | 4015 | Present Current Demand Phase 1
17 | A,B,C | R |  | 4373 | 5536 | 5537 | 4016 | Present Current Demand Phase 1
18 | A,B,C | R |  | 4374 | 5538 | 5539 | 4017 | Present Current Demand Phase 1
19 | A,B,C | R |  | 4375 | 5540 | 5541 | 4018 | Present Current Demand Phase 1
20 | A,B,C | R |  | 4376 | 5542 | 5543 | 4019 | Present Current Demand Phase 1
21 | A,B,C | R |  | 4377 | 5544 | 5545 | 4020 | Present Current Demand Phase 1
1 | A,B,C | R |  | 4378 | 5546 | 5547 | 4000 | Present Current Demand Phase 2
2 | A,B,C | R |  | 4379 | 5548 | 5549 | 4001 | Present Current Demand Phase 2
3 | A,B,C | R |  | 4380 | 5550 | 5551 | 4002 | Present Current Demand Phase 2
4 | A,B,C | R |  | 4381 | 5552 | 5553 | 4003 | Present Current Demand Phase 2
5 | A,B,C | R |  | 4382 | 5554 | 5555 | 4004 | Present Current Demand Phase 2
6 | A,B,C | R |  | 4383 | 5556 | 5557 | 4005 | Present Current Demand Phase 2
7 | A,B,C | R |  | 4384 | 5558 | 5559 | 4006 | Present Current Demand Phase 2
8 | A,B,C | R |  | 4385 | 5560 | 5561 | 4007 | Present Current Demand Phase 2
9 | A,B,C | R |  | 4386 | 5562 | 5563 | 4008 | Present Current Demand Phase 2
10 | A,B,C | R |  | 4387 | 5564 | 5565 | 4009 | Present Current Demand Phase 2
11 | A,B,C | R |  | 4388 | 5566 | 5567 | 4010 | Present Current Demand Phase 2
12 | A,B,C | R |  | 4389 | 5568 | 5569 | 4011 | Present Current Demand Phase 2
13 | A,B,C | R |  | 4390 | 5570 | 5571 | 4012 | Present Current Demand Phase 2
14 | A,B,C | R |  | 4391 | 5572 | 5573 | 4013 | Present Current Demand Phase 2
15 | A,B,C | R |  | 4392 | 5574 | 5575 | 4014 | Present Current Demand Phase 2
16 | A,B,C | R |  | 4393 | 5576 | 5577 | 4015 | Present Current Demand Phase 2
17 | A,B,C | R |  | 4394 | 5578 | 5579 | 4016 | Present Current Demand Phase 2
18 | A,B,C | R |  | 4395 | 5580 | 5581 | 4017 | Present Current Demand Phase 2
19 | A,B,C | R |  | 4396 | 5582 | 5583 | 4018 | Present Current Demand Phase 2
20 | A,B,C | R |  | 4397 | 5584 | 5585 | 4019 | Present Current Demand Phase 2
21 | A,B,C | R |  | 4398 | 5586 | 5587 | 4020 | Present Current Demand Phase 2
1 | A,B,C | R | NV | 4399 | 5588 | 5589 | 4000 | Max Current Demand Phase 1
2 | A,B,C | R | NV | 4400 | 5590 | 5591 | 4001 | Max Current Demand Phase 1
3 | A,B,C | R | NV | 4401 | 5592 | 5593 | 4002 | Max Current Demand Phase 1
4 | A,B,C | R | NV | 4402 | 5594 | 5595 | 4003 | Max Current Demand Phase 1
5 | A,B,C | R | NV | 4403 | 5596 | 5597 | 4004 | Max Current Demand Phase 1
6 | A,B,C | R | NV | 4404 | 5598 | 5599 | 4005 | Max Current Demand Phase 1
7 | A,B,C | R | NV | 4405 | 5600 | 5601 | 4006 | Max Current Demand Phase 1
8 | A,B,C | R | NV | 4406 | 5602 | 5603 | 4007 | Max Current Demand Phase 1
9 | A,B,C | R | NV | 4407 | 5604 | 5605 | 4008 | Max Current Demand Phase 1
10 | A,B,C | R | NV | 4408 | 5606 | 5607 | 4009 | Max Current Demand Phase 1
11 | A,B,C | R | NV | 4409 | 5608 | 5609 | 4010 | Max Current Demand Phase 1
12 | A,B,C | R | NV | 4410 | 5610 | 5611 | 4011 | Max Current Demand Phase 1
13 | A,B,C | R | NV | 4411 | 5612 | 5613 | 4012 | Max Current Demand Phase 1
14 | A,B,C | R | NV | 4412 | 5614 | 5615 | 4013 | Max Current Demand Phase 1
15 | A,B,C | R | NV | 4413 | 5616 | 5617 | 4014 | Max Current Demand Phase 1
16 | A,B,C | R | NV | 4414 | 5618 | 5619 | 4015 | Max Current Demand Phase 1
17 | A,B,C | R | NV | 4415 | 5620 | 5621 | 4016 | Max Current Demand Phase 1
18 | A,B,C | R | NV | 4416 | 5622 | 5623 | 4017 | Max Current Demand Phase 1
19 | A,B,C | R | NV | 4417 | 5624 | 5625 | 4018 | Max Current Demand Phase 1
20 | A,B,C | R | NV | 4418 | 5626 | 5627 | 4019 | Max Current Demand Phase 1
21 | A,B,C | R | NV | 4419 | 5628 | 5629 | 4020 | Max Current Demand Phase 1
1 | A,B,C | R | NV | 4420 | 5630 | 5631 | 4000 | Max Current Demand Phase 2
2 | A,B,C | R | NV | 4421 | 5632 | 5633 | 4001 | Max Current Demand Phase 2
3 | A,B,C | R | NV | 4422 | 5634 | 5635 | 4002 | Max Current Demand Phase 2
4 | A,B,C | R | NV | 4423 | 5636 | 5637 | 4003 | Max Current Demand Phase 2
5 | A,B,C | R | NV | 4424 | 5638 | 5639 | 4004 | Max Current Demand Phase 2
6 | A,B,C | R | NV | 4425 | 5640 | 5641 | 4005 | Max Current Demand Phase 2
7 | A,B,C | R | NV | 4426 | 5642 | 5643 | 4006 | Max Current Demand Phase 2
8 | A,B,C | R | NV | 4427 | 5644 | 5645 | 4007 | Max Current Demand Phase 2
9 | A,B,C | R | NV | 4428 | 5646 | 5647 | 4008 | Max Current Demand Phase 2
10 | A,B,C | R | NV | 4429 | 5648 | 5649 | 4009 | Max Current Demand Phase 2
11 | A,B,C | R | NV | 4430 | 5650 | 5651 | 4010 | Max Current Demand Phase 2
12 | A,B,C | R | NV | 4431 | 5652 | 5653 | 4011 | Max Current Demand Phase 2
13 | A,B,C | R | NV | 4432 | 5654 | 5655 | 4012 | Max Current Demand Phase 2
14 | A,B,C | R | NV | 4433 | 5656 | 5657 | 4013 | Max Current Demand Phase 2
15 | A,B,C | R | NV | 4434 | 5658 | 5659 | 4014 | Max Current Demand Phase 2
16 | A,B,C | R | NV | 4435 | 5660 | 5661 | 4015 | Max Current Demand Phase 2
17 | A,B,C | R | NV | 4436 | 5662 | 5663 | 4016 | Max Current Demand Phase 2
18 | A,B,C | R | NV | 4437 | 5664 | 5665 | 4017 | Max Current Demand Phase 2
19 | A,B,C | R | NV | 4438 | 5666 | 5667 | 4018 | Max Current Demand Phase 2
20 | A,B,C | R | NV | 4439 | 5668 | 5669 | 4019 | Max Current Demand Phase 2
21 | A,B,C | R | NV | 4440 | 5670 | 5671 | 4020 | Max Current Demand Phase 2
1 | A,B,C | R | NV | 4441 | 5672 | 5673 | 4000 | Max Current Phase 1
2 | A,B,C | R | NV | 4442 | 5674 | 5675 | 4001 | Max Current Phase 1
3 | A,B,C | R | NV | 4443 | 5676 | 5677 | 4002 | Max Current Phase 1
4 | A,B,C | R | NV | 4444 | 5678 | 5679 | 4003 | Max Current Phase 1
5 | A,B,C | R | NV | 4445 | 5680 | 5681 | 4004 | Max Current Phase 1
6 | A,B,C | R | NV | 4446 | 5682 | 5683 | 4005 | Max Current Phase 1
7 | A,B,C | R | NV | 4447 | 5684 | 5685 | 4006 | Max Current Phase 1
8 | A,B,C | R | NV | 4448 | 5686 | 5687 | 4007 | Max Current Phase 1
9 | A,B,C | R | NV | 4449 | 5688 | 5689 | 4008 | Max Current Phase 1
10 | A,B,C | R | NV | 4450 | 5690 | 5691 | 4009 | Max Current Phase 1
11 | A,B,C | R | NV | 4451 | 5692 | 5693 | 4010 | Max Current Phase 1
12 | A,B,C | R | NV | 4452 | 5694 | 5695 | 4011 | Max Current Phase 1
13 | A,B,C | R | NV | 4453 | 5696 | 5697 | 4012 | Max Current Phase 1
14 | A,B,C | R | NV | 4454 | 5698 | 5699 | 4013 | Max Current Phase 1
15 | A,B,C | R | NV | 4455 | 5700 | 5701 | 4014 | Max Current Phase 1
16 | A,B,C | R | NV | 4456 | 5702 | 5703 | 4015 | Max Current Phase 1
17 | A,B,C | R | NV | 4457 | 5704 | 5705 | 4016 | Max Current Phase 1
18 | A,B,C | R | NV | 4458 | 5706 | 5707 | 4017 | Max Current Phase 1
19 | A,B,C | R | NV | 4459 | 5708 | 5709 | 4018 | Max Current Phase 1
20 | A,B,C | R | NV | 4460 | 5710 | 5711 | 4019 | Max Current Phase 1
21 | A,B,C | R | NV | 4461 | 5712 | 5713 | 4020 | Max Current Phase 1
1 | A,B,C | R | NV | 4462 | 5714 | 5715 | 4000 | Max Current Phase 2
2 | A,B,C | R | NV | 4463 | 5716 | 5717 | 4001 | Max Current Phase 2
3 | A,B,C | R | NV | 4464 | 5718 | 5719 | 4002 | Max Current Phase 2
4 | A,B,C | R | NV | 4465 | 5720 | 5721 | 4003 | Max Current Phase 2
5 | A,B,C | R | NV | 4466 | 5722 | 5723 | 4004 | Max Current Phase 2
6 | A,B,C | R | NV | 4467 | 5724 | 5725 | 4005 | Max Current Phase 2
7 | A,B,C | R | NV | 4468 | 5726 | 5727 | 4006 | Max Current Phase 2
8 | A,B,C | R | NV | 4469 | 5728 | 5729 | 4007 | Max Current Phase 2
9 | A,B,C | R | NV | 4470 | 5730 | 5731 | 4008 | Max Current Phase 2
10 | A,B,C | R | NV | 4471 | 5732 | 5733 | 4009 | Max Current Phase 2
11 | A,B,C | R | NV | 4472 | 5734 | 5735 | 4010 | Max Current Phase 2
12 | A,B,C | R | NV | 4473 | 5736 | 5737 | 4011 | Max Current Phase 2
13 | A,B,C | R | NV | 4474 | 5738 | 5739 | 4012 | Max Current Phase 2
14 | A,B,C | R | NV | 4475 | 5740 | 5741 | 4013 | Max Current Phase 2
15 | A,B,C | R | NV | 4476 | 5742 | 5743 | 4014 | Max Current Phase 2
16 | A,B,C | R | NV | 4477 | 5744 | 5745 | 4015 | Max Current Phase 2
17 | A,B,C | R | NV | 4478 | 5746 | 5747 | 4016 | Max Current Phase 2
18 | A,B,C | R | NV | 4479 | 5748 | 5749 | 4017 | Max Current Phase 2
19 | A,B,C | R | NV | 4480 | 5750 | 5751 | 4018 | Max Current Phase 2
20 | A,B,C | R | NV | 4481 | 5752 | 5753 | 4019 | Max Current Phase 2
21 | A,B,C | R | NV | 4482 | 5754 | 5755 | 4020 | Max Current Phase 2
1 | A | R | NV | 4483 | 5756 | 5757 | 4021 | Max KW Total
2 | A | R | NV | 4484 | 5758 | 5759 | 4022 | Max KW Total
3 | A | R | NV | 4485 | 5760 | 5761 | 4023 | Max KW Total
4 | A | R | NV | 4486 | 5762 | 5763 | 4024 | Max KW Total
5 | A | R | NV | 4487 | 5764 | 5765 | 4025 | Max KW Total
6 | A | R | NV | 4488 | 5766 | 5767 | 4026 | Max KW Total
7 | A | R | NV | 4489 | 5768 | 5769 | 4027 | Max KW Total
8 | A | R | NV | 4490 | 5770 | 5771 | 4028 | Max KW Total
9 | A | R | NV | 4491 | 5772 | 5773 | 4029 | Max KW Total
10 | A | R | NV | 4492 | 5774 | 5775 | 4030 | Max KW Total
11 | A | R | NV | 4493 | 5776 | 5777 | 4031 | Max KW Total
12 | A | R | NV | 4494 | 5778 | 5779 | 4032 | Max KW Total
13 | A | R | NV | 4495 | 5780 | 5781 | 4033 | Max KW Total
14 | A | R | NV | 4496 | 5782 | 5783 | 4034 | Max KW Total
15 | A | R | NV | 4497 | 5784 | 5785 | 4035 | Max KW Total
16 | A | R | NV | 4498 | 5786 | 5787 | 4036 | Max KW Total
17 | A | R | NV | 4499 | 5788 | 5789 | 4037 | Max KW Total
18 | A | R | NV | 4500 | 5790 | 5791 | 4038 | Max KW Total
19 | A | R | NV | 4501 | 5792 | 5793 | 4039 | Max KW Total
20 | A | R | NV | 4502 | 5794 | 5795 | 4040 | Max KW Total
21 | A | R | NV | 4503 | 5796 | 5797 | 4041 | Max KW Total
1 | A | R |  | 4504 | 5798 | 5799 | 4021 | KVA Total
2 | A | R |  | 4505 | 5800 | 5801 | 4022 | KVA Total
3 | A | R |  | 4506 | 5802 | 5803 | 4023 | KVA Total
4 | A | R |  | 4507 | 5804 | 5805 | 4024 | KVA Total
5 | A | R |  | 4508 | 5806 | 5807 | 4025 | KVA Total
6 | A | R |  | 4509 | 5808 | 5809 | 4026 | KVA Total
7 | A | R |  | 4510 | 5810 | 5811 | 4027 | KVA Total
8 | A | R |  | 4511 | 5812 | 5813 | 4028 | KVA Total
9 | A | R |  | 4512 | 5814 | 5815 | 4029 | KVA Total
10 | A | R |  | 4513 | 5816 | 5817 | 4030 | KVA Total
11 | A | R |  | 4514 | 5818 | 5819 | 4031 | KVA Total
12 | A | R |  | 4515 | 5820 | 5821 | 4032 | KVA Total
13 | A | R |  | 4516 | 5822 | 5823 | 4033 | KVA Total
14 | A | R |  | 4517 | 5824 | 5825 | 4034 | KVA Total
15 | A | R |  | 4518 | 5826 | 5827 | 4035 | KVA Total
16 | A | R |  | 4519 | 5828 | 5829 | 4036 | KVA Total
17 | A | R |  | 4520 | 5830 | 5831 | 4037 | KVA Total
18 | A | R |  | 4521 | 5832 | 5833 | 4038 | KVA Total
19 | A | R |  | 4522 | 5834 | 5835 | 4039 | KVA Total
20 | A | R |  | 4523 | 5836 | 5837 | 4040 | KVA Total
21 | A | R |  | 4524 | 5838 | 5839 | 4041 | KVA Total
1 | A | R |  | 4525 | 5840 | 5841 | 4021 | KVA Phase 1
2 | A | R |  | 4526 | 5842 | 5843 | 4022 | KVA Phase 1
3 | A | R |  | 4527 | 5844 | 5845 | 4023 | KVA Phase 1
4 | A | R |  | 4528 | 5846 | 5847 | 4024 | KVA Phase 1
5 | A | R |  | 4529 | 5848 | 5849 | 4025 | KVA Phase 1
6 | A | R |  | 4530 | 5850 | 5851 | 4026 | KVA Phase 1
7 | A | R |  | 4531 | 5852 | 5853 | 4027 | KVA Phase 1
8 | A | R |  | 4532 | 5854 | 5855 | 4028 | KVA Phase 1
9 | A | R |  | 4533 | 5856 | 5857 | 4029 | KVA Phase 1
10 | A | R |  | 4534 | 5858 | 5859 | 4030 | KVA Phase 1
11 | A | R |  | 4535 | 5860 | 5861 | 4031 | KVA Phase 1
12 | A | R |  | 4536 | 5862 | 5863 | 4032 | KVA Phase 1
13 | A | R |  | 4537 | 5864 | 5865 | 4033 | KVA Phase 1
14 | A | R |  | 4538 | 5866 | 5867 | 4034 | KVA Phase 1
15 | A | R |  | 4539 | 5868 | 5869 | 4035 | KVA Phase 1
16 | A | R |  | 4540 | 5870 | 5871 | 4036 | KVA Phase 1
17 | A | R |  | 4541 | 5872 | 5873 | 4037 | KVA Phase 1
18 | A | R |  | 4542 | 5874 | 5875 | 4038 | KVA Phase 1
19 | A | R |  | 4543 | 5876 | 5877 | 4039 | KVA Phase 1
20 | A | R |  | 4544 | 5878 | 5879 | 4040 | KVA Phase 1
21 | A | R |  | 4545 | 5880 | 5881 | 4041 | KVA Phase 1
1 | A | R |  | 4546 | 5882 | 5883 | 4021 | KVA Phase 2
2 | A | R |  | 4547 | 5884 | 5885 | 4022 | KVA Phase 2
3 | A | R |  | 4548 | 5886 | 5887 | 4023 | KVA Phase 2
4 | A | R |  | 4549 | 5888 | 5889 | 4024 | KVA Phase 2
5 | A | R |  | 4550 | 5890 | 5891 | 4025 | KVA Phase 2
6 | A | R |  | 4551 | 5892 | 5893 | 4026 | KVA Phase 2
7 | A | R |  | 4552 | 5894 | 5895 | 4027 | KVA Phase 2
8 | A | R |  | 4553 | 5896 | 5897 | 4028 | KVA Phase 2
9 | A | R |  | 4554 | 5898 | 5899 | 4029 | KVA Phase 2
10 | A | R |  | 4555 | 5900 | 5901 | 4030 | KVA Phase 2
11 | A | R |  | 4556 | 5902 | 5903 | 4031 | KVA Phase 2
12 | A | R |  | 4557 | 5904 | 5905 | 4032 | KVA Phase 2
13 | A | R |  | 4558 | 5906 | 5907 | 4033 | KVA Phase 2
14 | A | R |  | 4559 | 5908 | 5909 | 4034 | KVA Phase 2
15 | A | R |  | 4560 | 5910 | 5911 | 4035 | KVA Phase 2
16 | A | R |  | 4561 | 5912 | 5913 | 4036 | KVA Phase 2
17 | A | R |  | 4562 | 5914 | 5915 | 4037 | KVA Phase 2
18 | A | R |  | 4563 | 5916 | 5917 | 4038 | KVA Phase 2
19 | A | R |  | 4564 | 5918 | 5919 | 4039 | KVA Phase 2
20 | A | R |  | 4565 | 5920 | 5921 | 4040 | KVA Phase 2
21 | A | R |  | 4566 | 5922 | 5923 | 4041 | KVA Phase 2
total registers in this section
1491

## -=E30 3PH Circuits=-
14 3-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed configuration
[5 empty] | Top Feed | Bottom Feed
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 3 | 2 | B
|  | 5 | 3 | C
| 2 | 2 | 1 | A
|  | 4 | 2 | B
|  | 6 | 3 | C
| 3 | 7 | 1 | A
|  | 9 | 2 | B
|  | 11 | 3 | C
| 4 | 8 | 1 | A
|  | 10 | 2 | B
|  | 12 | 3 | C
| 5 | 13 | 1 | A
|  | 15 | 2 | B
|  | 17 | 3 | C
| 6 | 14 | 1 | A
|  | 16 | 2 | B
|  | 18 | 3 | C
| 7 | 19 | 1 | A
|  | 21 | 2 | B
|  | 23 | 3 | C
| 8 | 20 | 1 | A
|  | 22 | 2 | B
|  | 24 | 3 | C
| 9 | 25 | 1 | A
|  | 27 | 2 | B
|  | 29 | 3 | C
| 10 | 26 | 1 | A
|  | 28 | 2 | B
|  | 30 | 3 | C
| 11 | 31 | 1 | A
|  | 33 | 2 | B
|  | 35 | 3 | C
| 12 | 32 | 1 | A
|  | 34 | 2 | B
|  | 36 | 3 | C
| 13 | 37 | 1 | A
|  | 39 | 2 | B
|  | 41 | 3 | C
| 14 | 38 | 1 | A
|  | 40 | 2 | B
|  | 42 | 3 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A | Sequential
|  | 2 | 2 | B
|  | 3 | 3 | C
| 2 | 4 | 1 | A
|  | 5 | 2 | B
|  | 6 | 3 | C
| 3 | 7 | 1 | A
|  | 8 | 2 | B
|  | 9 | 3 | C
| 4 | 10 | 1 | A
|  | 11 | 2 | B
|  | 12 | 3 | C
| 5 | 13 | 1 | A
|  | 14 | 2 | B
|  | 15 | 3 | C
| 6 | 16 | 1 | A
|  | 17 | 2 | B
|  | 18 | 3 | C
| 7 | 19 | 1 | A
|  | 20 | 2 | B
|  | 21 | 3 | C
| 8 | 22 | 1 | A
|  | 23 | 2 | B
|  | 24 | 3 | C
| 9 | 25 | 1 | A
|  | 26 | 2 | B
|  | 27 | 3 | C
| 10 | 28 | 1 | A
|  | 29 | 2 | B
|  | 30 | 3 | C
| 11 | 31 | 1 | A
|  | 32 | 2 | B
|  | 33 | 3 | C
| 12 | 34 | 1 | A
|  | 35 | 2 | B
|  | 36 | 3 | C
| 13 | 37 | 1 | A
|  | 38 | 2 | B
|  | 39 | 3 | C
| 14 | 40 | 1 | A
|  | 41 | 2 | B
|  | 42 | 3 | C
Voltage/Current Phasing for Single Row: Odd / Even configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A | Odd / Even
|  | 3 | 2 | B
|  | 5 | 3 | C
| 2 | 7 | 1 | A
|  | 9 | 2 | B
|  | 11 | 3 | C
| 3 | 13 | 1 | A
|  | 15 | 2 | B
|  | 17 | 3 | C
| 4 | 19 | 1 | A
|  | 21 | 2 | B
|  | 23 | 3 | C
| 5 | 25 | 1 | A
|  | 27 | 2 | B
|  | 29 | 3 | C
| 6 | 31 | 1 | A
|  | 33 | 2 | B
|  | 35 | 3 | C
| 7 | 37 | 1 | A
|  | 39 | 2 | B
|  | 41 | 3 | C
| 8 | 2 | 1 | A
|  | 4 | 2 | B
|  | 6 | 3 | C
| 9 | 8 | 1 | A
|  | 10 | 2 | B
|  | 12 | 3 | C
| 10 | 14 | 1 | A
|  | 16 | 2 | B
|  | 18 | 3 | C
| 11 | 20 | 1 | A
|  | 22 | 2 | B
|  | 24 | 3 | C
| 12 | 26 | 1 | A
|  | 28 | 2 | B
|  | 30 | 3 | C
| 13 | 32 | 1 | A
|  | 34 | 2 | B
|  | 36 | 3 | C
| 14 | 38 | 1 | A
|  | 40 | 2 | B
|  | 42 | 3 | C

## -=E31 3PH Circuits=-
14 3-PHASE CIRCUITS
Voltage/Current Phasing for Top Feed configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 3 | 2 | B
|  | 5 | 3 | C
| 2 | 2 | 1 | A
|  | 4 | 2 | B
|  | 6 | 3 | C
| 3 | 7 | 1 | A
|  | 9 | 2 | B
|  | 11 | 3 | C
| 4 | 8 | 1 | A
|  | 10 | 2 | B
|  | 12 | 3 | C
| 5 | 13 | 1 | A
|  | 15 | 2 | B
|  | 17 | 3 | C
| 6 | 14 | 1 | A
|  | 16 | 2 | B
|  | 18 | 3 | C
| 7 | 19 | 1 | A
|  | 21 | 2 | B
|  | 23 | 3 | C
| 8 | 20 | 1 | A
|  | 22 | 2 | B
|  | 24 | 3 | C
| 9 | 25 | 1 | A
|  | 27 | 2 | B
|  | 29 | 3 | C
| 10 | 26 | 1 | A
|  | 28 | 2 | B
|  | 30 | 3 | C
| 11 | 31 | 1 | A
|  | 33 | 2 | B
|  | 35 | 3 | C
| 12 | 32 | 1 | A
|  | 34 | 2 | B
|  | 36 | 3 | C
| 13 | 37 | 1 | A
|  | 39 | 2 | B
|  | 41 | 3 | C
| 14 | 38 | 1 | A
|  | 40 | 2 | B
|  | 42 | 3 | C
Voltage/Current Phasing for Single Row: Sequential configuration
|  | CT | Current | Voltage
| Circuit | Number | Phase | Phase
| 1 | 1 | 1 | A
|  | 2 | 2 | B
|  | 3 | 3 | C
| 2 | 4 | 1 | A
|  | 5 | 2 | B
|  | 6 | 3 | C
| 3 | 7 | 1 | A
|  | 8 | 2 | B
|  | 9 | 3 | C
| 4 | 10 | 1 | A
|  | 11 | 2 | B
|  | 12 | 3 | C
| 5 | 13 | 1 | A
|  | 14 | 2 | B
|  | 15 | 3 | C
| 6 | 16 | 1 | A
|  | 17 | 2 | B
|  | 18 | 3 | C
| 7 | 19 | 1 | A
|  | 20 | 2 | B
|  | 21 | 3 | C
| 8 | 22 | 1 | A
|  | 23 | 2 | B
|  | 24 | 3 | C
| 9 | 25 | 1 | A
|  | 26 | 2 | B
|  | 27 | 3 | C
| 10 | 28 | 1 | A
|  | 29 | 2 | B
|  | 30 | 3 | C
| 11 | 31 | 1 | A
|  | 32 | 2 | B
|  | 33 | 3 | C
| 12 | 34 | 1 | A
|  | 35 | 2 | B
|  | 36 | 3 | C
| 13 | 37 | 1 | A
|  | 38 | 2 | B
|  | 39 | 3 | C
| 14 | 40 | 1 | A
|  | 41 | 2 | B
|  | 42 | 3 | C

## 3PH Point Map
Note: This map assumes that all 3ph sets of branch CT's are identical
Modbus
Circuit | Model (A,B,C) | R/W | NV | Integer Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description
SCALE REGISTERS
1 | A,B,C | R | NV | 7000 |  |  |  | Current Scale
2 | A,B,C | R | NV | 7001 |  |  |  | Current Scale
3 | A,B,C | R | NV | 7002 |  |  |  | Current Scale
4 | A,B,C | R | NV | 7003 |  |  |  | Current Scale
5 | A,B,C | R | NV | 7004 |  |  |  | Current Scale
6 | A,B,C | R | NV | 7005 |  |  |  | Current Scale
7 | A,B,C | R | NV | 7006 |  |  |  | Current Scale
8 | A,B,C | R | NV | 7007 |  |  |  | Current Scale
9 | A,B,C | R | NV | 7008 |  |  |  | Current Scale
10 | A,B,C | R | NV | 7009 |  |  |  | Current Scale
11 | A,B,C | R | NV | 7010 |  |  |  | Current Scale
12 | A,B,C | R | NV | 7011 |  |  |  | Current Scale
13 | A,B,C | R | NV | 7012 |  |  |  | Current Scale
14 | A,B,C | R | NV | 7013 |  |  |  | Current Scale
1 | A | R | NV | 7014 |  |  |  | Power Scale
2 | A | R | NV | 7015 |  |  |  | Power Scale
3 | A | R | NV | 7016 |  |  |  | Power Scale
4 | A | R | NV | 7017 |  |  |  | Power Scale
5 | A | R | NV | 7018 |  |  |  | Power Scale
6 | A | R | NV | 7019 |  |  |  | Power Scale
7 | A | R | NV | 7020 |  |  |  | Power Scale
8 | A | R | NV | 7021 |  |  |  | Power Scale
9 | A | R | NV | 7022 |  |  |  | Power Scale
10 | A | R | NV | 7023 |  |  |  | Power Scale
11 | A | R | NV | 7024 |  |  |  | Power Scale
12 | A | R | NV | 7025 |  |  |  | Power Scale
13 | A | R | NV | 7026 |  |  |  | Power Scale
14 | A | R | NV | 7027 |  |  |  | Power Scale
1 | A | R | NV | 7028 |  |  |  | Energy Scale
2 | A | R | NV | 7029 |  |  |  | Energy Scale
3 | A | R | NV | 7030 |  |  |  | Energy Scale
4 | A | R | NV | 7031 |  |  |  | Energy Scale
5 | A | R | NV | 7032 |  |  |  | Energy Scale
6 | A | R | NV | 7033 |  |  |  | Energy Scale
7 | A | R | NV | 7034 |  |  |  | Energy Scale
8 | A | R | NV | 7035 |  |  |  | Energy Scale
9 | A | R | NV | 7036 |  |  |  | Energy Scale
10 | A | R | NV | 7037 |  |  |  | Energy Scale
11 | A | R | NV | 7038 |  |  |  | Energy Scale
12 | A | R | NV | 7039 |  |  |  | Energy Scale
13 | A | R | NV | 7040 |  |  |  | Energy Scale
14 | A | R | NV | 7041 |  |  |  | Energy Scale
RESETS
Also resets corresponding registers in 1PH and 2PH maps
1 | A,B,C | W |  | 7042 |  |  |  | Reset - Write the listed value to perform the listed reset:
10203 = Clear KWH value to zero
29877 = Clear all Max Current and Max KW values to zero
2 | A,B,C | W |  | 7043 |  |  |  | Reset
3 | A,B,C | W |  | 7044 |  |  |  | Reset
4 | A,B,C | W |  | 7045 |  |  |  | Reset
5 | A,B,C | W |  | 7046 |  |  |  | Reset
6 | A,B,C | W |  | 7047 |  |  |  | Reset
7 | A,B,C | W |  | 7048 |  |  |  | Reset
8 | A,B,C | W |  | 7049 |  |  |  | Reset
9 | A,B,C | W |  | 7050 |  |  |  | Reset
10 | A,B,C | W |  | 7051 |  |  |  | Reset
11 | A,B,C | W |  | 7052 |  |  |  | Reset
12 | A,B,C | W |  | 7053 |  |  |  | Reset
13 | A,B,C | W |  | 7054 |  |  |  | Reset
14 | A,B,C | W |  | 7055 |  |  |  | Reset
DATA
1 | A | R | NV | 7056 | 8000 | 8001 | 7028 | KWH (MSW)
1 | A | R | NV | 7057 |  |  |  | KWH (LSW)
2 | A | R | NV | 7058 | 8002 | 8003 | 7029 | KWH (MSW)
2 | A | R | NV | 7059 |  |  |  | KWH (LSW)
3 | A | R | NV | 7060 | 8004 | 8005 | 7030 | KWH (MSW)
3 | A | R | NV | 7061 |  |  |  | KWH (LSW)
4 | A | R | NV | 7062 | 8006 | 8007 | 7031 | KWH (MSW)
4 | A | R | NV | 7063 |  |  |  | KWH (LSW)
5 | A | R | NV | 7064 | 8008 | 8009 | 7032 | KWH (MSW)
5 | A | R | NV | 7065 |  |  |  | KWH (LSW)
6 | A | R | NV | 7066 | 8010 | 8011 | 7033 | KWH (MSW)
6 | A | R | NV | 7067 |  |  |  | KWH (LSW)
7 | A | R | NV | 7068 | 8012 | 8013 | 7034 | KWH (MSW)
7 | A | R | NV | 7069 |  |  |  | KWH (LSW)
8 | A | R | NV | 7070 | 8014 | 8015 | 7035 | KWH (MSW)
8 | A | R | NV | 7071 |  |  |  | KWH (LSW)
9 | A | R | NV | 7072 | 8016 | 8017 | 7036 | KWH (MSW)
9 | A | R | NV | 7073 |  |  |  | KWH (LSW)
10 | A | R | NV | 7074 | 8018 | 8019 | 7037 | KWH (MSW)
10 | A | R | NV | 7075 |  |  |  | KWH (LSW)
11 | A | R | NV | 7076 | 8020 | 8021 | 7038 | KWH (MSW)
11 | A | R | NV | 7077 |  |  |  | KWH (LSW)
12 | A | R | NV | 7078 | 8022 | 8023 | 7039 | KWH (MSW)
12 | A | R | NV | 7079 |  |  |  | KWH (LSW)
13 | A | R | NV | 7080 | 8024 | 8025 | 7040 | KWH (MSW)
13 | A | R | NV | 7081 |  |  |  | KWH (LSW)
14 | A | R | NV | 7082 | 8026 | 8027 | 7041 | KWH (MSW)
14 | A | R | NV | 7083 |  |  |  | KWH (LSW)
1 | A | R |  | 7084 | 8028 | 8029 | 7014 | KW Total
2 | A | R |  | 7085 | 8030 | 8031 | 7015 | KW Total
3 | A | R |  | 7086 | 8032 | 8033 | 7016 | KW Total
4 | A | R |  | 7087 | 8034 | 8035 | 7017 | KW Total
5 | A | R |  | 7088 | 8036 | 8037 | 7018 | KW Total
6 | A | R |  | 7089 | 8038 | 8039 | 7019 | KW Total
7 | A | R |  | 7090 | 8040 | 8041 | 7020 | KW Total
8 | A | R |  | 7091 | 8042 | 8043 | 7021 | KW Total
9 | A | R |  | 7092 | 8044 | 8045 | 7022 | KW Total
10 | A | R |  | 7093 | 8046 | 8047 | 7023 | KW Total
11 | A | R |  | 7094 | 8048 | 8049 | 7024 | KW Total
12 | A | R |  | 7095 | 8050 | 8051 | 7025 | KW Total
13 | A | R |  | 7096 | 8052 | 8053 | 7026 | KW Total
14 | A | R |  | 7097 | 8054 | 8055 | 7027 | KW Total
1 | A | R |  | 7098 | 8056 | 8057 | -3 | PF Total
2 | A | R |  | 7099 | 8058 | 8059 | -3 | PF Total
3 | A | R |  | 7100 | 8060 | 8061 | -3 | PF Total
4 | A | R |  | 7101 | 8062 | 8063 | -3 | PF Total
5 | A | R |  | 7102 | 8064 | 8065 | -3 | PF Total
6 | A | R |  | 7103 | 8066 | 8067 | -3 | PF Total
7 | A | R |  | 7104 | 8068 | 8069 | -3 | PF Total
8 | A | R |  | 7105 | 8070 | 8071 | -3 | PF Total
9 | A | R |  | 7106 | 8072 | 8073 | -3 | PF Total
10 | A | R |  | 7107 | 8074 | 8075 | -3 | PF Total
11 | A | R |  | 7108 | 8076 | 8077 | -3 | PF Total
12 | A | R |  | 7109 | 8078 | 8079 | -3 | PF Total
13 | A | R |  | 7110 | 8080 | 8081 | -3 | PF Total
14 | A | R |  | 7111 | 8082 | 8083 | -3 | PF Total
1 | A,B,C | R |  | 7112 | 8084 | 8085 | 7000 | Current Average of 3 phases
2 | A,B,C | R |  | 7113 | 8086 | 8087 | 7001 | Current Average of 3 phases
3 | A,B,C | R |  | 7114 | 8088 | 8089 | 7002 | Current Average of 3 phases
4 | A,B,C | R |  | 7115 | 8090 | 8091 | 7003 | Current Average of 3 phases
5 | A,B,C | R |  | 7116 | 8092 | 8093 | 7004 | Current Average of 3 phases
6 | A,B,C | R |  | 7117 | 8094 | 8095 | 7005 | Current Average of 3 phases
7 | A,B,C | R |  | 7118 | 8096 | 8097 | 7006 | Current Average of 3 phases
8 | A,B,C | R |  | 7119 | 8098 | 8099 | 7007 | Current Average of 3 phases
9 | A,B,C | R |  | 7120 | 8100 | 8101 | 7008 | Current Average of 3 phases
10 | A,B,C | R |  | 7121 | 8102 | 8103 | 7009 | Current Average of 3 phases
11 | A,B,C | R |  | 7122 | 8104 | 8105 | 7010 | Current Average of 3 phases
12 | A,B,C | R |  | 7123 | 8106 | 8107 | 7011 | Current Average of 3 phases
13 | A,B,C | R |  | 7124 | 8108 | 8109 | 7012 | Current Average of 3 phases
14 | A,B,C | R |  | 7125 | 8110 | 8111 | 7013 | Current Average of 3 phases
1 | A | R |  | 7126 | 8112 | 8113 | 7014 | KW Phase 1
2 | A | R |  | 7127 | 8114 | 8115 | 7015 | KW Phase 1
3 | A | R |  | 7128 | 8116 | 8117 | 7016 | KW Phase 1
4 | A | R |  | 7129 | 8118 | 8119 | 7017 | KW Phase 1
5 | A | R |  | 7130 | 8120 | 8121 | 7018 | KW Phase 1
6 | A | R |  | 7131 | 8122 | 8123 | 7019 | KW Phase 1
7 | A | R |  | 7132 | 8124 | 8125 | 7020 | KW Phase 1
8 | A | R |  | 7133 | 8126 | 8127 | 7021 | KW Phase 1
9 | A | R |  | 7134 | 8128 | 8129 | 7022 | KW Phase 1
10 | A | R |  | 7135 | 8130 | 8131 | 7023 | KW Phase 1
11 | A | R |  | 7136 | 8132 | 8133 | 7024 | KW Phase 1
12 | A | R |  | 7137 | 8134 | 8135 | 7025 | KW Phase 1
13 | A | R |  | 7138 | 8136 | 8137 | 7026 | KW Phase 1
14 | A | R |  | 7139 | 8138 | 8139 | 7027 | KW Phase 1
1 | A | R |  | 7140 | 8140 | 8141 | 7014 | KW Phase 2
2 | A | R |  | 7141 | 8142 | 8143 | 7015 | KW Phase 2
3 | A | R |  | 7142 | 8144 | 8145 | 7016 | KW Phase 2
4 | A | R |  | 7143 | 8146 | 8147 | 7017 | KW Phase 2
5 | A | R |  | 7144 | 8148 | 8149 | 7018 | KW Phase 2
6 | A | R |  | 7145 | 8150 | 8151 | 7019 | KW Phase 2
7 | A | R |  | 7146 | 8152 | 8153 | 7020 | KW Phase 2
8 | A | R |  | 7147 | 8154 | 8155 | 7021 | KW Phase 2
9 | A | R |  | 7148 | 8156 | 8157 | 7022 | KW Phase 2
10 | A | R |  | 7149 | 8158 | 8159 | 7023 | KW Phase 2
11 | A | R |  | 7150 | 8160 | 8161 | 7024 | KW Phase 2
12 | A | R |  | 7151 | 8162 | 8163 | 7025 | KW Phase 2
13 | A | R |  | 7152 | 8164 | 8165 | 7026 | KW Phase 2
14 | A | R |  | 7153 | 8166 | 8167 | 7027 | KW Phase 2
1 | A | R |  | 7154 | 8168 | 8169 | 7014 | KW Phase 3
2 | A | R |  | 7155 | 8170 | 8171 | 7015 | KW Phase 3
3 | A | R |  | 7156 | 8172 | 8173 | 7016 | KW Phase 3
4 | A | R |  | 7157 | 8174 | 8175 | 7017 | KW Phase 3
5 | A | R |  | 7158 | 8176 | 8177 | 7018 | KW Phase 3
6 | A | R |  | 7159 | 8178 | 8179 | 7019 | KW Phase 3
7 | A | R |  | 7160 | 8180 | 8181 | 7020 | KW Phase 3
8 | A | R |  | 7161 | 8182 | 8183 | 7021 | KW Phase 3
9 | A | R |  | 7162 | 8184 | 8185 | 7022 | KW Phase 3
10 | A | R |  | 7163 | 8186 | 8187 | 7023 | KW Phase 3
11 | A | R |  | 7164 | 8188 | 8189 | 7024 | KW Phase 3
12 | A | R |  | 7165 | 8190 | 8191 | 7025 | KW Phase 3
13 | A | R |  | 7166 | 8192 | 8193 | 7026 | KW Phase 3
14 | A | R |  | 7167 | 8194 | 8195 | 7027 | KW Phase 3
1 | A | R |  | 7168 | 8196 | 8197 | -3 | PF Phase 1
2 | A | R |  | 7169 | 8198 | 8199 | -3 | PF Phase 1
3 | A | R |  | 7170 | 8200 | 8201 | -3 | PF Phase 1
4 | A | R |  | 7171 | 8202 | 8203 | -3 | PF Phase 1
5 | A | R |  | 7172 | 8204 | 8205 | -3 | PF Phase 1
6 | A | R |  | 7173 | 8206 | 8207 | -3 | PF Phase 1
7 | A | R |  | 7174 | 8208 | 8209 | -3 | PF Phase 1
8 | A | R |  | 7175 | 8210 | 8211 | -3 | PF Phase 1
9 | A | R |  | 7176 | 8212 | 8213 | -3 | PF Phase 1
10 | A | R |  | 7177 | 8214 | 8215 | -3 | PF Phase 1
11 | A | R |  | 7178 | 8216 | 8217 | -3 | PF Phase 1
12 | A | R |  | 7179 | 8218 | 8219 | -3 | PF Phase 1
13 | A | R |  | 7180 | 8220 | 8221 | -3 | PF Phase 1
14 | A | R |  | 7181 | 8222 | 8223 | -3 | PF Phase 1
1 | A | R |  | 7182 | 8224 | 8225 | -3 | PF Phase 2
2 | A | R |  | 7183 | 8226 | 8227 | -3 | PF Phase 2
3 | A | R |  | 7184 | 8228 | 8229 | -3 | PF Phase 2
4 | A | R |  | 7185 | 8230 | 8231 | -3 | PF Phase 2
5 | A | R |  | 7186 | 8232 | 8233 | -3 | PF Phase 2
6 | A | R |  | 7187 | 8234 | 8235 | -3 | PF Phase 2
7 | A | R |  | 7188 | 8236 | 8237 | -3 | PF Phase 2
8 | A | R |  | 7189 | 8238 | 8239 | -3 | PF Phase 2
9 | A | R |  | 7190 | 8240 | 8241 | -3 | PF Phase 2
10 | A | R |  | 7191 | 8242 | 8243 | -3 | PF Phase 2
11 | A | R |  | 7192 | 8244 | 8245 | -3 | PF Phase 2
12 | A | R |  | 7193 | 8246 | 8247 | -3 | PF Phase 2
13 | A | R |  | 7194 | 8248 | 8249 | -3 | PF Phase 2
14 | A | R |  | 7195 | 8250 | 8251 | -3 | PF Phase 2
1 | A | R |  | 7196 | 8252 | 8253 | -3 | PF Phase 3
2 | A | R |  | 7197 | 8254 | 8255 | -3 | PF Phase 3
3 | A | R |  | 7198 | 8256 | 8257 | -3 | PF Phase 3
4 | A | R |  | 7199 | 8258 | 8259 | -3 | PF Phase 3
5 | A | R |  | 7200 | 8260 | 8261 | -3 | PF Phase 3
6 | A | R |  | 7201 | 8262 | 8263 | -3 | PF Phase 3
7 | A | R |  | 7202 | 8264 | 8265 | -3 | PF Phase 3
8 | A | R |  | 7203 | 8266 | 8267 | -3 | PF Phase 3
9 | A | R |  | 7204 | 8268 | 8269 | -3 | PF Phase 3
10 | A | R |  | 7205 | 8270 | 8271 | -3 | PF Phase 3
11 | A | R |  | 7206 | 8272 | 8273 | -3 | PF Phase 3
12 | A | R |  | 7207 | 8274 | 8275 | -3 | PF Phase 3
13 | A | R |  | 7208 | 8276 | 8277 | -3 | PF Phase 3
14 | A | R |  | 7209 | 8278 | 8279 | -3 | PF Phase 3
1 | A,B,C | R |  | 7210 | 8280 | 8281 | 7000 | Current Phase 1
2 | A,B,C | R |  | 7211 | 8282 | 8283 | 7001 | Current Phase 1
3 | A,B,C | R |  | 7212 | 8284 | 8285 | 7002 | Current Phase 1
4 | A,B,C | R |  | 7213 | 8286 | 8287 | 7003 | Current Phase 1
5 | A,B,C | R |  | 7214 | 8288 | 8289 | 7004 | Current Phase 1
6 | A,B,C | R |  | 7215 | 8290 | 8291 | 7005 | Current Phase 1
7 | A,B,C | R |  | 7216 | 8292 | 8293 | 7006 | Current Phase 1
8 | A,B,C | R |  | 7217 | 8294 | 8295 | 7007 | Current Phase 1
9 | A,B,C | R |  | 7218 | 8296 | 8297 | 7008 | Current Phase 1
10 | A,B,C | R |  | 7219 | 8298 | 8299 | 7009 | Current Phase 1
11 | A,B,C | R |  | 7220 | 8300 | 8301 | 7010 | Current Phase 1
12 | A,B,C | R |  | 7221 | 8302 | 8303 | 7011 | Current Phase 1
13 | A,B,C | R |  | 7222 | 8304 | 8305 | 7012 | Current Phase 1
14 | A,B,C | R |  | 7223 | 8306 | 8307 | 7013 | Current Phase 1
1 | A,B,C | R |  | 7224 | 8308 | 8309 | 7000 | Current Phase 2
2 | A,B,C | R |  | 7225 | 8310 | 8311 | 7001 | Current Phase 2
3 | A,B,C | R |  | 7226 | 8312 | 8313 | 7002 | Current Phase 2
4 | A,B,C | R |  | 7227 | 8314 | 8315 | 7003 | Current Phase 2
5 | A,B,C | R |  | 7228 | 8316 | 8317 | 7004 | Current Phase 2
6 | A,B,C | R |  | 7229 | 8318 | 8319 | 7005 | Current Phase 2
7 | A,B,C | R |  | 7230 | 8320 | 8321 | 7006 | Current Phase 2
8 | A,B,C | R |  | 7231 | 8322 | 8323 | 7007 | Current Phase 2
9 | A,B,C | R |  | 7232 | 8324 | 8325 | 7008 | Current Phase 2
10 | A,B,C | R |  | 7233 | 8326 | 8327 | 7009 | Current Phase 2
11 | A,B,C | R |  | 7234 | 8328 | 8329 | 7010 | Current Phase 2
12 | A,B,C | R |  | 7235 | 8330 | 8331 | 7011 | Current Phase 2
13 | A,B,C | R |  | 7236 | 8332 | 8333 | 7012 | Current Phase 2
14 | A,B,C | R |  | 7237 | 8334 | 8335 | 7013 | Current Phase 2
1 | A,B,C | R |  | 7238 | 8336 | 8337 | 7000 | Current Phase 3
2 | A,B,C | R |  | 7239 | 8338 | 8339 | 7001 | Current Phase 3
3 | A,B,C | R |  | 7240 | 8340 | 8341 | 7002 | Current Phase 3
4 | A,B,C | R |  | 7241 | 8342 | 8343 | 7003 | Current Phase 3
5 | A,B,C | R |  | 7242 | 8344 | 8345 | 7004 | Current Phase 3
6 | A,B,C | R |  | 7243 | 8346 | 8347 | 7005 | Current Phase 3
7 | A,B,C | R |  | 7244 | 8348 | 8349 | 7006 | Current Phase 3
8 | A,B,C | R |  | 7245 | 8350 | 8351 | 7007 | Current Phase 3
9 | A,B,C | R |  | 7246 | 8352 | 8353 | 7008 | Current Phase 3
10 | A,B,C | R |  | 7247 | 8354 | 8355 | 7009 | Current Phase 3
11 | A,B,C | R |  | 7248 | 8356 | 8357 | 7010 | Current Phase 3
12 | A,B,C | R |  | 7249 | 8358 | 8359 | 7011 | Current Phase 3
13 | A,B,C | R |  | 7250 | 8360 | 8361 | 7012 | Current Phase 3
14 | A,B,C | R |  | 7251 | 8362 | 8363 | 7013 | Current Phase 3
1 | A | R |  | 7252 | 8364 | 8365 | 7014 | Present KW-Total Demand
2 | A | R |  | 7253 | 8366 | 8367 | 7015 | Present KW-Total Demand
3 | A | R |  | 7254 | 8368 | 8369 | 7016 | Present KW-Total Demand
4 | A | R |  | 7255 | 8370 | 8371 | 7017 | Present KW-Total Demand
5 | A | R |  | 7256 | 8372 | 8373 | 7018 | Present KW-Total Demand
6 | A | R |  | 7257 | 8374 | 8375 | 7019 | Present KW-Total Demand
7 | A | R |  | 7258 | 8376 | 8377 | 7020 | Present KW-Total Demand
8 | A | R |  | 7259 | 8378 | 8379 | 7021 | Present KW-Total Demand
9 | A | R |  | 7260 | 8380 | 8381 | 7022 | Present KW-Total Demand
10 | A | R |  | 7261 | 8382 | 8383 | 7023 | Present KW-Total Demand
11 | A | R |  | 7262 | 8384 | 8385 | 7024 | Present KW-Total Demand
12 | A | R |  | 7263 | 8386 | 8387 | 7025 | Present KW-Total Demand
13 | A | R |  | 7264 | 8388 | 8389 | 7026 | Present KW-Total Demand
14 | A | R |  | 7265 | 8390 | 8391 | 7027 | Present KW-Total Demand
1 | A | R | NV | 7266 | 8392 | 8393 | 7014 | Max KW-Total Demand
2 | A | R | NV | 7267 | 8394 | 8395 | 7015 | Max KW-Total Demand
3 | A | R | NV | 7268 | 8396 | 8397 | 7016 | Max KW-Total Demand
4 | A | R | NV | 7269 | 8398 | 8399 | 7017 | Max KW-Total Demand
5 | A | R | NV | 7270 | 8400 | 8401 | 7018 | Max KW-Total Demand
6 | A | R | NV | 7271 | 8402 | 8403 | 7019 | Max KW-Total Demand
7 | A | R | NV | 7272 | 8404 | 8405 | 7020 | Max KW-Total Demand
8 | A | R | NV | 7273 | 8406 | 8407 | 7021 | Max KW-Total Demand
9 | A | R | NV | 7274 | 8408 | 8409 | 7022 | Max KW-Total Demand
10 | A | R | NV | 7275 | 8410 | 8411 | 7023 | Max KW-Total Demand
11 | A | R | NV | 7276 | 8412 | 8413 | 7024 | Max KW-Total Demand
12 | A | R | NV | 7277 | 8414 | 8415 | 7025 | Max KW-Total Demand
13 | A | R | NV | 7278 | 8416 | 8417 | 7026 | Max KW-Total Demand
14 | A | R | NV | 7279 | 8418 | 8419 | 7027 | Max KW-Total Demand
1 | A,B,C | R |  | 7280 | 8420 | 8421 | 7000 | Present Current Demand Phase 1
2 | A,B,C | R |  | 7281 | 8422 | 8423 | 7001 | Present Current Demand Phase 1
3 | A,B,C | R |  | 7282 | 8424 | 8425 | 7002 | Present Current Demand Phase 1
4 | A,B,C | R |  | 7283 | 8426 | 8427 | 7003 | Present Current Demand Phase 1
5 | A,B,C | R |  | 7284 | 8428 | 8429 | 7004 | Present Current Demand Phase 1
6 | A,B,C | R |  | 7285 | 8430 | 8431 | 7005 | Present Current Demand Phase 1
7 | A,B,C | R |  | 7286 | 8432 | 8433 | 7006 | Present Current Demand Phase 1
8 | A,B,C | R |  | 7287 | 8434 | 8435 | 7007 | Present Current Demand Phase 1
9 | A,B,C | R |  | 7288 | 8436 | 8437 | 7008 | Present Current Demand Phase 1
10 | A,B,C | R |  | 7289 | 8438 | 8439 | 7009 | Present Current Demand Phase 1
11 | A,B,C | R |  | 7290 | 8440 | 8441 | 7010 | Present Current Demand Phase 1
12 | A,B,C | R |  | 7291 | 8442 | 8443 | 7011 | Present Current Demand Phase 1
13 | A,B,C | R |  | 7292 | 8444 | 8445 | 7012 | Present Current Demand Phase 1
14 | A,B,C | R |  | 7293 | 8446 | 8447 | 7013 | Present Current Demand Phase 1
1 | A,B,C | R |  | 7294 | 8448 | 8449 | 7000 | Present Current Demand Phase 2
2 | A,B,C | R |  | 7295 | 8450 | 8451 | 7001 | Present Current Demand Phase 2
3 | A,B,C | R |  | 7296 | 8452 | 8453 | 7002 | Present Current Demand Phase 2
4 | A,B,C | R |  | 7297 | 8454 | 8455 | 7003 | Present Current Demand Phase 2
5 | A,B,C | R |  | 7298 | 8456 | 8457 | 7004 | Present Current Demand Phase 2
6 | A,B,C | R |  | 7299 | 8458 | 8459 | 7005 | Present Current Demand Phase 2
7 | A,B,C | R |  | 7300 | 8460 | 8461 | 7006 | Present Current Demand Phase 2
8 | A,B,C | R |  | 7301 | 8462 | 8463 | 7007 | Present Current Demand Phase 2
9 | A,B,C | R |  | 7302 | 8464 | 8465 | 7008 | Present Current Demand Phase 2
10 | A,B,C | R |  | 7303 | 8466 | 8467 | 7009 | Present Current Demand Phase 2
11 | A,B,C | R |  | 7304 | 8468 | 8469 | 7010 | Present Current Demand Phase 2
12 | A,B,C | R |  | 7305 | 8470 | 8471 | 7011 | Present Current Demand Phase 2
13 | A,B,C | R |  | 7306 | 8472 | 8473 | 7012 | Present Current Demand Phase 2
14 | A,B,C | R |  | 7307 | 8474 | 8475 | 7013 | Present Current Demand Phase 2
1 | A,B,C | R |  | 7308 | 8476 | 8477 | 7000 | Present Current Demand Phase 3
2 | A,B,C | R |  | 7309 | 8478 | 8479 | 7001 | Present Current Demand Phase 3
3 | A,B,C | R |  | 7310 | 8480 | 8481 | 7002 | Present Current Demand Phase 3
4 | A,B,C | R |  | 7311 | 8482 | 8483 | 7003 | Present Current Demand Phase 3
5 | A,B,C | R |  | 7312 | 8484 | 8485 | 7004 | Present Current Demand Phase 3
6 | A,B,C | R |  | 7313 | 8486 | 8487 | 7005 | Present Current Demand Phase 3
7 | A,B,C | R |  | 7314 | 8488 | 8489 | 7006 | Present Current Demand Phase 3
8 | A,B,C | R |  | 7315 | 8490 | 8491 | 7007 | Present Current Demand Phase 3
9 | A,B,C | R |  | 7316 | 8492 | 8493 | 7008 | Present Current Demand Phase 3
10 | A,B,C | R |  | 7317 | 8494 | 8495 | 7009 | Present Current Demand Phase 3
11 | A,B,C | R |  | 7318 | 8496 | 8497 | 7010 | Present Current Demand Phase 3
12 | A,B,C | R |  | 7319 | 8498 | 8499 | 7011 | Present Current Demand Phase 3
13 | A,B,C | R |  | 7320 | 8500 | 8501 | 7012 | Present Current Demand Phase 3
14 | A,B,C | R |  | 7321 | 8502 | 8503 | 7013 | Present Current Demand Phase 3
1 | A,B,C | R | NV | 7322 | 8504 | 8505 | 7000 | Max Current Demand Phase 1
2 | A,B,C | R | NV | 7323 | 8506 | 8507 | 7001 | Max Current Demand Phase 1
3 | A,B,C | R | NV | 7324 | 8508 | 8509 | 7002 | Max Current Demand Phase 1
4 | A,B,C | R | NV | 7325 | 8510 | 8511 | 7003 | Max Current Demand Phase 1
5 | A,B,C | R | NV | 7326 | 8512 | 8513 | 7004 | Max Current Demand Phase 1
6 | A,B,C | R | NV | 7327 | 8514 | 8515 | 7005 | Max Current Demand Phase 1
7 | A,B,C | R | NV | 7328 | 8516 | 8517 | 7006 | Max Current Demand Phase 1
8 | A,B,C | R | NV | 7329 | 8518 | 8519 | 7007 | Max Current Demand Phase 1
9 | A,B,C | R | NV | 7330 | 8520 | 8521 | 7008 | Max Current Demand Phase 1
10 | A,B,C | R | NV | 7331 | 8522 | 8523 | 7009 | Max Current Demand Phase 1
11 | A,B,C | R | NV | 7332 | 8524 | 8525 | 7010 | Max Current Demand Phase 1
12 | A,B,C | R | NV | 7333 | 8526 | 8527 | 7011 | Max Current Demand Phase 1
13 | A,B,C | R | NV | 7334 | 8528 | 8529 | 7012 | Max Current Demand Phase 1
14 | A,B,C | R | NV | 7335 | 8530 | 8531 | 7013 | Max Current Demand Phase 1
1 | A,B,C | R | NV | 7336 | 8532 | 8533 | 7000 | Max Current Demand Phase 2
2 | A,B,C | R | NV | 7337 | 8534 | 8535 | 7001 | Max Current Demand Phase 2
3 | A,B,C | R | NV | 7338 | 8536 | 8537 | 7002 | Max Current Demand Phase 2
4 | A,B,C | R | NV | 7339 | 8538 | 8539 | 7003 | Max Current Demand Phase 2
5 | A,B,C | R | NV | 7340 | 8540 | 8541 | 7004 | Max Current Demand Phase 2
6 | A,B,C | R | NV | 7341 | 8542 | 8543 | 7005 | Max Current Demand Phase 2
7 | A,B,C | R | NV | 7342 | 8544 | 8545 | 7006 | Max Current Demand Phase 2
8 | A,B,C | R | NV | 7343 | 8546 | 8547 | 7007 | Max Current Demand Phase 2
9 | A,B,C | R | NV | 7344 | 8548 | 8549 | 7008 | Max Current Demand Phase 2
10 | A,B,C | R | NV | 7345 | 8550 | 8551 | 7009 | Max Current Demand Phase 2
11 | A,B,C | R | NV | 7346 | 8552 | 8553 | 7010 | Max Current Demand Phase 2
12 | A,B,C | R | NV | 7347 | 8554 | 8555 | 7011 | Max Current Demand Phase 2
13 | A,B,C | R | NV | 7348 | 8556 | 8557 | 7012 | Max Current Demand Phase 2
14 | A,B,C | R | NV | 7349 | 8558 | 8559 | 7013 | Max Current Demand Phase 2
1 | A,B,C | R | NV | 7350 | 8560 | 8561 | 7000 | Max Current Demand Phase 3
2 | A,B,C | R | NV | 7351 | 8562 | 8563 | 7001 | Max Current Demand Phase 3
3 | A,B,C | R | NV | 7352 | 8564 | 8565 | 7002 | Max Current Demand Phase 3
4 | A,B,C | R | NV | 7353 | 8566 | 8567 | 7003 | Max Current Demand Phase 3
5 | A,B,C | R | NV | 7354 | 8568 | 8569 | 7004 | Max Current Demand Phase 3
6 | A,B,C | R | NV | 7355 | 8570 | 8571 | 7005 | Max Current Demand Phase 3
7 | A,B,C | R | NV | 7356 | 8572 | 8573 | 7006 | Max Current Demand Phase 3
8 | A,B,C | R | NV | 7357 | 8574 | 8575 | 7007 | Max Current Demand Phase 3
9 | A,B,C | R | NV | 7358 | 8576 | 8577 | 7008 | Max Current Demand Phase 3
10 | A,B,C | R | NV | 7359 | 8578 | 8579 | 7009 | Max Current Demand Phase 3
11 | A,B,C | R | NV | 7360 | 8580 | 8581 | 7010 | Max Current Demand Phase 3
12 | A,B,C | R | NV | 7361 | 8582 | 8583 | 7011 | Max Current Demand Phase 3
13 | A,B,C | R | NV | 7362 | 8584 | 8585 | 7012 | Max Current Demand Phase 3
14 | A,B,C | R | NV | 7363 | 8586 | 8587 | 7013 | Max Current Demand Phase 3
1 | A,B,C | R | NV | 7364 | 8588 | 8589 | 7000 | Max Current Phase 1
2 | A,B,C | R | NV | 7365 | 8590 | 8591 | 7001 | Max Current Phase 1
3 | A,B,C | R | NV | 7366 | 8592 | 8593 | 7002 | Max Current Phase 1
4 | A,B,C | R | NV | 7367 | 8594 | 8595 | 7003 | Max Current Phase 1
5 | A,B,C | R | NV | 7368 | 8596 | 8597 | 7004 | Max Current Phase 1
6 | A,B,C | R | NV | 7369 | 8598 | 8599 | 7005 | Max Current Phase 1
7 | A,B,C | R | NV | 7370 | 8600 | 8601 | 7006 | Max Current Phase 1
8 | A,B,C | R | NV | 7371 | 8602 | 8603 | 7007 | Max Current Phase 1
9 | A,B,C | R | NV | 7372 | 8604 | 8605 | 7008 | Max Current Phase 1
10 | A,B,C | R | NV | 7373 | 8606 | 8607 | 7009 | Max Current Phase 1
11 | A,B,C | R | NV | 7374 | 8608 | 8609 | 7010 | Max Current Phase 1
12 | A,B,C | R | NV | 7375 | 8610 | 8611 | 7011 | Max Current Phase 1
13 | A,B,C | R | NV | 7376 | 8612 | 8613 | 7012 | Max Current Phase 1
14 | A,B,C | R | NV | 7377 | 8614 | 8615 | 7013 | Max Current Phase 1
1 | A,B,C | R | NV | 7378 | 8616 | 8617 | 7000 | Max Current Phase 2
2 | A,B,C | R | NV | 7379 | 8618 | 8619 | 7001 | Max Current Phase 2
3 | A,B,C | R | NV | 7380 | 8620 | 8621 | 7002 | Max Current Phase 2
4 | A,B,C | R | NV | 7381 | 8622 | 8623 | 7003 | Max Current Phase 2
5 | A,B,C | R | NV | 7382 | 8624 | 8625 | 7004 | Max Current Phase 2
6 | A,B,C | R | NV | 7383 | 8626 | 8627 | 7005 | Max Current Phase 2
7 | A,B,C | R | NV | 7384 | 8628 | 8629 | 7006 | Max Current Phase 2
8 | A,B,C | R | NV | 7385 | 8630 | 8631 | 7007 | Max Current Phase 2
9 | A,B,C | R | NV | 7386 | 8632 | 8633 | 7008 | Max Current Phase 2
10 | A,B,C | R | NV | 7387 | 8634 | 8635 | 7009 | Max Current Phase 2
11 | A,B,C | R | NV | 7388 | 8636 | 8637 | 7010 | Max Current Phase 2
12 | A,B,C | R | NV | 7389 | 8638 | 8639 | 7011 | Max Current Phase 2
13 | A,B,C | R | NV | 7390 | 8640 | 8641 | 7012 | Max Current Phase 2
14 | A,B,C | R | NV | 7391 | 8642 | 8643 | 7013 | Max Current Phase 2
1 | A,B,C | R | NV | 7392 | 8644 | 8645 | 7000 | Max Current Phase 3
2 | A,B,C | R | NV | 7393 | 8646 | 8647 | 7001 | Max Current Phase 3
3 | A,B,C | R | NV | 7394 | 8648 | 8649 | 7002 | Max Current Phase 3
4 | A,B,C | R | NV | 7395 | 8650 | 8651 | 7003 | Max Current Phase 3
5 | A,B,C | R | NV | 7396 | 8652 | 8653 | 7004 | Max Current Phase 3
6 | A,B,C | R | NV | 7397 | 8654 | 8655 | 7005 | Max Current Phase 3
7 | A,B,C | R | NV | 7398 | 8656 | 8657 | 7006 | Max Current Phase 3
8 | A,B,C | R | NV | 7399 | 8658 | 8659 | 7007 | Max Current Phase 3
9 | A,B,C | R | NV | 7400 | 8660 | 8661 | 7008 | Max Current Phase 3
10 | A,B,C | R | NV | 7401 | 8662 | 8663 | 7009 | Max Current Phase 3
11 | A,B,C | R | NV | 7402 | 8664 | 8665 | 7010 | Max Current Phase 3
12 | A,B,C | R | NV | 7403 | 8666 | 8667 | 7011 | Max Current Phase 3
13 | A,B,C | R | NV | 7404 | 8668 | 8669 | 7012 | Max Current Phase 3
14 | A,B,C | R | NV | 7405 | 8670 | 8671 | 7013 | Max Current Phase 3
1 | A | R | NV | 7406 | 8672 | 8673 | 7014 | Max KW Total
2 | A | R | NV | 7407 | 8674 | 8675 | 7015 | Max KW Total
3 | A | R | NV | 7408 | 8676 | 8677 | 7016 | Max KW Total
4 | A | R | NV | 7409 | 8678 | 8679 | 7017 | Max KW Total
5 | A | R | NV | 7410 | 8680 | 8681 | 7018 | Max KW Total
6 | A | R | NV | 7411 | 8682 | 8683 | 7019 | Max KW Total
7 | A | R | NV | 7412 | 8684 | 8685 | 7020 | Max KW Total
8 | A | R | NV | 7413 | 8686 | 8687 | 7021 | Max KW Total
9 | A | R | NV | 7414 | 8688 | 8689 | 7022 | Max KW Total
10 | A | R | NV | 7415 | 8690 | 8691 | 7023 | Max KW Total
11 | A | R | NV | 7416 | 8692 | 8693 | 7024 | Max KW Total
12 | A | R | NV | 7417 | 8694 | 8695 | 7025 | Max KW Total
13 | A | R | NV | 7418 | 8696 | 8697 | 7026 | Max KW Total
14 | A | R | NV | 7419 | 8698 | 8699 | 7027 | Max KW Total
1 | A | R |  | 7420 | 8700 | 8701 | 7014 | KVA Total
2 | A | R |  | 7421 | 8702 | 8703 | 7015 | KVA Total
3 | A | R |  | 7422 | 8704 | 8705 | 7016 | KVA Total
4 | A | R |  | 7423 | 8706 | 8707 | 7017 | KVA Total
5 | A | R |  | 7424 | 8708 | 8709 | 7018 | KVA Total
6 | A | R |  | 7425 | 8710 | 8711 | 7019 | KVA Total
7 | A | R |  | 7426 | 8712 | 8713 | 7020 | KVA Total
8 | A | R |  | 7427 | 8714 | 8715 | 7021 | KVA Total
9 | A | R |  | 7428 | 8716 | 8717 | 7022 | KVA Total
10 | A | R |  | 7429 | 8718 | 8719 | 7023 | KVA Total
11 | A | R |  | 7430 | 8720 | 8721 | 7024 | KVA Total
12 | A | R |  | 7431 | 8722 | 8723 | 7025 | KVA Total
13 | A | R |  | 7432 | 8724 | 8725 | 7026 | KVA Total
14 | A | R |  | 7433 | 8726 | 8727 | 7027 | KVA Total
1 | A | R |  | 7434 | 8728 | 8729 | 7014 | KVA Phase 1
2 | A | R |  | 7435 | 8730 | 8731 | 7015 | KVA Phase 1
3 | A | R |  | 7436 | 8732 | 8733 | 7016 | KVA Phase 1
4 | A | R |  | 7437 | 8734 | 8735 | 7017 | KVA Phase 1
5 | A | R |  | 7438 | 8736 | 8737 | 7018 | KVA Phase 1
6 | A | R |  | 7439 | 8738 | 8739 | 7019 | KVA Phase 1
7 | A | R |  | 7440 | 8740 | 8741 | 7020 | KVA Phase 1
8 | A | R |  | 7441 | 8742 | 8743 | 7021 | KVA Phase 1
9 | A | R |  | 7442 | 8744 | 8745 | 7022 | KVA Phase 1
10 | A | R |  | 7443 | 8746 | 8747 | 7023 | KVA Phase 1
11 | A | R |  | 7444 | 8748 | 8749 | 7024 | KVA Phase 1
12 | A | R |  | 7445 | 8750 | 8751 | 7025 | KVA Phase 1
13 | A | R |  | 7446 | 8752 | 8753 | 7026 | KVA Phase 1
14 | A | R |  | 7447 | 8754 | 8755 | 7027 | KVA Phase 1
1 | A | R |  | 7448 | 8756 | 8757 | 7014 | KVA Phase 2
2 | A | R |  | 7449 | 8758 | 8759 | 7015 | KVA Phase 2
3 | A | R |  | 7450 | 8760 | 8761 | 7016 | KVA Phase 2
4 | A | R |  | 7451 | 8762 | 8763 | 7017 | KVA Phase 2
5 | A | R |  | 7452 | 8764 | 8765 | 7018 | KVA Phase 2
6 | A | R |  | 7453 | 8766 | 8767 | 7019 | KVA Phase 2
7 | A | R |  | 7454 | 8768 | 8769 | 7020 | KVA Phase 2
8 | A | R |  | 7455 | 8770 | 8771 | 7021 | KVA Phase 2
9 | A | R |  | 7456 | 8772 | 8773 | 7022 | KVA Phase 2
10 | A | R |  | 7457 | 8774 | 8775 | 7023 | KVA Phase 2
11 | A | R |  | 7458 | 8776 | 8777 | 7024 | KVA Phase 2
12 | A | R |  | 7459 | 8778 | 8779 | 7025 | KVA Phase 2
13 | A | R |  | 7460 | 8780 | 8781 | 7026 | KVA Phase 2
14 | A | R |  | 7461 | 8782 | 8783 | 7027 | KVA Phase 2
1 | A | R |  | 7462 | 8784 | 8785 | 7014 | KVA Phase 3
2 | A | R |  | 7463 | 8786 | 8787 | 7015 | KVA Phase 3
3 | A | R |  | 7464 | 8788 | 8789 | 7016 | KVA Phase 3
4 | A | R |  | 7465 | 8790 | 8791 | 7017 | KVA Phase 3
5 | A | R |  | 7466 | 8792 | 8793 | 7018 | KVA Phase 3
6 | A | R |  | 7467 | 8794 | 8795 | 7019 | KVA Phase 3
7 | A | R |  | 7468 | 8796 | 8797 | 7020 | KVA Phase 3
8 | A | R |  | 7469 | 8798 | 8799 | 7021 | KVA Phase 3
9 | A | R |  | 7470 | 8800 | 8801 | 7022 | KVA Phase 3
10 | A | R |  | 7471 | 8802 | 8803 | 7023 | KVA Phase 3
11 | A | R |  | 7472 | 8804 | 8805 | 7024 | KVA Phase 3
12 | A | R |  | 7473 | 8806 | 8807 | 7025 | KVA Phase 3
13 | A | R |  | 7474 | 8808 | 8809 | 7026 | KVA Phase 3
14 | A | R |  | 7475 | 8810 | 8811 | 7027 | KVA Phase 3
total registers in this section
1288