## PSO Platform
Power SCADA Operation Device Driver Support Matrix
Notes PSO supports a range of protocol drivers capable of communicating with a variety of devices supporting those protocols. Power SCADA inherits a stack of drivers for communicating with a variety of process control and other instrumentation. Citect drivers can be downloaded on the Citect Driver Web (https://softwaresupportsp.aveva.com/#/connectivityhub). Most drivers are licensed via Citect SCADA and are provided at no additional cost. However there are some exceptions where the driver requires an additional purchase cost to license it. Any drivers that require a purchase cost are only commercially available for Citect SCADA and are NOT commercially allowed for use with Power SCADA Operation. Non-Native/3rd Party devices are supported through open protocol drivers. Device types and profiles can be engineered based on device documentation using the Profile Editor. PwrModbus, IEC61850, IEC 60870-0-104, BACnet and DNP3 are open protocol drivers. Other protocol drivers available from Citect at the link above. Many power modbus protocol devices can be supported using IEC61850 when the device is installed on a PowerLogic G3200 gateway.
Legend:
ü - Supported  - Supported by device but not in PowerSCADA N/A - Not supported functionality in the device
Device drivers which are not native can be downloaded from any of the following locations: - https://community.exchange.se.com/t5/EcoStruxure-Power-SCADA/PowerLogic-Driver-Pack-Latest-Release-for-PowerSCADA-7-40-or/m-p/150186
<<-- Expand for Notes and legend
Device Type | Protocols | Native Device Type | Default Device Profile(s) | Real-time Data | Onboard Alarms (Logs and Time Stamps) | Historical Logs | Waveforms | Breaker Control | PSE 7.40 | PSE 8.0 | PSE 8.1 | PSE 8.2 | PSO 9.0 | PSO 2020 | Additional Info
Acti 9 Smartlink | Modbus | ü | Acti 9 Smartlink Ethernet Full Acti 9 Smartlink RS485 Full | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native
ASCO 7000/4000 ATS | Modbus | ü | ASCO 7000_4000 full | ü | ü | N/A | N/A | ü |  |  |  |  | Installer | Native
BCPM | Modbus (JBUS) | ü | BCPM Full | ü |  | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
CM2000 | Modbus | ü | Circuit Monitor 2000 Standard | ü | ü |  | ü | N/A | Native | Native | Native | Native | Native | Native
| IEC61850* |  | N/A |  |  |  |  | N/A | [6 empty] | *Only available through G3200 Gateway
CM3000 | Modbus | ü | Circuit Monitor 3000 Standard | ü | ü |  | ü | N/A | Native | Native | Native | Native | Native | Native
| IEC61850* |  | N/A |  |  |  |  | N/A | [6 empty] | *Only available through G3200 Gateway
CM4000 | Modbus | ü | Circuit Monitor 4000 Standard, Circuit Monitor 4000 Full | ü | ü |  | ü | N/A | Native | Native | Native | Native | Native | Native
| IEC61850* |  | N/A | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | *Only available through G3200 Gateway
Cyber Sciences SER2408 & SER3200 | Modbus | ü | N/A | ü | ü | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
EM4800 | Modbus | ü | Branch Circuit Monitor Full | ü |  | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
Enercept | Modbus | ü | Enercept Full | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
Galaxy V Series | Modbus | ü | Galaxy V Series Standard | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native
iEM3000 | Modbus | ü | IEM 3000 Standard | ü |  | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
ION6200 | Modbus |  | N/A | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
| ION | ü* | N/A | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no ION6200 device type
ION73xx | Modbus |  | N/A | ü |  |  |  | N/A | Native | Native | Native | Native | Native | Native
| ION | ü* | N/A | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no ION73xx device type
| DNP3 |  | N/A | ü | ü |  |  | N/A | Native | Native | Native | Native | Native | Native
ION7400 | ION | ü* | N/A | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no ION7400 modbus device type
ION8650, ION7650, ION7550 | Modbus | ION7650 only | N/A | ü |  |  |  | N/A | Native | Native | Native | Native | Native | Native | ION devices are supported via the ION Protocol Driver. Device types/profiles do not exist for all ION devices.
| ION | ü* | ION 7650 Standard | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, ION7650 device type used for Modbus, DNP3 protocols
| DNP3 | ION7650 only | N/A | ü | ü |  |  | N/A | Native | Native | Native | Native | Native | Native
| IEC61850 | N/A | N/A | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Waveforms through FTP protocol
ION8600 | Modbus |  | N/A | ü |  |  |  | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no PM8000 modbus device type
| ION | ü | N/A | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no PM8000 modbus device type
| DNP3 |  | N/A | ü | ü |  |  | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no PM8000 modbus device type
ION9000 | ION | ü | ION 9000 Standard | ü | ü | ü | ü | N/A | Installer | Installer | Installer | Installer | Native | Native | Generic ION device type, no ION8000 modbus device type
LVSMC (device is the counterpart to the Compact NSX for China) | Modbus | ü | LVSMC Standard | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native
Micrologic 5.2/6.2/5.3/6.3 A (Micrologic A Compact NSX) | Modbus | ü | Micrologic NSX Type A | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 5.2/6.2/5.3/6.3/7.2/7.3 E (Micrologic E Compact NSX) | Modbus | ü | Micrologic NSX Type E | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 2.0/5.0/6.0/7.0 A (Micrologic A) | Modbus | ü | Micrologic Type A Full, Micrologic Type A Standard, Micrologic Type A Full FW v2, Micrologic Type A Standard FW v2 | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 2.0/5.0/6.0 E (Micrologic E) | Modbus | ü | Micrologic Type E Full, Micrologic Type E Standard | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 5.0/6.0/7.0 P (Micrologic P) | Modbus | ü | Micrologic Type P Full, Micrologic Type P Standard, Micrologic Type P Full FW v2, Micrologic Type P Standard FW v2 | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 5.0/6.0/7.0 H (Micrologic H) | Modbus | ü | Micrologic Type H Full, Micrologic Type H Standard, Micrologic Type H Full FW v2, Micrologic Type H Standard FW v2 | ü | ü | N/A | ü | ü | Installer | Installer | Installer | Native | Native | Native
Micrologic 2.0/5.0/6.0/7.0 A IFE_IFM (Micrologic A IFE_IFM) | Modbus | ü | Micrologic Type A IFE IFM Full | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native | Updated Micrologic Driver to support IFE/IFM comms architecture
Micrologic 2.0/5.0/6.0 E IFE_IFM (Micrologic E IFE_IFM) | Modbus | ü | Micrologic Type E IFE IFM Full | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native | Updated Micrologic Driver to support IFE/IFM comms architecture
Micrologic 5.0/6.0/7.0 P IFE_IFM (Micrologic P IFE_IFM) | Modbus | ü | Micrologic Type P IFE IFM Full | ü | ü | N/A | N/A | ü | Installer | Installer | Installer | Native | Native | Native | Updated Micrologic Driver to support IFE/IFM comms architecture
Micrologic 5.0/6.0/7.0 H IFE_IFM (Micrologic H IFE_IFM) | Modbus | ü | Micrologic Type H IFE IFM Full | ü | ü | N/A | ü | ü | Installer | Installer | Installer | Native | Native | Native | Updated Micrologic Driver to support IFE/IFM comms architecture
Micrologic 2.0/3.0/5.0/6.0/7.0 X (Masterpact MTZ) | Modbus | ü | Micrologic MTZ Micrologic MTZ FW V2 Micrologic MTZ FW V3 | ü | ü | N/A | ü | ü |  |  | Installer | Native | Native | Native | Updated Micrologic X driver to support latest Micrologic Control Unit (V003.010.004)
PM1200 | Modbus | ü | PM1200_LE_Full | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native | See driver help for needed StatusRegister ini parameter to ensure comms
PM2000 series | Modbus | ü | PM2X05 PM2X20 PM2X25 PM2X30 | ü | ü | N/A | N/A | N/A |  |  |  |  |  | Native | PM2000 Series driver can be connected to Power SCADA Operation using the Modbus RTU via Gateway protocol.
PM51xx | Modbus | ü | N/A | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native | Important for time sync - set parameter
PM53xx | Modbus | ü | PM5350 Standard, PM5350 iBusway Standard | ü | ü* |  | N/A | N/A | Native | Native | Native | Native | Native | Native | *Limited only by supported device functionality (logs - kWh, kVaH)
PM55xx | Modbus | ü | N/A | ü | ü |  | N/A | N/A | Native | Native | Native | Native | Native | Native
PM650 | Modbus | ü | Power Meter 650 Standard | ü | ü | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
PM700 series | Modbus | ü | Power Meter 700 Standard | ü | ü |  | N/A | N/A | Native | Native | Native | Native | Native | Native
PM800 series | Modbus | ü | PM810 Full, PM820 Full, PM850 Full, PM870 Full, Power Meter 800 Standard | ü | ü |  | ü* | N/A | Installer | Installer | Installer | Native | Native | Native | Late-arriving alarms fix in versions 8.1 and prior issued as update in installer
PM8000 | ION | ü* | Power Meter 8000 Standard | ü | ü | ü | ü | N/A | Native | Native | Native | Native | Native | Native | Generic ION device type, no PM8000 modbus device type
PM9C | Modbus | ü | PM9C Full | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
PowerTag | Modbus | ü | PowerTag Standard | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native
PowerTag NSX | Modbus | ü | PowerTag NSX Standard | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native
ProTime SER (Monaghan Engineering) | Modbus | ü | N/A | ü | ü | N/A | N/A | N/A |  | Native | Native | Native | Native | Native
SEPAM series 20, 40, 80, 2000 | Modbus | ü | Sepam S20 Standard, Sepam S20 Full, Sepam S40 Standard, Sepam S42 Full, Sepam S80 Standard, Sepam S2000 Full | ü | ü | N/A | ü |  | Native | Native | Native | Native | Native | Native
| DNP3 | ü |  | ü | ü | N/A | ü |  | Native | Native | Native | Native | Native | Native
| IEC61850* | N/A |  | ü | ü | N/A | ü |  | Native | Native | Native | Native | Native | Native | Requires ACE850 module for IEC61850
| IEC104* | N/A |  | ü | ü | N/A |  |  | Native | Native | Native | Native | Native | Native | Through G3200 gateway
Switchgear Monitoring Device | Modbus | ü | Switchgear Monitoring Device | ü | N/A | N/A | N/A | N/A |  |  |  |  | Native | Native | Used with Thermal Monitoring solution
Trendpoint Enersure | Modbus (JBUS) | ü | Trendpoint Enersure Standard | ü |  |  |  | N/A | Native | Native | Native | Native | Native | Native
Tesys T | Modbus (JBUS) | ü | TeSys T Full | ü | N/A | N/A | N/A | N/A | Native | Native | Native | Native | Native | Native
Vigilohm IFL12 Series | Modbus | ü | Vigilohm IFL12 C Vigilohm IFL12 H Vigilohm IFL12 LMCT | ü | ü |  | N/A | N/A |  |  |  |  | Installer | Native | Supported models: IMDIFL12C, IMDIFL12H, IMDIFL12MC, IMDIFL12LMC, IMDIFL12MCT, IMDIFL12LMCT
coming soon

## 3rd party device support
3rd party devices can be supported via a variety of protocols using productivity tools not available in the core Citect platform
Protocol | Real time data | Onboard data logs | Onboard alarm logs | Alarm time stamp quality | COMTRADE waveforms | Tools used during commissioning
Modbus TCP/IP | yes | no | no | no | * via FTP | Profile Editor
IEC-61850 Ed.1 | yes | * yes | * yes | no | * yes | Profile Editor
IEC 60870-5-104 | yes | no | * yes | no | * via FTP | Profile Editor
DNP3 | yes | no | * yes | no | * via FTP | Profile Editor
SNMP v.2 | yes | no | no | n/a | n/a | PowerSCADA Studio
BACNet | yes | no | no | n/a | n/a | PowerSCADA Studio
* if supported in device