DATE: February 12th 2019

# TO: Users of Schneider Electric, Modicon X80 I/O

Quality Problem Notification

weighing transmitter module – PMESWT0100

#### DELIVER TO PERSON IN CHARGE OF QUALITY / MAINTENANCE IN YOUR ORGANIZATION

SUBJECT: PRB-219878 - IDPAC - PMESWT0100 transmitted weighing value is fixed

Dear valued customer,

We have discovered that the PMESWT0100 weighing partner transmitter module has a firmware bug which may cause the freeze of the weighing value transmitted from the module to the CPU after several weeks of operation.

As a consequence, the value transmitted, displayed in UnityPro screen (HMI values which are connected to the SCAIME HMI port are not affected), does not change based on the actual weight and remains fixed in its last good value.

In case the module is unplugged and plugged again, the function will work again until the next possible event.

Probability of this event is random and issue happened on very specific contexts. Criticality largely depends on how the site application is developed and if other means to detect any potential issues on the weighting function are present, such as continuous monitoring of an analog value by application.

Product References Impacted:

PMESWT0100 PV 01 – from commercialization to Date of Manufacturing (DOM) 1905 (year 2019, week 05).

Improvements correcting this firmware bug are natively installed in the Product version 02 or greater.

PV 02 are manufactured since DOM (Date of Manufacturing) 1906 – week 06 of year 2019.

Product version is reported in the side label of the product.

Proposed Remedial Actions

Schneider Electric is requesting that any product, within the impacted date codes, is upgraded to the last Firmware version available (minimum software version required is 1.15).

Activity can be scheduled based on process characteristics (ex: next maintenance phase) and potential impact of the “freeze”.

The package (Firmware + Upgrade procedure + Release note + Hotfixes) is available on SE.com website and Scaime website. New firmware version 1.15 or greater must be used only with:

- EcoStruxure™ Control Expert SV14 or greater version,

or

- Unity Pro SV13.1 with the following Hotfixes installed: “UnityPro_V131_HF0470178R” (DFB output pins) and “UnityPro_V131_HF0465853R” (SCAIME DTM).

If additional information is required, please contact your local Schneider Electric Office.

We apologize for any inconvenience caused by this Notice.

Schneider Electric considers product safety and reliability as its first priority.

Yours faithfully,

Country Quality Department

<=S= local service addresses and phone numbers to contact for more information>