## DataLog
Only edit the cells in the "WHITE" Area
Data Log Memory Calculation
Logging Interval (Minutes) |  |  |  | 1
Item | Register Description | Register Number | Data Type | # of Bytes
1 | Active Energy Delivered (Into Load) | 3204 | INT64 | 8
2 | Active Energy Received (Out of Load) | 3208 | INT64 | 8
3 | Reactive Energy Delivered | 3220 | INT64 | 8
4 | Reactive Energy Received | 3224 | INT64 | 8
5 | Apparent Energy Delivered | 3236 | INT64 | 8
6 | Apparent Energy Received | 3240 | INT64 | 8
7 | Input Metering Accumulation Channel 01 | 3570 | INT64 | 8
8 | Input Metering Accumulation Channel 02 | 3574 | INT64 | 8
9 | Input Metering Accumulation Channel 03 | 3578 | INT64 | 8
10 | Input Metering Accumulation Channel 04 | 3582 | INT64 | 8
11 | Base Unit - Digital Input DI1 - Count | 8915 | INT32U | 4
12 | Base Unit - Digital Input DI2 - Count | 8919 | INT32U | 4
13 | Base Unit - Digital Input DI3 - Count | 8923 | INT32U | 4
14 | Base Unit - Digital Input DI4 - Count | 8927 | INT32U | 4
Total # of Bytes per Record |  |  |  | 96
|  | Record Content | Data Type | Bytes
|  | Date Time Stamp | DATETIME | 8
|  | Status | INT32U | 4
|  | Total # of Bytes per Record | Bytes | 96
|  | Single Record Size in Bytes |  | 108
|  | Max Number of Logs |  | 15810
|  | Max Number of Days in the Log |  | 10.9792
|  | Max Number of Months in the Log |  | 0.36597

## Misc
1 | Max Number of Records | Record | 35040 | Active Energy Delivered (Into Load) | 3204 | R_ENG_ACC_KWH_DEL | INT64 | 8
5 | Total Logging Memory Available | Bytes | 1707480 | Active Energy Received (Out of Load) | 3208 | R_ENG_ACC_KWH_REC | INT64 | 8
10 |  |  |  | Reactive Energy Delivered | 3220 | R_ENG_ACC_KVARH_DEL | INT64 | 8
15 |  |  |  | Reactive Energy Received | 3224 | R_ENG_ACC_KVARH_REC | INT64 | 8
30 |  |  |  | Apparent Energy Delivered | 3236 | R_ENG_ACC_KVAH_DEL | INT64 | 8
60 |  |  |  | Apparent Energy Received | 3240 | R_ENG_ACC_KVAH_REC | INT64 | 8
1440 |  |  |  | Input Metering Accumulation Channel 01 | 3570 | R_INPUT_METER_ACCUM_01 | INT64 | 8
|  |  |  | Input Metering Accumulation Channel 02 | 3574 | R_INPUT_METER_ACCUM_02 | INT64 | 8
|  |  |  | Input Metering Accumulation Channel 03 | 3578 | R_INPUT_METER_ACCUM_03 | INT64 | 8
|  |  |  | Input Metering Accumulation Channel 04 | 3582 | R_INPUT_METER_ACCUM_04 | INT64 | 8
|  |  |  | Base Unit - Digital Input DI1 - Count | 8915 | R_DIGIN_COUNT_S01 | INT32U | 4
|  |  |  | Base Unit - Digital Input DI2 - Count | 8919 | R_DIGIN_COUNT_S02 | INT32U | 4
|  |  |  | Base Unit - Digital Input DI3 - Count | 8923 | R_DIGIN_COUNT_S03 | INT32U | 4
|  |  |  | Base Unit - Digital Input DI4 - Count | 8927 | R_DIGIN_COUNT_S04 | INT32U | 4
|  |  |  | Current A | 3000 | R_IA_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Current B | 3002 | R_IB_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Current C | 3004 | R_IC_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Current N | 3006 | R_IN_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Current G | 3008 | R_IG_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Current Avg | 3010 | R_IAVG_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage A-B | 3020 | R_VAB_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage B-C | 3022 | R_VBC_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage C-A | 3024 | R_VCA_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage L-L Avg | 3026 | R_VLL_50_60_CYC_RMS_AVG | FLOAT32 | 4
|  |  |  | Voltage A-N | 3028 | R_VAN_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage B-N | 3030 | R_VBN_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Voltage C-N | 3032 | R_VCN_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Active Power A | 3054 | R_PA_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Active Power B | 3056 | R_PB_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Active Power C | 3058 | R_PC_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Active Power Total | 3060 | R_PTOT_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Reactive Power A | 3062 | R_QA_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Reactive Power B | 3064 | R_QB_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Reactive Power C | 3066 | R_QC_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Reactive Power Total | 3068 | R_QTOT_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Apparent Power A | 3070 | R_SA_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Apparent Power B | 3072 | R_SB_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Apparent Power C | 3074 | R_SC_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Apparent Power Total | 3076 | R_STOT_50_60_CYC_RMS | FLOAT32 | 4
|  |  |  | Power Factor A | 3078 | R_PFA_50_60_CYC_TRUE | 4Q_FP_PF | 4
|  |  |  | Power Factor B | 3080 | R_PFB_50_60_CYC_TRUE | 4Q_FP_PF | 4
|  |  |  | Power Factor C | 3082 | R_PFC_50_60_CYC_TRUE | 4Q_FP_PF | 4
|  |  |  | Power Factor Total | 3084 | R_PFTOT_50_60_CYC_TRUE | 4Q_FP_PF | 4