## Intro
EOCR-iSEM2
Software system specification
Register map
The register map (or "mapping") gives the list of the registers existing in EOCR-iSEM2 systems.
All the data accessible through an external serial port are listed in this document.
All the objects have only one Modbus address indepent of the communication port.
The register map file is also the main source of information to create user's manuals of registers of products.
Sheet descriptions
"Revision" sheet shows history of this document
"Permission" sheet describes every permission of registers
"Config" sheet descripbes register which is used for configuration
"Map" sheet descripbes full definition of the every registers
Rev. No. | Rev. Date | Rev. Item | Doc. Number
1.4.0 | 2025-02-10 | 00 | RD24-03-005
Copyright of Schneider Electric Korea Ltd. & All Rights Reserved 6F Daebang Building, 248 Gonghang-daero, Gangseo-gu, Seoul, Korea (07805) Homepage : http://www.se.com

## Permission
Permission
Permission | Description
Read Only | Only reading is allowed, writing is not allowed.
R/W | Any reading or writing is allowed.
R/Wman | Any reading is allowed, but writing is allowed only in the manufacturing mode.
R/Wnet | Any reading is allowed. And, any writing is allowed through the PDM port. (But, Network access (Reg484.0 is 1) must be activated through ETH or NET port)
R/Woff_net | Any reading is allowed. And, any writing is allowed through the PDM port when Motor is stopped. (But, Network access (Reg484.0 is 1) must be activated through the ETH port or NET port)
Reserved | Reserved area which is for internal use only
R/Wsys | Any reading is allowed. And, any writing is allowed through the PDM port when Motor is stopped and SysConfig mode is enabled(Reg601.0 is 1). (But, Network access (Reg484.0 is 1) must be activated through the ETH port or NET port)
R/Whmi | Any reading is allowed, but writing is only allowed through PDM port.
R/Windirect | Any reading is allowed, but writing is allowed as indirect register's permission.
Attribute of Default value
Attribute | Description
RFS All | Cleared with Reg705.0
Statistics | Cleared with Reg705.1
Thermal | Cleared with Reg705.2
Settings | Cleared with Reg705.3
Network | Cleared with Reg705.4
None | Not cleared with Reg705
Sub-Map of F/W
Sub-Map
METER_MAP | Metering
PRO_MAP | Protections
MAN_MAP | Manufacturing
MOTOR_MAP | Motor, Motor Cycle
HMI_MAP | HMI Display, Sensor Data
DIO_MAP | Digital Processing, Digital IO, Waveform
IND_ADD_MAP | Remap Address
IND_VAL_MAP | Remapped Data
FAULT_MAP | Fault History
COM_MAP | Serial Communication
ETH_MAP | Ethernet Communication

## Config
Register | Name | Bit | Name | Bit Description | Default | Comment
540 | Logic Operating Mode | 0 | AUTO Wire type | 0: 2Wire, 1: 3Wire | 0 | Reg540.0: It is only allowed on PREMIUM Reference. It is not allowed if LOP(Reg683.8) is enabled. Reg540.1-3: It is only allowed on PREMIUM Reference.
|  | 1 | Logic Operation mode | 0: DOL, 1: Inverter, 2: ByPass, 3: Wye-delta | 0
2
3
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Reserved |  | 0
|  | 7 | Reserved |  | 0
|  | 8 | Reserved |  | 0
|  | 9 | Reserved |  | 0
|  | 10 | Reserved |  | 0
|  | 11 | Reserved |  | 0
|  | 12 | Reserved |  | 0
|  | 13 | Reserved |  | 0
|  | 14 | Reserved |  | 0
|  | 15 | Reserved |  | 0
601 | Global Configuration Register | 0 | Sys Configuration mode | 0: Normal mode, 1: System configuration mode | 0 | Reg601.7: If external CT has configured, built-in ZCT will not be allowed.
|  | 1 | Reserved |  | 0
|  | 2 | Reserved |  | 0
|  | 3 | Fail safe mode enabled for 97-98, 95-96 relay | 0: disable, 1: enabled | 0
|  | 4 | Fail safe mode enabled for 57-58 relay | 0: disable, 1: enabled | 0
|  | 5 | Low frequency | 0: 20-400Hz(Normal) 1: 5-400Hz(Low frequency) | 0
|  | 6 | Reserved |  | 0
|  | 7 | ZCT Selection | 0: External, 1: Built-in | 1
|  | 8 | Reserved |  | 0
|  | 9 | Voltage option | 0: Voltage not available, 1: Voltage available | 1
|  | 10 | Reserved |  | 0
|  | 11 | System Frequency | 0: 60Hz, 1: 50Hz | 0
|  | 12 | Star-Delta | 0: Off, 1: Star-Delta | 0
|  | 13 | 1 Phase Motor | 0: 3 phase motor, 1: Single phase | 0
|  | 14 | DC output type | 0: Loop current, 1: Metering pulse | 0
|  | 15 | Reserved |  | 0
602 | Global Configuration Register 2 | 0 | Fault Reset Mode | 0: Manual reset, 1: Remote Network, 2: Auto reset | 1 | Reg602.12-14: It is only allowed on PREMIUM Reference. Reg602.13-14 are automatically deactivated by default whenever the logic function (Reg6012.0) is enabled.
1
2
|  | 3 | Reserved |  | 0
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Reserved |  | 0
|  | 7 | Overload config | 0: Off, 1: Definite | 1
|  | 8 |  | 2: Thermal
|  | 9 |  | 4: Inverse
|  | 10 | Reserved |  | 0
|  | 11 | Reserved |  | 0
|  | 12 | Insulation Resistance Test - Type select | 0: Insulation resistance test, 1: Status resistance test | 0
|  | 13 | Insulation Resistance Test - Interlocking OL contact select | 0: Off, 1: Interlocking OL contact | 0
|  | 14 | Insulation Resistance Test - Automatic mode | 0: Manual, 1: Automatic | 0
|  | 15 | Reserved |  | 0
603 | Global Configuration Register 3 | 0 | Supervisor Mode | 0: disable, 1: enabled | 1 | Reg603.11-15 : Write value Reg603.11-14 is allowed only with SPDM display.
|  | 1 | SWD Path | 0: Ethernet, 1: CPU | 1
|  | 2 | Reset Button Mode | 0: Fault Reset, 1: System Reset | 0
|  | 3 | Major Interal Fault Mode | 0: System Reset automatically, 1: Fault Display | 0
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Reserved |  | 0
|  | 7 | Reserved |  | 0
|  | 8 | Reserved |  | 0
|  | 9 | Reserved |  | 0
|  | 10 | Reserved |  | 0
|  | 11 | Alert config 07-08 | 0: none, 1: alert-A, 2: alert-up_F, 3: alert-lo_F, 4: alert-up_H, 5: alert-lo_H | 0
|  | 12 |  | 6: alert-to, 7: alert-uc, 8: Short Protection, 9: Insulation Resistance, 10: MC Counter
|  | 13 |  | 11: Voltage Protection, 12: Power Protection, 13: Voltage Frequency
|  | 14 |  | 14: SPDM_Temp, 15: SPDM_Humidity, 16: SPDM_PT100, 17: SPDM_LC420
|  | 15 |  | 18: Current Degradation, 19: Current THD
604 | Global Configuration Register 4 | 0 | Logic Function | 0: disable, 1: enabled | 0 | Reg604.0-1: It is only allowed on PREMIUM Reference. The logic trip mode(Reg604.1) is automatically activated by default whenever the logic function (Reg604.0) is enabled. And, The logic trip mode(Reg604.1) is automatically deactivated by default whenever the logic function (Reg604.0) is disabled. Reg604.6-10 : It is only allowed if Logic function(Reg604.0) is enabled and PREMIUM Reference. Write value 11-14 is allowed only with SPDM display. Reg604.11-15 : It is only allowed if Logic function(Reg604.0) is enabled and PREMIUM Reference. Write value 11-14 is allowed only with SPDM display.
|  | 1 | Logic Trip Mode | 0: disable, 1: enabled | 0
|  | 2 | Reserved |  | 0
|  | 3 | Reserved |  | 0
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Alert config O1-CO | 0: none, 1: alert-A, 2: alert-up_F, 3: alert-lo_F, 4: alert-up_H, 5: alert-lo_H | 0
|  | 7 |  | 6: alert-to, 7: alert-uc, 8: Short Protection, 9: Insulation Resistance, 10: MC Counter
|  | 8 |  | 11: Voltage Protection, 12: Power Protection, 13: Voltage Frequency
|  | 9 |  | 14: SPDM_Temp, 15: SPDM_Humidity, 16: SPDM_PT100, 17: SPDM_LC420
|  | 10 |  | 18: Current Degradation, 19: Current THD
|  | 11 | Alert config O2-CO | 0: none, 1: alert-A, 2: alert-up_F, 3: alert-lo_F, 4: alert-up_H, 5: alert-lo_H | 0
|  | 12 |  | 6: alert-to, 7: alert-uc, 8: Short Protection, 9: Insulation Resistance, 10: MC Counter | 0
|  | 13 |  | 11: Voltage Protection, 12: Power Protection, 13: Voltage Frequency | 0
|  | 14 |  | 14: SPDM_Temp, 15: SPDM_Humidity, 16: SPDM_PT100, 17: SPDM_LC420 | 0
|  | 15 |  | 18: Current Degradation, 19: Current THD | 0
631 | Fault Enable Status 1 | 0 | Short Enable |  | 0 | Reg631.0: It is not allowed if any alert type(Reg603.11-14 or Reg604.6-10 or Reg604.11-15) is not Short. Reg631.14: It is not allowed If the over current threshold(Reg557) is less than 5A or the ZCT type is external ZCT(Reg601.7=0).
|  | 1 | Stall Enable |  | 0
|  | 2 | Ground Fault Enable |  | 0
|  | 3 | Thermal/Overload Enable | 0: 602.6-7 is zero, 1: 602.6-7 is not zero | 1
|  | 4 | External fault Enable | Always 1 | 1
|  | 5 | Jam Enable |  | 0
|  | 6 | Current Imbalance Enable |  | 0
|  | 7 | Undercurrent Enable |  | 0
|  | 8 | Current Phase Loss Enable |  | 0
|  | 9 | Current Reverse Phase Enable |  | 0
|  | 10 | Test trip Enable | Always 1 | 1
|  | 11 | Internal fault Enable | Always 1 | 1
|  | 12 | PDM Comm Loss Enable |  | 0
|  | 13 | Ethernet Network Comm Loss Enable |  | 0
|  | 14 | Ground Fault (Residual Current) Enable |  | 0
|  | 15 | Serial Network Comm Loss Enable |  | 0
632 | Fault Enable Status 2 | 0 | Reserved |  | 0
|  | 1 | Reserved |  | 0
|  | 2 | Reserved |  | 0
|  | 3 | Reserved |  | 0
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Reserved |  | 0
|  | 7 | Voltage Phase Imbalance Enable |  | 0
|  | 8 | Voltage Phase Loss Enable |  | 0
|  | 9 | Voltage Phase Reversal Enable |  | 0
|  | 10 | UnderVoltage Enable |  | 0
|  | 11 | OverVoltage Enable |  | 0
|  | 12 | UnderPower Enable |  | 0
|  | 13 | OverPower Enable |  | 0
|  | 14 | UnderPowerFactor Enable |  | 0
|  | 15 | OverPowerFactor Enable |  | 0
633 | Fault Enable Status 3 | 0 | Logic Control Diagnosis Fault Enable |  | 0 | Reg633.0: It is only allowed if Logic function(Reg604.0) is enabled and PREMIUM Reference. It is automatically activated by default whenever the logic function (Reg604.0) is enabled,
|  | 1 | Reserved |  | 0
|  | 2 | Reserved |  | 0
|  | 3 | Reserved |  | 0
|  | 4 | Reserved |  | 0
|  | 5 | Reserved |  | 0
|  | 6 | Reserved |  | 0
|  | 7 | Reserved |  | 0
|  | 8 | Reserved |  | 0
|  | 9 | Reserved |  | 0
|  | 10 | Reserved |  | 0
|  | 11 | Reserved |  | 0
|  | 12 | Reserved |  | 0
|  | 13 | Reserved |  | 0
|  | 14 | Reserved |  | 0
|  | 15 | Reserved |  | 0
683 | Logic Control Mode | 0 | Reserved |  | 0 | Reg683.5-6: It is not allowed that Reg683.5-6 can not be all 1. Network and AUTO cannot exist togather.
|  | 1 | Reserved |  | 0
|  | 2 | Reserved |  | 0
|  | 3 | Reserved |  | 0
|  | 4 | Reserved |  | 0
|  | 5 | Network channel | 0: Network not exist, 1: Network exist | 0
|  | 6 | AUTO channel | 0: AUTO not exist, 1: AUTO exist | 0
|  | 7 | Reserved |  | 0
|  | 8 | Local channel | 0: LOP not exist, 1: LOP exist | 1
|  | 9 | MCC channel | 0: MCC not exist, 1: MCC exist | 0
|  | 10 | Bump enable | 0: Bumpless, 1: Bump | 1
|  | 11 | Reserved |  | 0
|  | 12 | Global MCC Stop | 0 - Disable, 1 - Enable | 0
|  | 13 | Global NET Stop | 0 - Disable, 1 - Enable | 0
|  | 14 | Reserved |  | 0
|  | 15 | Reserved |  | 0
704 | Network Control Register | 0 | Logic - Run Command | 0: Off, 1: On |  | Reg704.0: It is only allowed if Logic function(Reg604.0) is enabled and PREMIUM Reference. Reg704.1: It is only allowed if Logic function(Reg604.0) is enabled and PREMIUM Reference. Reg704.5: While the motor is running, the self-test (Reg704.5) cannot be initiated. Reg704.8: It is only allowed if the insulation resistance test type (Reg602.12) is ins and PREMIUM Reference. While the motor is running, the insulation resistance test (Reg704.8) cannot be initiated. Reg704.14: It is only allowed if PREMIUM Reference.
|  | 1 | Reserved
|  | 2 | Logic - Stop Command | 0: Off, 1: On
|  | 3 | Reset | Network fault reset command
|  | 4 | Reserved
|  | 5 | Start Self test
|  | 6 | Reserved
|  | 7 | Start Recording waveform
|  | 8 | Start Insulation Resistance test | Start insulation Resistance test
|  | 9 | Reserved
|  | 10 | Reserved
|  | 11 | Reserved
|  | 12 | Reserved
|  | 13 | Cancel Self test | Cancel Self test
|  | 14 | Cancel Insulation Resistance test | Cancel Insulation Resistance test
|  | 15 | Thermal clear | Write 1 => Clear thermal and ar timer count
705 | RFS (Clear) Register | 0 | RFS_ALL
|  | 1 | RFS_STAT | FaultHistory, Waveform, Date and Time for Motor Monitor
|  | 2 | RFS_THERMAL
|  | 3 | RFS_SETTINGS
|  | 4 | RFS_NETWORKS
|  | 5 | Reserved
|  | 6 | S/W RESET
|  | 7 | Clear Total Power (k Wh, k Var)
|  | 8 | Clear Total Running Hour
|  | 9 | Clear Waveform
|  | 10 | Clear MC Count
|  | 11 | Clear Reset Count
|  | 12 | Reserved
|  | 13 | Reserved
|  | 14 | Reserved
|  | 15 | Reserved
1200 | Logic Status | 0 | Logic - Run Command | 0:Off, 1: On |  | Reg1200.4: The Logic function shall set Reg1200.4 ON while the transition timer is running in Two-Step motor controller. Reg1200.5-7: These bits shows current selected channel. Reg1200.8-9: These bits should be saved NVR(Non Volitile Ram) in EU not to miss after Power-cycle.
|  | 1 | Logic - Stop Command | 0:Off, 1: On
|  | 2 | Fault | 0:Off, 1: On
|  | 3 | Second Step | 0:Off, 1: On
|  | 4 | Transition | 0:Off, 1: On
|  | 5 | Current Selected Channel | 0: None, 1: MCC, 2: Auto, 3: COMM, 4: LOP 5-7: Reserved
6
7
|  | 8 | Last Remote Channel | 0: MCC, 1: Auto, 2: COMM | 0
9
|  | 10 | Reserved
|  | 11 | Reserved
|  | 12 | Reserved
|  | 13 | LO1 Relay | 0 - Off, 1 - On
|  | 14 | LO2 Relay | 0 - Off, 1 - On
|  | 15 | Reserved
Note on B157: btjung: bit #704 0 LO1 1 LO2
Note on G162: Description: Description for Self test bit(Reg704.5) Writing this bit forces the system Self test: - write 1 => launch the self test - write 0 => no action, do not stop the self test. Reading this bit reports about the status of the self test - read 0 => system self test completed - read 1 => self test processing Writng 1 shall be ignored when insulation test is progressing .
Note on G164: Description: Description for Waveform recording bit(Reg704.7) Writing this bit forces the Waveform recording: - write 1 => launch the record waveform - write 0 => no action, Reading this bit reports about the status of the Waveform recording - read 0 => recording waveform is completed - read 1 => recording waveform is processing
Note on G165: Description: Description for Self test bit(Reg704.8) Writing this bit forces the insulation test: - write 1 => launch the insulation test - write 0 => no action, do not stop the insulation test. Reading this bit reports about the status of the insulation test - read 0 => system insulation test completed - read 1 => insulation processing Writng 1 shall be ignored when insulation is progressing .
Note on G170: Description: Description for Self test clear bit(Reg704.13) Writing this bit forces the system stop Self test: - write 1 => stop the self test - write 0 => no action Reading always 0
Note on G171: Description: Description for Self test clear bit(Reg704.14) Writing this bit forces the system stop insulation test: - write 1 => stop the insulation resistance test - write 0 => no action Reading always 0
Note on G172: Description: Description for Thermal clear bit(Reg704.15) Writing this bit forces the system clear thermal memory & rapid cycle timer: - write 1 => clear thermal memory & rapid cycle timer - write 0 => no action Reading always 0

## Map
INFORMATION !!
■ MODBUS Master can read up to 121 registers of EOCR-iSEM2 in a row ■ EOCR-iSEM2 supports the following MODBUS function codes 03: Read holding registers 06: Write single register 16: Write multiple registers ■ Undefined registers between 70 and 700 shall be treated as reserved register.
Address | Description | Permisstion | Type | Unit | Min | Max | Step | Default | Attribute | F/W Sub-Map | Comment | Comment2
45 | CPU Usage | Read Only | u16 | % | 0 | 100 |  | - | None | PRO_MAP
46 | ADC CH0 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
47 | ADC CH0 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
48 | ADC CH1 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
49 | ADC CH1 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
50 | ADC CH2 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
51 | ADC CH2 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
52 | ADC CH3 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
53 | ADC CH3 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
54 | ADC CH4 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
55 | ADC CH4 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
56 | ADC CH5 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
57 | ADC CH5 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
58 | ADC CH6 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
59 | ADC CH6 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
60 | ADC CH7 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
61 | ADC CH7 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
62 | ADC CH8 Scaled Data MSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
63 | ADC CH8 Scaled Data LSB | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
64 | ADC CH9 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
65 | ADC CH10 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
66 | ADC CH11 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
67 | ADC CH12 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
68 | ADC CH13 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
69 | ADC CH14 Scaled Data | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
70 | Control unit serial nbr : CCCC = Reference | R/Wman | u16 | Word | 6201 | 6203 |  | - | None | MAN_MAP
71 | Control unit serial nbr : YYWWD = Year/Week/Day | R/Wman | u16 | Word | 0 | 65535 |  | - | None | MAN_MAP
72 | Control unit serial nbr : ZZXXX = Batch/Running | R/Wman | u16 | Word | 0 | 65535 |  | - | None | MAN_MAP
73 | Control unit serial nbr : RR = Revision | R/Wman | u16 | Word | 0 | 99 |  | - | None | MAN_MAP
76 | sEOCR - Version Number | Read Only | u16 | Unit | - | - |  | - | None | MOTOR_MAP
80 | PDM - Version Number | Read Only | u16 | Unit | - | - |  | - | None | MOTOR_MAP
94 | CT ratio : MSB | Read Only | u16 | 0.01 | - | - |  | - | None | MOTOR_MAP
95 | CT ratio : LSB | Read Only | u16 | 0.01 | - | - |  | - | None | MOTOR_MAP
98 | Current Loop Limit | R/Wnet | u16 | 100(*10) mA | 0 | 1000 (*) | * | 0 | Settings | PRO_MAP
115 | AutoResetCount | Read Only | u16 | Unit | - | - |  | - | None | PRO_MAP
119 | Total Running Hour : MSB | Read Only | u16 | 0.1 hour | - | - |  | - | None | MOTOR_MAP
120 | Total Running Hour : LSB | Read Only | u16 | 0.1 hour | - | - |  | - | None | MOTOR_MAP
130 | MC Counter Set | R/Wnet | u16 | 100 | 0 | 9900 | * | 0 | Settings | MOTOR_MAP
131 | MC Counter Mode | R/Wnet | u16 | Unit | 0 | 1 | 1 | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
132 | MC Counter Display : MSB | Read Only | u16 | Unit | - | - |  | 0 | Settings | MOTOR_MAP |  | MC ON/OFF Count :MSB
133 | MC Counter Display : LSB | Read Only | u16 | Unit | - | - |  | 0 | Settings | MOTOR_MAP |  | MC ON/OFF Count :LSB
134 | MC Counter Recognition Level | R/Wnet | u16 | 100(*10) mA | 4 | 80% of OC/UC | * | 4 | Settings | MOTOR_MAP
135 | MC Counter Recognition Time | R/W | u16 | 0.1sec | 0 | 50 | 1 | 5 | Settings | MOTOR_MAP
136 | MC Counter Recognition Active Power | R/Wnet | u16 | 1 W | 100 | 65500 | 100 | 100 | Settings | MOTOR_MAP
143 | Active Power Consumption : MSB | Read Only | u16 | 0.01 kWh | - | - |  | - | None | METER_MAP |  | 유효 전력량(KWh) : MSB
144 | Active Power Consumption : LSB | Read Only | u16 | 0.01 kWh | - | - |  | - | None | METER_MAP |  | 유효 전력량(KWh) : LSB
145 | Reactive Power Consumption : MSB | Read Only | u16 | 0.01 kVARh | - | - |  | - | None | METER_MAP |  | 무효 전력량(KVarh) : MSB
146 | Reactive Power Consumption : LSB | Read Only | u16 | 0.01 kVARh | - | - |  | - | None | METER_MAP |  | 무효 전력량(KVarh) : LSB
150 | Fault Number (Trip n-0) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
151 | Fault Phase (Trip n-0) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
155 | Fault Threshold (Trip n-0) | Read Only | u16 | 0.1 A | - | - |  | - | Statistics | FAULT_MAP
156 | Fault duration (Trip n-0) | Read Only | u16 | - | - | - |  | - | Statistics | FAULT_MAP
162 | Date and Time1 (Trip n-0) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-0) fault - SSXX = second / reserved
163 | Date and Time2 (Trip n-0) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-0) fault - HHMM = hour / minute
164 | Date and Time3 (Trip n-0) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-0) fault - MMDD = month / day
165 | Date and Time4 (Trip n-0) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-0) fault - YYYY = year
166 | L3L1 voltage (Trip n-0) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
167 | L1L2 voltage (Trip n-0) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
168 | L2L3 voltage (Trip n-0) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
169 | Active Power (Trip n-0) | Read Only | u16 | 0.1kW | - | - |  | - | Statistics | FAULT_MAP
170 | Reactive Power (Trip n-0) | Read Only | u16 | 0.1VAR | - | - |  | - | Statistics | FAULT_MAP
171 | PowerFactor (Trip n-0) | Read Only | u16 | 0.01 | - | - |  | - | Statistics | FAULT_MAP
180 | Fault Number (Trip n-1) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
181 | Fault Phase (Trip n-1) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
185 | Fault Threshold (Trip n-1) | Read Only | u16 | 0.1 A | - | - |  | - | Statistics | FAULT_MAP
186 | Fault duration (Trip n-1) | Read Only | u16 | - | - | - |  | - | Statistics | FAULT_MAP
192 | Date and Time1 (Trip n-1) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-1) fault - SSXX = second / reserved
193 | Date and Time2 (Trip n-1) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-1) fault - HHMM = hour / minute
194 | Date and Time3 (Trip n-1) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-1) fault - MMDD = month / day
195 | Date and Time4 (Trip n-1) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-1) fault - YYYY = year
196 | L3L1 voltage (Trip n-1) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
197 | L1L2 voltage (Trip n-1) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
198 | L2L3 voltage (Trip n-1) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
199 | Active Power (Trip n-1) | Read Only | u16 | 0.1kW | - | - |  | - | Statistics | FAULT_MAP
200 | Reactive Power (Trip n-1) | Read Only | u16 | 0.1VAR | - | - |  | - | Statistics | FAULT_MAP
201 | PowerFactor (Trip n-1) | Read Only | u16 | 0.01 | - | - |  | - | Statistics | FAULT_MAP
210 | Fault Number (Trip n-2) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
211 | Fault Phase (Trip n-2) | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
215 | Fault Threshold (Trip n-2) | Read Only | u16 | 0.1 A | - | - |  | - | Statistics | FAULT_MAP
216 | Fault duration (Trip n-2) | Read Only | u16 | - | - | - |  | - | Statistics | FAULT_MAP
222 | Date and Time1 (Trip n-2) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-2) fault - SSXX = second / reserved
223 | Date and Time2 (Trip n-2) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-2) fault - HHMM = hour / minute
224 | Date and Time3 (Trip n-2) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-2) fault - MMDD = month / day
225 | Date and Time4 (Trip n-2) | Read Only | u16 | Word | - | - |  | - | Statistics | FAULT_MAP | (n-2) fault - YYYY = year
226 | L3L1 voltage (Trip n-2) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
227 | L1L2 voltage (Trip n-2) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
228 | L2L3 voltage (Trip n-1) | Read Only | u16 | 0.1 V | - | - |  | - | Statistics | FAULT_MAP
229 | Active Power (Trip n-2) | Read Only | u16 | 0.1kW | - | - |  | - | Statistics | FAULT_MAP
230 | Reactive Power (Trip n-2) | Read Only | u16 | 0.1VAR | - | - |  | - | Statistics | FAULT_MAP
231 | PowerFactor (Trip n-2) | Read Only | u16 | 0.01 | - | - |  | - | Statistics | FAULT_MAP
302 | L1 Current (Trip n-0) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
303 | L1 Current (Trip n-0) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
304 | L2 Current (Trip n-0) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
305 | L2 Current (Trip n-0) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
306 | L3 Current (Trip n-0) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
307 | L3 Current (Trip n-0) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
308 | Ground Current (Trip n-0) : MSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
309 | Ground Current (Trip n-0) : LSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
332 | L1 Current (Trip n-1) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
333 | L1 Current (Trip n-1) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
334 | L2 Current (Trip n-1) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
335 | L2 Current (Trip n-1) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
336 | L3 Current (Trip n-1) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
337 | L3 Current (Trip n-1) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
338 | Ground Current (Trip n-1) : MSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
339 | Ground Current (Trip n-1) : LSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
362 | L1 Current (Trip n-2) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
363 | L1 Current (Trip n-2) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
364 | L2 Current (Trip n-2) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
365 | L2 Current (Trip n-2) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
366 | L3 Current (Trip n-2) : MSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
367 | L3 Current (Trip n-2) : LSB | Read Only | u16 | 0.01 A | - | - |  | - | Statistics | FAULT_MAP
368 | Ground Current (Trip n-2) : MSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
369 | Ground Current (Trip n-2) : LSB | Read Only | u16 | 1 mA | - | - |  | - | Statistics | FAULT_MAP
451 | Fault number | Read Only | u16 | Unit | - | - |  | - | Statistics | FAULT_MAP
452 | Fault Status 1 | Read Only | u16 | Bit Field | - | - |  | - | None | FAULT_MAP
453 | Fault Status 2 | Read Only | u16 | Bit Field | - | - |  | - | None | FAULT_MAP
454 | Fault Status 3 | Read Only | u16 | Bit Field | - | - |  | - | None | FAULT_MAP
455 | Global Status register | Read Only | u16 | Bit Field | - | - |  | - | None | MOTOR_MAP |  | 모터 상태: 운전, 정지, 트립
456 | System Status register | Read Only | u16 | Bit Field | - | - |  | - | None | MOTOR_MAP
457 | Logic Input Status | Read Only | u16 | Bit Field | - | - |  | - | None | DIO_MAP
458 | Logic Output Status | Read Only | u16 | Bit Field | - | - |  | - | None | DIO_MAP
459 | Logic LED Status | Read Only | u16 | Bit Field | - | - |  | - | None | DIO_MAP
462 | Warning Status1 | Read Only | u16 | Bit Field | - | - |  | - | None | FAULT_MAP
463 | Warning Status2 | Read Only | u16 | Bit Field | - | - |  | - | None | FAULT_MAP
465 | Thermal Capacity Level | Read Only | u16 | % Trip Level | 0 | 200 |  | - | Thermal | METER_MAP
466 | Current Max Ratio | Read Only | u16 | % OC | 0 | 65535 |  | - | None | METER_MAP
467 | L1 Current Ratio | Read Only | u16 | % Inom | 0 | 65535 |  | - | None | METER_MAP
468 | L2 Current Ratio | Read Only | u16 | % Inom | 0 | 65535 |  | - | None | METER_MAP
469 | L3 Current Ratio | Read Only | u16 | % Inom | 0 | 65535 |  | - | None | METER_MAP
471 | Current Unbalance Max | Read Only | u16 | % imb | - | - |  | - | None | METER_MAP
474 | Frequency of Voltage | Read Only | u16 | 0.1 Hz | - | - |  | - | None | METER_MAP |  | 전압 주파수
476 | Average Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP
477 | L3-L1 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | L3-L1 선간 전압
478 | L1-L2 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | L1-L2 선간 전압
479 | L2-L3 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | L2-L3 선간 전압
480 | Voltage Unbalance Max | Read Only | u16 | % imb | - | - |  | - | None | METER_MAP
481 | PowerFactor | Read Only | u16 | 0.01 | 0 | 100 | 1 | - | None | METER_MAP |  | 역률
482 | PowerFactor Status (Lag / Lead) | Read Only | u16 | Unit | 0 | 1 | 1 | - | None | METER_MAP |  | 지상 / 진상
483 | Phase Shift Angle | Read Only | u16 | 0.1 degree | - | - |  | - | None | METER_MAP |  | 위상각
484 | Network Write Access | R/W | u16 | Unit | - | 1 |  | 0 | Settings | MOTOR_MAP
485 | Last Power Off Duration | Read Only | u16 | 0.1sec | 0 | 65535 |  | - | None | METER_MAP
486 | Active Power: MSB | Read Only | u16 | 1 W | - | - |  | - | None | METER_MAP |  | 유효 전력(W) : MSB
487 | Active Power: LSB | Read Only | u16 | 1 W | - | - |  | - | None | METER_MAP |  | 유효 전력(W) : LSB
488 | Reactive Power: MSB | Read Only | u16 | 1 Var | - | - |  | - | None | METER_MAP |  | 무효 전력(VAR) : MSB
489 | Reactive Power: MSB | Read Only | u16 | 1 Var | - | - |  | - | None | METER_MAP |  | 무효 전력(Var) : LSB
499 | Frequency of Current | Read Only | u16 | 0.1 Hz | - | - |  | - | None | METER_MAP |  | 전류 주파수
500 | Avg Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 3상 전류의 평균값 : MSB
501 | Avg Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 3상 전류의 평균값 : LSB
502 | L1 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L1 상 전류 : MSB
503 | L1 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L1 상 전류 : LSB
504 | L2 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L2 상 전류 : MSB
505 | L2 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L2 상 전류 : LSB
506 | L3 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L3 상 전류 : MSB
507 | L3 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 L3 상 전류 : LSB
508 | Ground Current : MSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP |  | 16ms 주기의 지락 전류 : MSB
509 | Ground Current : LSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP |  | 16ms 주기의 지락 전류 : LSB
510 | Max Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 3상 중 최대상의 전류 : MSB
511 | Max Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 100ms 주기의 3상 중 최대상의 전류 : LSB
512 | Residual Current : MSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP |  | 100ms 주기의 잔류 전류 : MSB
513 | Residual Current : LSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP |  | 100ms 주기의 잔류 전류 : LSB
515 | Unbalance Max Phases | Read Only | u16 | Bit Field | - | - |  | - | None | METER_MAP
520 | Fast Avg Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 3상 전류의 평균값 : MSB
521 | Fast Avg Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 3상 전류의 평균값 : LSB
522 | Fast L1 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L1 상 전류 : MSB
523 | Fast L1 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L1 상 전류 : LSB
524 | Fast L2 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L2 상 전류 : MSB
525 | Fast L2 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L2 상 전류 : LSB
526 | Fast L3 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L3 상 전류 : MSB
527 | Fast L3 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L3 상 전류 : LSB
530 | Fast Max Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 3상 중 최대상의 전류 : MSB
531 | Fast Max Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP |  | 33ms 주기의 3상 중 최대상의 전류 : LSB
536 | Voltage Min Ratio | Read Only | u16 | % Vnom | - | - |  | - | None | METER_MAP
476 | Fast Average Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | 33ms 주기의 3상 선간 전압의 평균값
537 | Fast L3-L1 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L3-L1 선간 전압
538 | Fast L1-L2 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L1-L2 선간 전압
539 | Fast L2-L3 Voltage | Read Only | u16 | 0.1 V | - | - |  | - | None | METER_MAP |  | 33ms 주기의 L2-L3 선간 전압
540 | Logic Operating Mode | R/Wsys | u16 | Bit Field | - | - |  | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
541 | Logic Y-D Transition Time | R/Wnet | u16 | 0.1 Sec | 0 | 30 | 1 | 10 | Settings | MOTOR_MAP | PREMIUM Reference Only
542 | Running Hour : MSB | Read Only | u16 | 0.1 hour | - | 255 |  | 0 | Statistics | METER_MAP
543 | Running Hour : LSB | Read Only | u16 | 0.1 hour | - | 65535 |  | 0 | Statistics | METER_MAP
544 | Alert Threshold for Running Hour | R/Wnet | u16 | 1 hour | - | 9990 | * | 0 | Settings | PRO_MAP
545 | Logic AC Input Type | R/Wnet | u16 | Unit | 0 | 2 | 1 | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
547 | Thermal overload trip class | R/Wnet | u16 | Unit | 1 | 30 |  | 5 | Settings | PRO_MAP
558 | Under Alert Threshold | R/Wnet | u16 | % UC | 50 | 100 |  | 50 | Settings | PRO_MAP
553 | Logic Rapid Cycle timeout | R/Wnet | u16 | 1 Sec | 0 | 999 | 1 | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
554 | Auto Reset Limit in 30 minutes | R/Wnet | u16 | Unit | - | 5 |  | 0 | Settings | MOTOR_MAP
555 | Current Phase Loss Fault Duration | R/Wnet | u16 | 0.01 Sec | 50 | 500 | * | 200 | Settings | PRO_MAP
556 | Over Current Fault Duration | R/Wnet | u16 | 0.01 Sec | 20 | 12000 | * | 500 | Settings | PRO_MAP
557 | Over Current Fault Threshold | R/Wnet | u16 | 100(*10) mA | 5 | 1000 (*) | * | 50 (*) | Settings | PRO_MAP
558 | Over Alert Threshold | R/Wnet | u16 | % OC | 50 | 100 |  | 50 | Settings | PRO_MAP
562 | Ground Fault Duration | R/Wnet | u16 | 0.001 Sec | 30 | 10000 |  | 1000 | Settings | PRO_MAP
563 | Ground Fault Threshold | R/Wnet | u16 | 0.01 A | 3 | 1000 |  | 250 | Settings | PRO_MAP
564 | Ground Fault Detection Delay | R/Wnet | u16 | 0.001 Sec | 0 | 30000 |  | 0 | Settings | PRO_MAP
565 | Motor Norminal Voltage | R/Wnet | u16 | 1 V | 110 | 690 |  | 440 | Settings | MOTOR_MAP
566 | Voltage Phase Imbalance Fault Duration | R/Wnet | u16 | 0.01 Sec | 20 | 2000 | 10 | 500 | Settings | PRO_MAP
568 | Voltage Phase Imbalance Fault Threshold | R/Wnet | u16 | % imb | 3 | 15 | 1 | 10 | Settings | PRO_MAP
570 | Over voltage Fault Duration | R/Wnet | u16 | 0.01 Sec | 20 | 3000 | 10 | 300 | Settings | PRO_MAP
571 | Over voltage Fault Threshold | R/Wnet | u16 | % Vnom | 101 | 115 | 1 | 110 | Settings | PRO_MAP
573 | Under voltage Fault Duration | R/Wnet | u16 | 0.01Sec | 20 | 3000 | 1 | 300 | Settings | PRO_MAP
574 | Under voltage Fault Threshold | R/Wnet | u16 | % Vnom | 70 | 99 | 1 | 85 | Settings | PRO_MAP
576 | Voltage phase loss fault Fault Duration | R/Wnet | u16 | 0.01 Sec | 10 | 3000 | 10 | 200 | Settings | PRO_MAP
583 | Motor Norminal Power | R/Wnet | u16 | 0.1kW | 1 | 65500 |  | 750 | Settings | MOTOR_MAP
584 | Over power Fault Duration | R/Wnet | u16 | 1 Sec | 1 | 100 |  | 60 | Settings | PRO_MAP
585 | Over power Fault Threshold | R/Wnet | u16 | % Pnom | 101 | 800 | 1 | 150 | Settings | PRO_MAP
587 | Under power Fault Duration | R/Wnet | u16 | 0.01Sec | 1 | 30 |  | 1 | Settings | PRO_MAP
588 | Under power Fault Threshold | R/Wnet | u16 | % Pnom | 20 | 99 |  | 20 | Settings | PRO_MAP
590 | Under power factor Fault Duration | R/Wnet | u16 | 0.01Sec | 100 | 3000 |  | 1000 | Settings | PRO_MAP
591 | Under power factor Fault Threshold | R/Wnet | u16 | 0.01 PF | 0 | 100 |  | 60 | Settings | PRO_MAP
593 | Over power factor Fault Duration | R/Wnet | u16 | 0.1 sec | 200 | 3000 | 10 | 1000 | Settings | PRO_MAP
594 | Over power factor Fault Threshold | R/Wnet | u16 | 0.01 PF | 0 | 100 | 1 | 90 | Settings | PRO_MAP
600 | HMI Password for Parameter Security | Read Only | u16 | Unit | - | 999 |  | 0 | None | HMI_MAP
601 | Global configuration Register 1 | R/Wsys | u16 | Bit Field | - | - |  | 0x0280 | Settings | MOTOR_MAP
602 | Global configuration Register 2 | R/Woff_net | u16 | Bit Field | - | - |  | 0x0081 | Settings | MOTOR_MAP
603 | Global configuration Register 3 | R/Woff_net | u16 | Bit Field | - | - |  | 0x0003 | Settings | MOTOR_MAP
604 | Global configuration Register 4 | R/Woff_net | u16 | Bit Field | - | - |  | 0x0000 | Settings | MOTOR_MAP
605 | Short Circuit Fault Threshold | R/Wnet | u16 | % OC | 200 | 5000 |  | 1000 | Settings | PRO_MAP
607 | Short Detection Delay | R/Wnet | u16 | 0.001 Sec | - | 20000 | 1000 | 0 | Settings | PRO_MAP
611 | Residual Current Fault Threshold | R/Wnet | u16 | % OC | 30 | 100 |  | 100 | Settings | PRO_MAP
614 | Current imbalance Fault Duration | R/Wnet | u16 | 0.01 Sec | 100 | 1000 | 100 | 500 | Settings | PRO_MAP
615 | Current imbalance Fault Threshold | R/Wnet | u16 | % imb | 10 | 50 | 1 | 50 | Settings | PRO_MAP
617 | Jam Fault Duration | R/Wnet | u16 | 0.01Sec | 20 | 1000 | * | 500 | Settings | PRO_MAP
618 | Jam Fault Threshold | R/Wnet | u16 | % OC | 150 | 800 | 10(100) | 400 | Settings | PRO_MAP
620 | Under current Fault Duration | R/Wnet | u16 | 0.01Sec | 50 | 12000 | * | 500 | Settings | PRO_MAP
621 | Under current Fault Threshold | R/Wnet | u16 | 100(*10) mA | 5 | OC - 1step | * | 5 | Settings | PRO_MAP
623 | Stall Fault Duration | R/Wnet | u16 | 1 Sec | - | 600 |  | 5 | Settings | PRO_MAP
624 | Stall Fault Threshold | R/Wnet | u16 | % OC | 200 | 800 |  | 400 | Settings | PRO_MAP
628 | Load CT Primary | R/Wsys | u16 | Unit | 1 | 5000 | 5 | 1 | Settings | MOTOR_MAP
629 | Load CT Secondary | R/Wsys | u16 | Unit | 1 | 5 | * | 1 | Settings | MOTOR_MAP
630 | Load CT Mutiple Passes | R/Wsys | u16 | Unit | 1 | 5 | 1 | 1 | Settings | MOTOR_MAP
631 | Fault enable status 1 | R/Wnet | u16 | Bit Field | - | - |  | 0x0C18 | Settings | PRO_MAP
632 | Fault enable status 2 | R/Wnet | u16 | Bit Field | - | - |  | 0x0000 | Settings | PRO_MAP
633 | Fault enable status 3 | R/Wnet | u16 | Bit Field | - | - |  | 0x0000 | Settings | PRO_MAP
638 | Auto Reset Delay | R/Wnet | u16 | 0.1Sec | 5 | 12000 |  | 50 | Settings | PRO_MAP
643 | Logic Y-D One Step Time | R/Wnet | u16 | 0.1Sec | 1 | 9990 |  | 30 | Settings | MOTOR_MAP | PREMIUM Reference Only
652 | Motor Norminal Current | R/Wnet | u16 | 100(*10) mA | 5 | 1000 (*) | * | 50 (*) | Settings | MOTOR_MAP
655 | Date and Time setting1 | R/Wnet | u18 | Word | 0x0000 | 0x5900 |  | 0x0000 | Settings | MOTOR_MAP
656 | Date and Time setting2 | R/Wnet | u19 | Word | 0x0000 | 0x2359 |  | 0x0000 | Settings | MOTOR_MAP
657 | Date and Time setting3 | R/Wnet | u20 | Word | 0x0101 | 0x1231 |  | 0x0101 | Settings | MOTOR_MAP
658 | Date and Time setting4 | R/Wnet | u21 | Word | 0x2020 | 0x2099 |  | 0x2020 | Settings | MOTOR_MAP
661 | Voltage Frequency Alert Threshold | R/Wnet | u16 | 0.1 Hz | 450 | 750 | 1 | 700 | Settings | PRO_MAP
670 | Metering Pulse Constant | R/Wnet | u16 | 1 Wh | 100 | 9000 |  | 100 | Settings | MOTOR_MAP
671 | Motor Cycle Optimized Status | Read Only | u16 | Word | - | - |  | - | None | MOTOR_MAP
683 | Logic Control Mode | R/Wsys | u16 | Bit Field | - | - |  | 0x0500 | Settings | MOTOR_MAP | PREMIUM Reference Only
684 | Logic LI1 Function Mode | R/Wsys | u16 | Unit | 0 | 1 | 1 | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
685 | Logic LI4 Function Mode | R/Wsys | u16 | Unit | 0 | 1 | 1 | 0 | Settings | MOTOR_MAP | PREMIUM Reference Only
686 | Logic LI5 Function Mode | R/Wsys | u16 | Unit | 0 | 2 | 1 | 2 | Settings | MOTOR_MAP | PREMIUM Reference Only
692 | Ethernet Network Loss Timeout (Modbus TCP) | R/Wnet | u16 | 1 Sec | 1 | 990 | 1 | 10 | Network | COM_MAP
693 | Serial Network Loss Timeout (Modbus RTU) | R/Wnet | u16 | 1 Sec | 1 | 990 | 1 | 10 | Network | COM_MAP
694 | Network port parity setting | R/Wnet | u16 | Unit | 0 | 3 |  | 1 | Network | COM_MAP
695 | Network communication speed setting | R/Wnet | u16 | Word | 1200 | 57600 |  | 19200 | Network | COM_MAP
696 | Slave address setting on network | R/Wnet | u16 | Word | 1 | 247 |  | 1 | Network | COM_MAP
700 | Heartbeat | Read Only | u16 | Unit | - | - |  | - | Network | COM_MAP
704 | Network Control Register | R/W | u16 | Bit Field | - | - |  | - | Settings | DIO_MAP
705 | MOP Command Register (from IEC61915) | R/Woff_net | u16 | Bit Field | - | - |  | 0 | Settings | MOTOR_MAP
710 | Reset count : POR | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
711 | Reset count : External | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
712 | Reset count : Internal | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
713 | Reset count : Software | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
714 | Reset count : RFS | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
715 | Reset count : Syscfg | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
716 | Reset count : Minor Internal Fault | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
717 | Reset count : Major Internal Fault | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | MOTOR_MAP
730 | Insulation Resistance Test Status | Read Only | u16 | Unit | 0 | 32767 |  | 0 | None | DIO_MAP | PREMIUM Reference Only
731 | Insulation Resistance Test Auto Delay | R/Wnet | u16 | 0.1Sec | 3000 | 36000 | 600 | 6000 | Settings | DIO_MAP | PREMIUM Reference Only
732 | Insulation Resistance Test Auto Delay Remaining | Read Only | u16 | 0.1Sec | - | - |  | 0 | None | DIO_MAP | PREMIUM Reference Only
733 | Insulation Resistance Test Level | R/Wnet | u16 | 0.01 Mohms | 100 | 1000 | 100 | 1000 | Settings | DIO_MAP | PREMIUM Reference Only
734 | Insulation Resistance Test Value | Read Only | u16 | 0.01 Mohms | 0 | 30000 |  | - | None | DIO_MAP | PREMIUM Reference Only
800~898 | Remap : User Map Address | R/W | u16 | Word | - | - |  | - | None | IND_ADD_MAP
900~998 | Remap : User Map Values | R/Windirect | u16 | Word | - | - |  | - | None | IND_VAL_MAP
1000 | PDM Keypad state | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1001 | PDM Display : LSB=digit1 / MSB=digit2 | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1002 | PDM Display : LSB=digit3 / MSB=digit4 | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1003 | PDM Display : LSB=digit5 / MSB=digit6 | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1004 | PDM Display : LSB=digit7 / MSB=reserved | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1005 | OCU LED indicator | Read Only | u16 | Bit Field | - | - |  | - | None | HMI_MAP
1006 | OCU Command register | Read Only | u16 | Bit Field | - | - |  | - | None | HMI_MAP
1010 | PDM Display Add Type | R/W | u16 | Unit | 1 | 3 | 1 | 2 | Settings | HMI_MAP
1020 | PDM Firmware Version | R/W | u16 | Word | - | - |  | - | None | HMI_MAP
1021 | Temperature of sensor in SPDM | R/W | s16 | 0.1 °C | -32768 | 32767 | 1 | 32767 | None | HMI_MAP |  | 온도
1022 | Humidity of sensor in PDM | R/W | u16 | 1% | 0 | 65535 | 1 | 65535 | None | HMI_MAP |  | 습도
1023 | Temperature of PT100 in SPDM | R/W | s16 | 0.1 °C | -32768 | 32767 | 1 | 32767 | None | HMI_MAP |  | PT100
1024 | 420 input in PDM | R/W | u16 | 0.01 mA | 0 | 65535 | 1 | 65535 | None | HMI_MAP |  | 4-20mA 입력
1025 | Temperature Offset of PT100 in SPDM | R/W | s16 | 0.1 °C | -32768 | 32767 | 1 | 0 | None | HMI_MAP
1030 | Waveform page select | R/W | u16 | Unit | 0 | 1 |  | - | None | DIO_MAP
1031 | Waveform Index | R/W | u16 | Unit | 0 | 199 |  | - | None | DIO_MAP
1032 | Waveform data0 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1033 | Waveform data1 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1034 | Waveform data2 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1035 | Waveform data3 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1036 | Waveform data4 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1037 | Waveform data5 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1038 | Waveform data6 | Read Only | u16 | Unit | - | - |  | - | Statistics | DIO_MAP
1100 | PDM Manufactured mode | Read Only | u16 | Word | - | - |  | - | None | HMI_MAP
1200 | Logic Status | Read Only | u16 | Bit Field | - | - |  | - | None | DIO_MAP
1201 | Logic Version | Read Only | u16 | Word | - | - |  | - | None | DIO_MAP
1270 | External System status | R/W | u16 | Bit Field | - | - |  | - | None | DIO_MAP
1300 | Motor Monitor Enable Status for Waveform | R/W | u16 | Bit Field | - | - |  | 0x0000 | None | DIO_MAP
1301 | Motor Monitor Start Date and Time1 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | SSXX = second / reserved
1302 | Motor Monitor Start Date and Time2 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | HHMM = hour / minute
1303 | Motor Monitor Start Date and Time3 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | MMDD = month / day
1304 | Motor Monitor Start Date and Time4 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | YYYY = year
1305 | Motor Monitor Stop Date and Time1 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | SSXX = second / reserved
1306 | Motor Monitor Stop Date and Time2 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | HHMM = hour / minute
1307 | Motor Monitor Stop Date and Time3 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | MMDD = month / day
1308 | Motor Monitor Stop Date and Time4 | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP | YYYY = year
1320 | Motor Monitor Operating time MSB | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP
1321 | Motor Monitor Operating time LSB | Read Only | u16 | Word | - | - |  |  | None | DIO_MAP
1500 | Temperature on CPU Junction | Read Only | u16 | °C | -40 | 125 |  | - | None | METER_MAP
1510 | Internal reference voltage | Read Only | u16 | 0.001V | - | - |  | - | None | METER_MAP
1511 | Analog Voltage Supply | Read Only | u16 | 0.001V | - | - |  | - | None | METER_MAP
1512 | External Battery Voltage Supply (Super capacitor) | Read Only | u16 | 0.001V | - | - |  | - | None | METER_MAP
1513 | Main Power Supply 12VDC | Read Only | u16 | 0.001V | - | - |  | - | None | METER_MAP
1520 | Internal Ground Current Saturation Count | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
1521 | External Ground Current Saturation Count | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP
2000 | Average - Avg Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2001 | Average - Avg Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2002 | Average - L1 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2003 | Average - L1 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2004 | Average - L2 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2005 | Average - L2 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2006 | Average - L3 Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2007 | Average - L3 Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2008 | Average - Ground current : MSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP
2009 | Average - Ground current : LSB | Read Only | u16 | 1 mA | - | - |  | - | None | METER_MAP
2010 | Average - Max Rms Current : MSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2011 | Average - Max Rms Current : LSB | Read Only | u16 | 0.01 A | - | - |  | - | None | METER_MAP
2012 | Average - L3-L1 voltage | Read Only | u16 | 1 V | - | - |  | - | None | METER_MAP
2013 | Average - L1-L2 voltage | Read Only | u16 | 1 V | - | - |  | - | None | METER_MAP
2014 | Average - L2-L3 voltage | Read Only | u16 | 1 V | - | - |  | - | None | METER_MAP
2015 | Average - PowerFactor | Read Only | u16 | 0.01 | 0 | 100 | 1 | - | None | METER_MAP
2016 | Average - Active Power | Read Only | u16 | 0.1kW | - | - |  | - | None | METER_MAP
2017 | Average - Reactive Power | Read Only | u16 | 0.1VAR | - | - |  | - | None | METER_MAP
2101 | L1 Current CF | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP |  | L1 전류 파고율
2102 | L2 Current CF | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP |  | L2 전류 파고율
2103 | L3 Current CF | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP |  | L3 전류 파고율
2105 | Max Current CF | Read Only | u16 | Unit | - | - |  | - | None | METER_MAP |  | 최대 전류 파고율
2197 | Fundamental Frequency Mode | R/Wnet | u16 | Unit | 0 | 1 | 1 | 0 | Settings | MOTOR_MAP
2198 | Current Fundamental Frequency | Read Only | u16 | 0.1 Hz | - | - |  | - | None | METER_MAP |  | 전류 기본 주파수
2199 | Voltage Fundamental Frequency | Read Only | u16 | 0.1 Hz | - | - |  | - | None | METER_MAP |  | 전압 기본 주파수
2200 | Avg Current THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 평균 전류 전 고조파 왜곡율
2201 | L1 Current THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L1 전류 전 고조파 왜곡율
2202 | L2 Current THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L2 전류 전 고조파 왜곡율
2203 | L3 Current THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L3 전류 전 고조파 왜곡율
2204 | Max Current THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 최대 전류 전 고조파 왜곡율
2205 | Total Current Degradation | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 토탈 전류 저하도
2206 | L1 Current Degradation | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L1 전류 저하도
2207 | L2 Current Degradation | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L2 전류 저하도
2208 | L3 Current Degradation | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L3 전류 저하도
2209 | Max Current Degradation | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 최대 전류 저하도
2210 | L1 Fundamental Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L1 기본 주파수 전류 : MSB
2211 | L1 Fundamental Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L1 기본 주파수 전류 : LSB
2212 | L2 Fundamental Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L2 기본 주파수 전류 : MSB
2213 | L2 Fundamental Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L2 기본 주파수 전류 : LSB
2214 | L3 Fundamental Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L3 기본 주파수 전류 : MSB
2215 | L3 Fundamental Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L3 기본 주파수 전류 : LSB
2220 | L1 Total Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L1 전체 전류 : MSB
2221 | L1 Total Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L1 전체 전류 : LSB
2222 | L2 Total Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L2 전체 전류 : MSB
2223 | L2 Total Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L2 전체 전류 : LSB
2224 | L3 Total Current : MSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L3 전체 전류 : MSB
2225 | L3 Total Current : LSB | Read Only | u16 | 0.001 A | - | - |  | - | None | METER_MAP |  | L3 전체 전류 : LSB
2800 | Fundamental Current Cutoff Level | R/Wnet | u16 | 100(*10) mA | 3 | 1000 (*) | * | 3 | Settings | MOTOR_MAP
2801 | Fundamental Voltage Cutoff Level | R/Wnet | u16 | 0.1 V | 10 | 690 | * | 10 | Settings | MOTOR_MAP
2840 | Alarm Level for Current THD | R/Wnet | u16 | 0.01% | 0 | 10000 | 100 | 1000 | Settings | PRO_MAP
2841 | Alarm Duration for Current THD | R/Wnet | u16 | 1 Sec | 1 | 990 | 1 | 60 | Settings | PRO_MAP
2860 | Alarm Level for Current Degradation | R/Wnet | u16 | 0.01% | 100 | 30000 | 100 | 1000 | Settings | PRO_MAP
2861 | Alarm Duration for Current Degradation | R/Wnet | u16 | 1 Sec | 10 | 990 | 1 | 60 | Settings | PRO_MAP
2899 | Alarm Duration for Sensor PDM | R/Wnet | u16 | 1 Sec | 1 | 990 | 1 | 60 | Settings | PRO_MAP
2900 | Alarm High Lev for Temperature of sensor in PDM | R/W | s16 | 0.1 C | -400 | 1000 | 10 | 1000 | Settings | PRO_MAP
2901 | Alarm Low Lev for Temperature of sensor in PDM | R/W | s16 | 0.1 C | -400 | 1000 | 10 | -400 | Settings | PRO_MAP
2902 | Alarm High Lev for Humidity of sensor in PDM | R/W | u16 | 1% | 0 | 100 | 1 | 100 | Settings | PRO_MAP
2903 | Alarm Low Lev for Humidity of sensor in PDM | R/W | u16 | 1% | 0 | 100 | 1 | 0 | Settings | PRO_MAP
2904 | Alarm High Lev for Temperature of PT100 in PDM | R/W | s16 | 0.1 C | -1000 | 3000 | * | 3000 | Settings | PRO_MAP
2905 | Alarm Low Lev for Temperature of PT100 in PDM | R/W | s16 | 0.1 C | -1000 | 3000 | * | -1000 | Settings | PRO_MAP
2906 | Alarm High Lev for 420 input in PDM | R/W | u16 | 0.01 mA | 0 | 2000 | * | 2000 | Settings | PRO_MAP
2907 | Alarm Low Lev for 420 input in PDM | R/W | u16 | 0.01 mA | 0 | 2000 | * | 0 | Settings | PRO_MAP
3000 | IP Address1 (Here.x.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 169 | None | ETH_MAP
3001 | IP Address2 (x.Here.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 254 | None | ETH_MAP
3002 | IP Address3 (x.x.Here.x) | R/W | u16 | Unit | 0 | 255 | 1 | 0 | None | ETH_MAP
3003 | IP Address4 (x.x.x.Here) | R/W | u16 | Unit | 0 | 255 | 1 | 10 | None | ETH_MAP
3004 | SUB NET Address1 (Here.x.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 255 | None | ETH_MAP
3005 | SUB NET Address2 (x.Here.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 255 | None | ETH_MAP
3006 | SUB NET Address3 (x.x.Here.x) | R/W | u16 | Unit | 0 | 255 | 1 | 255 | None | ETH_MAP
3007 | SUB NET Address4 (x.x.x.Here) | R/W | u16 | Unit | 0 | 255 | 1 | 0 | None | ETH_MAP
3008 | GATE WAY Address1 (Here.x.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 169 | None | ETH_MAP
3009 | GATE WAY Address2 (x.Here.x.x) | R/W | u16 | Unit | 0 | 255 | 1 | 254 | None | ETH_MAP
3010 | GATE WAY Address3 (x.x.Here.x) | R/W | u16 | Unit | 0 | 255 | 1 | 0 | None | ETH_MAP
3011 | GATE WAY Address4 (x.x.x.Here) | R/W | u16 | Unit | 0 | 255 | 1 | 254 | None | ETH_MAP
3012 | MAC Address1 (Here-x-x-x-x-x) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 02 | None | ETH_MAP
3013 | MAC Address2 (x-Here-x-x-x-x) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 00 | None | ETH_MAP
3014 | MAC Address3 (x-x-Here-x-x-x) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 00 | None | ETH_MAP
3015 | MAC Address4 (x-x-x-Here-x-x) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 00 | None | ETH_MAP
3016 | MAC Address5 (x-x-x-x-Here-x) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 00 | None | ETH_MAP
3017 | MAC Address6 (x-x-x-x-x-Here) | R/Wnet | u16 | Unit | 0 | 255 | 1 | 00 | None | ETH_MAP
3100 | ETHERNET - Version Number | R/W | u16 | Word | - | - |  | - | None | ETH_MAP
4200 | Average Voltage THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 평균 전압 전 고조파 왜곡율
4201 | L3-L1 Voltage THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L3-L1 전압 전 고조파 왜곡율
4202 | L1-L2 Voltage THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L1-L2 전압 전 고조파 왜곡율
4203 | L2-L3 Voltage THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | L2-L3 전압 전 고조파 왜곡율
4204 | Max Voltage THD | Read Only | u16 | 0.01% | - | - |  | - | None | METER_MAP |  | 최대 전압 전고조파왜곡율
4210 | L3-L1 Fundamental Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L3-L1 기본 주파수 전압 : MSB
4211 | L3-L1 Fundamental Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L3-L1 기본 주파수 전압 : LSB
4212 | L1-L2 Fundamental Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L1-L2 기본 주파수 전압 : MSB
4213 | L1-L2 Fundamental Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L1-L2 기본 주파수 전압 : LSB
4214 | L2-L3 Fundamental Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L2-L3 기본 주파수 전압 : MSB
4215 | L2-L3 Fundamental Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L2-L3 기본 주파수 전압 : LSB
4220 | L3-L1 Total Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L3-L1 전체 전압 : MSB
4221 | L3-L1 Total Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L3-L1 전체 전압 : LSB
4222 | L1-L2 Total Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L1-L2 전체 전압 : MSB
4223 | L1-L2 Total Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L1-L2 전체 전압 : LSB
4224 | L2-L3 Total Voltage : MSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L2-L3 전체 전압 : MSB
4225 | L2-L3 Total Voltage : LSB | Read Only | u16 | 0.001 V | - | - |  | - | None | METER_MAP |  | L2-L3 전체 전압 : LSB
5000 | Filter Setting | R/Wnet | u16 | Bit Field | - | - |  | 0x0000 | Settings | MOTOR_MAP
7000 | Spectral Waveform Capture Status | Read Only | u16 | Unit | - | - |  | 0 | None | DIO_MAP | PREMIUM Reference Only
7001 | Spectral Waveform Capture Control | R/W | u16 | Bit Field | - | - |  | 0x0000 | None | DIO_MAP | PREMIUM Reference Only
7002 | Spectral Waveform Capture Config | R/W | u16 | Unit | - | - |  | 0 | None | DIO_MAP | PREMIUM Reference Only
7003 | Spectral Waveform Capture Data Type | R/W | u16 | Unit | 0 | 2 |  | 0 | None | DIO_MAP | PREMIUM Reference Only
7004 | Spectral Waveform Capture Data Index | R/W | u16 | Unit | 0 | 999 |  | 0 | None | DIO_MAP | PREMIUM Reference Only
7005-7084 | Spectral Waveform Capture Data Address | Read Only | u16 | Word | - | - |  | - | None | DIO_MAP | PREMIUM Reference Only
Note on L7: Description: This register shows CPU usage.
Note on L8: Description: ADC value of Current L1 MSB
Note on L9: Description: ADC value of Current L1 LSB
Note on L10: Description: ADC value of Current L2 MSB
Note on L11: Description: ADC value of Current L2 LSB
Note on L12: Description: ADC value of Current L3 MSB
Note on L13: Description: ADC value of Current L3 LSB
Note on L14: Description: ADC value of Current L123 MSB
Note on L15: Description: ADC value of Current L123 LSB
Note on L16: Description: ADC value of Built-in ZCT MSB
Note on L17: Description: ADC value of Built-in ZCT LSB
Note on L18: Description: ADC value of External ZCT MSB
Note on L19: Description: ADC value of External ZCT LSB
Note on L20: Description: ADC value of Voltage L1 MSB
Note on L21: Description: ADC value of Voltage L1 LSB
Note on L22: Description: ADC value of Voltage L2 MSB
Note on L23: Description: ADC value of Voltage L2 LSB
Note on L24: Description: ADC value of Voltage L3 MSB
Note on L25: Description: ADC value of Voltage L3 LSB
Note on L26: Description: ADC value of Internal Reference Voltage
Note on L27: Description: ADC value of Analog Voltage Supply
Note on L28: Description: ADC value of External Battery Voltage Supply
Note on L29: Description: ADC value of Power Monitoring
Note on L30: Description: ADC value of Insulation Resistance Monitoring
Note on L31: Description: ADC value of CPU Junction Temperature
Note on L32: Description: This register has reference number of product. Refer to "Referece code in war-room" for detail information
Note on L38: Desription: The calculation of this value is: Load CT Ratio = Load CT Primary / (Load CT Secondary x Ext Passes) (Reg628) / (Reg629 x Reg630)
Note on E40: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F40: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on G40: Description: Builtin CT: 100A x CT ratio(Reg94-95) / 100 External CT: Secondary 5 6A x CT ratio(Reg94-95) / 100 Secondary 1 1.2A x CT ratio(Reg94-95) / 100
Note on H40: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on L41: Description: The auto-reset counter is incremented at each successful auto-reset of any fault. Auto-reset attempts, which failed, have no effect on this counter. When the maximum number (65535) is reached, the counter is no longer incremented.
Note on H44: Description: Step for MC Counter Set Write value <100 : Step is 10 100 <= Write value < 1000 : Step is 50 1000 <= Write value <= 9900 : Step is100
Note on L45: Description: 0 : MC Counter by both Current and MC Status 1 : MC Counter by Current
Note on L46: Description: MC Count Display max value : 99999
Note on E48: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F48: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on H48: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on I48: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on L48: Description: Matched to ON_LEVEL. UC is dominant compared to OC about MAX value.
Note on L50: Description: Below design is not rational. MC Counter Recognition Level by Active Power. Instead, just show by Reg671.10 bit field register
Note on E57: Description: This register has the threshold for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg557 FLT_UPPER_VOLTAGE Reg571 FLT_LONG_START Reg624 FLT_JAM Reg618 FLT_CURRENT_IMBALANCE Reg615 FLT_VOLTAGE_IMBALANCE Reg568 FLT_LOWER_CURRENT Reg621 FLT_LOWER_VOLTAGE Reg574 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL Reg563 FLT_GRND_RESIDUAL Reg611 FLT_SHORT Reg605 FLT_LOWER_COS_PHI Reg591 FLT_LOWER_COS_PHI Reg594 FLT_LOWER_POWER Reg588 FLT_UPPER_POWER Reg585 Others 0
Note on E58: Description: This register has the duration for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_CURRENT_PHASE_LOSS Reg555 FLT_VOLTAGE_PHASE_LOSS Reg576 FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg556 FLT_UPPER_VOLTAGE Reg570 FLT_LONG_START Reg623 FLT_JAM Reg617 FLT_CURRENT_IMBALANCE Reg614 FLT_VOLTAGE_IMBALANCE Reg566 FLT_LOWER_CURRENT Reg620 FLT_LOWER_VOLTAGE Reg573 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL FLT_GRND_RESIDUAL Reg562 FLT_SHORT Reg607 FLT_LOWER_COS_PHI Reg590 FLT_LOWER_COS_PHI Reg593 FLT_LOWER_POWER Reg587 FLT_UPPER_POWER Reg584 Others 0
Note on E71: Description: This register has the threshold for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg557 FLT_UPPER_VOLTAGE Reg571 FLT_LONG_START Reg624 FLT_JAM Reg618 FLT_CURRENT_IMBALANCE Reg615 FLT_VOLTAGE_IMBALANCE Reg568 FLT_LOWER_CURRENT Reg621 FLT_LOWER_VOLTAGE Reg574 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL Reg563 FLT_GRND_RESIDUAL Reg611 FLT_SHORT Reg605 FLT_LOWER_COS_PHI Reg591 FLT_LOWER_COS_PHI Reg594 FLT_LOWER_POWER Reg588 FLT_UPPER_POWER Reg585 Others 0
Note on E72: Description: This register has the duration for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_CURRENT_PHASE_LOSS Reg555 FLT_VOLTAGE_PHASE_LOSS Reg576 FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg556 FLT_UPPER_VOLTAGE Reg570 FLT_LONG_START Reg623 FLT_JAM Reg617 FLT_CURRENT_IMBALANCE Reg614 FLT_VOLTAGE_IMBALANCE Reg566 FLT_LOWER_CURRENT Reg620 FLT_LOWER_VOLTAGE Reg573 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL FLT_GRND_RESIDUAL Reg562 FLT_SHORT Reg607 FLT_LOWER_COS_PHI Reg590 FLT_LOWER_COS_PHI Reg593 FLT_LOWER_POWER Reg587 FLT_UPPER_POWER Reg584 Others 0
Note on E85: Description: This register has the threshold for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg557 FLT_UPPER_VOLTAGE Reg571 FLT_LONG_START Reg624 FLT_JAM Reg618 FLT_CURRENT_IMBALANCE Reg615 FLT_VOLTAGE_IMBALANCE Reg568 FLT_LOWER_CURRENT Reg621 FLT_LOWER_VOLTAGE Reg574 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL Reg563 FLT_GRND_RESIDUAL Reg611 FLT_SHORT Reg605 FLT_LOWER_COS_PHI Reg591 FLT_LOWER_COS_PHI Reg594 FLT_LOWER_POWER Reg588 FLT_UPPER_POWER Reg585 Others 0
Note on E86: Description: This register has the duration for each fault as follows. i.e. This register value should be read differently in accordance with fault code. FLT_CURRENT_PHASE_LOSS Reg555 FLT_VOLTAGE_PHASE_LOSS Reg576 FLT_INVERSE FLT_THERMAL FLT_UPPER_CURRENT FLT_SELFTEST Reg556 FLT_UPPER_VOLTAGE Reg570 FLT_LONG_START Reg623 FLT_JAM Reg617 FLT_CURRENT_IMBALANCE Reg614 FLT_VOLTAGE_IMBALANCE Reg566 FLT_LOWER_CURRENT Reg620 FLT_LOWER_VOLTAGE Reg573 FLT_INT_GRND_CURRENT FLT_EXT_GRND_CURRENT FLT_GRND_CURRENT_FULL FLT_GRND_RESIDUAL Reg562 FLT_SHORT Reg607 FLT_LOWER_COS_PHI Reg590 FLT_LOWER_COS_PHI Reg593 FLT_LOWER_POWER Reg587 FLT_UPPER_POWER Reg584 Others 0
Note on L121: Description: Refer to FaultCode sheet
Note on L122: Description: Bit definition is same as Reg631 Bit0 : Short-circuit fault Bit1 : Stall(Long Start) fault Bit2 : Ground fault Bit3 : Thermal/Overload fault Bit4: External fault Bit5 : Jam fault Bit6 : Current imbalance fault Bit7 : Under current fault Bit8 : Current Phase Loss fault Bit9 : Current Phase Reversal fault Bit10 : Test Trip fault Bit11 : Internal fault Bit12 : PDM Communication loss fault Bit13 : Ethernet Network Communication loss fault Bit14 : Ground fault (Residual Current) Bit15 : Serial Network Communication loss fault
Note on L123: Description: Bit definition is same as Reg632 Bit0-6: Reserved Bit7 : VoltagePhaseImbalanceFault Bit8 : VoltagePhaseLossFault Bit9 : VoltagePhaseReversalFault Bit10 : UnderVoltageFault Bit11 : OverVoltageFault Bit12 : UnderPowerFault Bit13 : OverPowerFault Bit14 : UnderPowerFactorFault Bit15 : OverPowerFactorFault
Note on L124: Description: Bit definition is same as Reg633 Bit0: Logic Control Diagnosis Fault Bit1-15: Reserved
Note on L125: Description: Bit definition for Reg455 Bit0: System Ready (not motor tirp status as normal state) Normal State:1, Motor trip: 0 Bit1: System On (motor starting or running) Motor starting or running : 1, Motor stop 0 Bit2: System Fault (motor trip status) Motor trip: 1, otherwise 0 Bit3: Reserved Bit4: System Tripped (stopped motor trip status) Stpped Motor trip: 1, otherwise 0 Bit5: Reserved Bit6: Reserved Bit7: Motor Running(the same as Reg455.1) Motor starting or running : 1, Motor stop 0 Bit8: When Reg602.12 is 0, Insulation Resistance Level State, Not Good : 1, Good : 0 When Reg602.12 is 1, Status Resistance Input State, Closed:1, Open: 0 Bit9: Reserved Bit10: Motor Status by MC Count recognition)\ Motor Running: 1, Stop : 0 Bit11-14: Reserved Bit15: Motor starting (during D-time) Motor starting(during D-time): 1, otherwise 0
Note on L126: Description: Bit Description for Reg456 Bit0 - 3: Reserved Bit4 : Rapid Cycle Lockout Bit5-6: Reserved Bit7: Ethernet Network Port Comm Loss Bit8: Serial Network Port Comm Loss Bit9: Motor Transition Time Lockout
Note on L127: Description: Bit definition for Reg457 Bit0: Digital Input 1 Bit1-2: Reserved Bit3: Digital Input 4 Bit4: Digital Input 5 Bit5: Reserved Bit6: Reset button Bit7~15: Reserved
Note on L128: Description: Bit definition for Reg458 Bit0 : LO-1 (97-98 & 95-96 relay) Bit1 : LO-2 (57-58 relay) Bit2 : LO-3 (07-08 relay) Bit4 : LO-4 (O1-CO relay) Bit5 : LO-5 (O2-CO relay) Bit6 : LO-6 (Insulation Resistance Test - Internal relay) Bit Value : 0 (closed) / 1 (opened)
Note on L129: Description: 2 bit LED status 00: Off 01: On 10: Low blink 11: Fast blink Bit definition for Reg459 Bit0-1 : Power Bit2-3 : Fault Bit4-5 : Network (TCP/IP) Bit6-7 : Network (Serial) Bit8-9 : Digital Input 1 Bit10-11 : Digital Input 4 Bit12-13 : Digital Input 5 Bit14-15: Reserved
Note on L130: Description: Bit definition is same as Reg631 NA: Not Available Bit0 : Short-circuit warning NA 1 : Stall(Long Start) warning NA 2 : Ground warning NA 3 : Thermal/Overload warning NA 4: External warning NA 5 : Jam warning NA 6 : Current imbalance warning NA 7 : Under current warning 8 : Current Phase Loss warning NA 9 : Current Phase Reversal warning NA 10 : Test Trip warning NA 11 : Internal warning NA 12 : PDM Communication loss warning NA 13 : Ethernet Network communication loss warning NA 14 : Ground warning (Residual Current) NA 15 : Serial Network communication loss warning NA
Note on L131: Description: Bit definition is same as Reg632 NA: Not Available Bit0-6: Reserved Bit7 : Voltage Phase Imbalance Warning Bit8 : Voltage Phase Loss Warning Bit9 : Voltage Phase Reversal Warning Bit10 : Under Voltage Warning Bit11 : Over Voltage Warning Bit12 : Under Power Warning Bit13 : Over Power Warning Bit14 : Under Power Factor Warning Bit15 : Over Power Factor Warning
Note on L133: Description: Max(L1, L2, L3) of %OC
Note on L134: Description: L1 of % Inom
Note on L135: Description: L2 of % Inom
Note on L136: Description: L3 of % Inom
Note on L143: Description: 3 phase: Vavg = (L1-L2 voltage + L2-L3 voltage + L3-L1 voltage) / 3 1 phase: Vavg = L3-L1 voltage VImbalance Vimb = 100 x (Vavg - Vph-ph ) / Vagv Max Vimb = Max (VimbL3-L1, VimbL1-L2, VimbL2-L3)
Note on L145: Description: PF Lagging : 0, PF Leading : 1
Note on L147: Description: 0: Network access no 1: Network access yes
Note on L148: Description: The time while power is OFF is taken into account for thermal update If time is over than 30 minutes, this register reports 65535
Note on L168: Description: 0 : L1 Current Phase 1 : L2 Current Phase 2 : L3 Current Phase
Note on L184: Description: Refer to "config" sheet
Note on H188: Description: Step for Alert threshold for running hour 0-999 : step is 1hr 1000-9990 : step is 10hr
Note on L189: Description: 0 : 220VAC 1 : 110VAC 2 : Special
Note on H194: Description: Step for Current phase loss Fault Duration 50 <= write value < 100 : step is 10 100 <= write value <= 500 : step is 100v
Note on H195: Description: Step for Over current Fault Duration 20 <= write value < 100 : step is 10 100 <= write value <= 12000 : step is 100
Note on E196: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F196: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on G196: Description: Builtin CT: 100Ax CT ratio(Reg94-95) / 100 External CT: Secondary 5 6A x CT ratio(Reg94-95) / 100 Secondary 1 1.2A x CT ratio(Reg94-95) / 100
Note on H196: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on I196: Description: Builtin CT: 5A x CT ratio(Reg94-95) / 100 External CT: Secondary 5 5A x CT ratio(Reg94-95) / 100 Secondary 1 1A x CT ratio(Reg94-95) / 100
Note on L218: ATTENTION: This register value is not clear by RFS. If user set the password, Keep the password safely.
Note on L219: Description: Refer to "config" sheet
Note on L220: Description: Refer to "config" sheet
Note on L221: Description: Refer to "config" sheet
Note on L222: Description: Refer to "config" sheet
Note on H228: Description: Step for JAM Fault Duration 20 <= write value < 100 : step is 10 100 <= write value <= 1000 : step is 100
Note on H229: Description: Step for JAM Fault Threshold write value < 200 : Step = 10 write value >= 200 : Step = 100
Note on H230: Description: Step for Under current Fault Duration 50 <= write value < 100 : step is 10 100 <= write value <= 12000 : step is 100
Note on E231: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F231: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on H231: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on I231: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on H234: Description: Step for CT Primary 800 <= write value : Step is 50 100 <= write value < 800 : Step is 10 10 <= write value < 100 : Step is 5
Note on H235: Description: 1 or 5
Note on H236: Description: 1, 2, 3, 4 or 5
Note on L237: Description: Refer to "config" sheet
Note on L238: Description: Refer to "config" sheet
Note on L239: Description: Refer to "config" sheet
Note on H240: Description: Step for Auto Reset Delay Write value < 1 Second : Step is 0.1 s 1s <= Write value < 1 min : Step is 1 s 1min <= Write value < 20 min : Step is 1 min
Note on H241: Description: Step: value < 10 Second : Step is 0.1 second 10s <= value < 9990s : Step is 1 second
Note on E242: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F242: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on G242: Description: Builtin CT: 100A x CT ratio(Reg94-95) / 100 External CT: Secondary 5 6A x CT ratio(Reg94-95) / 100 Secondary 1 1.2A x CT ratio(Reg94-95) / 100
Note on H242: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on I242: Description: Builtin CT: 5A x CT ratio(Reg94-95) / 100 External CT: Secondary 5 5A x CT ratio(Reg94-95) / 100 Secondary 1 1A x CT ratio(Reg94-95) / 100
Note on L243: Description: 0xSSxx, For example 0x1200 for 12 seconds xx is unused area - By writing this parameter, the user set the current date and time for the controller. - By reading this parameter, the user get the current date and time used by the controller for datation. This value is stored in historical records at each fault. The format is the IEC61131-3 Date and Time format. It can be managed directly as DT variable in Unity Pro. Min value: DT#2020-01-01:00:00:00 Max value: DT#2099-12-31:23:59:59 This Date and Time are stored every 1 seconds.
Note on L244: Description: 0xHHMM, For example 0x1359 for 1:59 PM Refer to Reg655 comment for more information
Note on L245: Description: 0xMMDD, For example 0x0804 for 4th August Refer to Reg655 comment for more information
Note on L246: Description: 0xYYYY, For example 0x2020 for 2020
Note on L248: Description: Metering Pulse constant 100(1pulse=100Wh) 200(1pulse=200Wh) 500(1pulse=500Wh) 1000(1pulse=1000Wh) 5000(1pulse=5000Wh) 9000(1pulse=9000Wh)
Note on L249: Description: Bit description for Reg671 Bit0: System Ready Bit1: System On Bit2: System Fault Bit3-9: Reserved Bit 10: Active Power On If the active power is greater than the set level (Reg136), the bit field state turns on. Bit15: Motor starting
Note on L250: Description: Refer to "config" sheet
Note on L251: Description: 0 : None Function 1 : Logic Function (LI1:RUN, LI4:STOP, LI5:RESET) 2 : Alternative Function (MC Status)
Note on L252: Description: 0 : None Function 1 : Logic Function (LI1:RUN, LI4:STOP, LI5:RESET) 2 : Alternative Function (MC Status)
Note on L253: Description: 0 : None Function 1 : Logic Function (LI1:RUN, LI4:STOP, LI5:RESET) 2 : Alternative Function (MC Status)
Note on L256: Description: 0: None(2 stop bit) 1: Even(1 stop bit) 2: Odd(1 stop bit) 3: None(1 stop bit)
Note on L257: Description: 1200: 1200 bps 2400: 2400 bps 4800: 4800 bps 9600: 9600 bps 19200: 19200 bps 38400: 38400 bps 57600: 57600 bps
Note on L259: Description: Bit definition for Reg700 Bit0-7: Count Up 0 ~ 255 Every 100ms Bit8: Toggle Bit Every 800ms Bit9: Toggle Bit Every 1s Bit10: Toggle Bit Every 5s Bit11: Toggle Bit Every 15s Bit12: Toggle Bit Every 30s Bit13: Toggle Bit Every 60s Bit14: Toggle Bit Every 360s (6mins)
Note on L260: Description: Refer to "config" sheet
Note on L261: Description: Refer to "config" sheet
Note on L270: Description: Bit description for Reg730 Bit0: Auto Test Mode Enable Bit1: Ready (Not Started) Bit2: Delay in Auto Test Mode Bit3; In Running Bit4: Finished Bit5-15: Reserved
Note on L277: Description: Bit Description for Reg1000 (with PDM) Bit0: Escape Bit1: Up Bit2: Down Bit3: Set Bit4-15: Reserved Bit Description for Reg1000 (with OCU) Bit0: Escape Bit1: Up Bit2: Down Bit3: Set Bit4: OM Bit5: Reset Bit6: FWD Bit7: Reserved Bit8: STOP Bit4-15: Reserved
Note on L282: Description: Bit description for Reg1005 Bit0: COMM Bit1: MCC Bit2: AUTO Bit3: LOP Bit4: Run(Red) Bit5: Fault Bit6: Stop(Green) Bit7: Run(Green) Bit8: Stop(Red) Bit9-15: Reserved
Note on L283: Description: This register value will be clear after read Bit Description for Reg31006 Bit0: Switch OCU to NET mode Bit1-15: Reserved
Note on L284: Description: 1 : Display in HMI_DSP_ADD_NONE 2 : Display in HMI_DSP_ADD_TPOW (default) 3 : Display in HMI_DSP_ADD_TE_HU 4 : Display in HMI_DSP_ADD_TPOW_TE_HU
Note on L290: Description: When PDM is connected it is written to the EOCR only for the first time like PDM Version.
Note on L291: Description: 0: New page 1: Old page
Note on L292: Description: Total samples : 200
Note on L293: Description: L1 Current
Note on L294: Description: L2 Current
Note on L295: Description: L3 Current
Note on L296: Description: Ground Current
Note on L297: Description: L1 Voltage
Note on L298: Description: L2 Voltage
Note on L299: Description: L3 Voltage
Note on L301: Description: Refer to "Config sheet" for bit description
Note on L303: Description: Bit description for Reg1270 Bit0: External fault exist bit Bit1~15: Reserved
Note on L304: Description: bit0 : 1 Motor Stop Waveform Mode (Waveform page0: Fault , Waveform page1: Motor Stop) 0 Fault Waveform Mode (default) (page0: Fault , page1: Fault) bit1-15 : Reserved
Note on L344: Description: 0: Automatic Following 1: System Freqeuncy Setting (50Hz or 60Hz)
Note on E369: Description: If CT ratio(Refer to reg94-95) is less than 100, Unit is 10mA, Other's 100mA.
Note on F369: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on G369: Description: Builtin CT: 100A x CT ratio(Reg94-95) / 100 External CT: Secondary 5 6A x CT ratio(Reg94-95) / 100 Secondary 1 1.2A x CT ratio(Reg94-95) / 100
Note on H369: Description: Step for Over current Fault Threshold * When Unit is 100mA 0A <= write value < 10A : Step is 100mA 10A <= write value <1000A : Step is 1A 1000A <= write value : Step is 10A * When Unit is 10mA Step is always 10mA
Note on I369: Description: This min/max/defalut value is for CT none If CT ratio(Reg94-95) is not 100, min/max/default value is chagned min/max/default x CT ratio(Reg94-95) / 100
Note on H380: Description: Step for Alarm level for PT100 2500 < write value : Step is 100 1100 < write value <= 2500 : Step is 10 1000 < write value <= 1100 : Step is 100 -500 < write value <= 1000 : Step is 10 write value <= -500 : Step is 100
Note on H381: Description: Step for Alarm level for PT100 2500 < write value : Step is 100 1100 < write value <= 2500 : Step is 10 1000 < write value <= 1100 : Step is 100 -500 < write value <= 1000 : Step is 10 write value <= -500 : Step is 100
Note on H382: Description: Step for Alarm level for 420 input 400 < write value <= 2000 : Step is 100 0 <= write value <= 400 : Step is 400
Note on H383: Description: Step for Alarm level for 420 input 400 < write value <= 2000 : Step is 100 0 <= write value <= 400 : Step is 400
Note on L420: Description: Bit description for Reg5000 bit0: Low pass filter for ground current bit1-15 : Reserved
Note on L421: Description: Bit description for Reg7000 Bit0: 0 No sampling for transmission 1 Under the sampling Bit1: 0 Not data ready (not buffer full) 1 Data ready (buffer full)
Note on L422: Description: Bit description for Reg7001 Bit0: 0 No operation 1 Continue the sampling Bit1: 0 No operation 1 Capture the spectral waveform (Stopping the sample) Bit2-14: Reserved Bit15: 0: No operation 1: Clear the spectral waveform
Note on L424: Description: 0: L1 Current 1: L2 Current 2: L3 Current
Note on L425: Description: Total samples : 80000 Data channels 80 x Index 1000 = 80000

## FaultCode
Fault Code List
# | Name | HMI Display | Meaning | Enable Register | Fault Threshold | Fault Duration
0 | FLT_NONE | noFLt | 발생 없음 (초기 상태) | - | - | -
1 | FLT_CT_REVERSE | N/A | N/A | - | - | -
2 | FLT_CURRENT_PHASE_REVERSAL | --IrP- | 전류 역상 동작 | Reg631.9 | - | -
3 | FLT_CURRENT_PHASE_LOSS | PL | 전류 결상 동작 | Reg631.8 | - | Reg555
4 | FLT_EEPROM | EP | 자가진단(본체 내부 메모리 저장 기능)에 문제 발생 | Always | - | -
5 | FLT_PDM_COMM | PdLos | 본체와 PDM Display 장치와의 통신 두절 발생 | Reg631.12 | - | -
6 | FLT_INVERSE | oc | 과전류 반한시 동작 | Reg602.6-7 | Reg557 | Reg556
7 | FLT_THERMAL | oc | 과전류 열적반한시 동작 | Reg602.6-7 | Reg557 | Reg556
8 | FLT_UPPER_CURRENT | oc | 과전류 정한시 동작 | Reg602.6-7 | Reg557 | Reg556
9 | FLT_LONG_START | Sc | 기동중 구속 동작 | Reg631.1 | Reg624 | Reg623
10 | FLT_JAM | Ja | 운전중 구속 동작 | Reg631.5 | Reg618 | Reg617
11 | FLT_CURRENT_IMBALANCE | Ub | 전류 불평형 동작 | Reg631.6 | Reg615 | Reg614
12 | FLT_LOWER_CURRENT | uc | 부족 전류 동작 | Reg631.7 | Reg621 | Reg620
13 | FLT_SHORT | SH | 단락 전류 동작 | Reg631.0 | Reg605 | Reg607
14 | FLT_INT_GRND_CURRENT | Ec | 지락 전류 동작 | Reg631.2 | Reg563 | Reg562
15 | FLT_EXT_GRND_CURRENT | Ec | 지락 전류 동작 | Reg631.2 | Reg563 | Reg562
16 | FLT_NETWORK_COMM_RTU | ntLos | 본체와 외부 Serial Network 간 통신 두절 발생 | Reg631.15 | - | Reg693
17 | FLT_STUCK_BU | btn | 자가진단(본체 버튼 입력 기능)에 문제 발생 | Always | - | -
18 | FLT_RANGE_ERROR | ItErr | 자가진단(본체 내부오류, RTC Chip 기능 등) 문제 발생 | Always | - | -
19 | FLT_SELFTEST | -End- | Self Test 동작 | Always | - | -
20 | FLT_RUN | runEr | 운전(Run) 명령이 실행되었으나 전류감지가 안되는 문제 발생 | - | - | -
21 | FLT_RUN_CHECK | cbrun | 운전 도중에 정지명령이 없이 모터가 정지하는 문제 발생 | - | - | -
22 | FLT_STOP | StpEr | 정지 (Stop) 명령이 실행되었으나 전류가 계속 감지되는 문제 발생 | - | - | -
23 | FLT_STOP_CHECK | cbStP | 정지 중에 운전명령이 없이 모터가 운전되는 문제 발생 | - | - | -
24 | FLT_EXTERNAL | EtFLt | 통신 Reg1270.0 비트필드에 트리거 명령으로 Trip 동작 | Always | - | -
25 | FLT_UPPER_VOLTAGE | oU | 과전압 동작 | Reg632.11 | Reg571 | Reg570
26 | FLT_LOWER_VOLTAGE | uU | 부족전압 동작 | Reg632.10 | Reg574 | Reg573
27 | FLT_VOLTAGE_IMBALANCE | Ub | 전압 불평형 동작 | Reg632.7 | Reg568 | Reg566
28 | FLT_VOLTAGE_PHASE_LOSS | UL | 전압 결상 동작 | Reg632.8 |  | Reg576
29 | FLT_VOLTAGE_PHASE_REVERSAL | --UrP- | 전압 역상 동작 | Reg632.9
30 | FLT_UPPER_COS_PHI | oF | 과역률 동작 | Reg632.15 | Reg594 | Reg593
31 | FLT_LOWER_COS_PH | uF | 저역률 동작 | Reg632.14 | Reg591 | Reg590
32 | FLT_UPPER_POWER | oP | 과전력(유효전력, W) 동작 | Reg632.13 | Reg585 | Reg584
33 | FLT_LOWER_POWER | uP | 저전력(유효전력, W) 동작 | Reg632.12 | Reg588 | Reg587
34 | FLT_GRND_CURRENT_RESIDUAL | rc | 잔류 전류 동작 | Reg631.14 | Reg611 | Reg562
35 | FLT_GRND_CURRENT_FULL | EcFul | 지락 전류(본체 내부/외부 ZCT 에 의한) 동작 | Reg631.2 | Reg563 | Reg562
36 | FLT_NETWORK_COMM_TCP | ntLos | 본체와 외부 Ethernet Network 간 통신 두절 발생