# How to Operate this Sample Program

Contents

How to Operate this Sample Program	1

When are these FBs needed?	1

This sample includes	1

Connections	2

Setup	2

FB Documentation	2

How to Use these FBs in your Programs	4

## When are these FBs needed?

- Normally any variable (except I/O variables) may be selected as Retained as shown in red below:

This causes the RTU to save the current value of the variable even when the RTU is power cycled. This works well, expect when significant changes are made to the program where the variable is used. After a change like this, the retained variables are typically zeroed when the newly loaded program is first executed.

- To retain the value under all conditions, the best solution is to save the value of the variable in a DNP point. The FBs provided in this sample offer a counter, a timer, and a combination of both timer & counter that retain their values over program downloads and power cycles. See the end of this document for a detailed description of each FB.

## This sample includes

- SCADAPack Workbench project – Complete example showing how to use all three FBs.

- E Configuration – Example for sp334E and sp350E.

- Just the FBs – After trying out the complete project example, there is an export of just the FBs for you to import into your existing Workbench projects.

## Connections

- Connect your PC to your SCADAPack E RTU using an Ethernet connection.

- Connect USB cable from PC to RTU.

## Setup

- Run the E Configurator and open the configuration file included in this sample for a 334E or a 350E.

- Edit the TCP/IP folder and set the RTU’s IP Address to an address compatible with your PC’s IP address. (e.g. PC = 192.168.2.100 and RTU = 192.168.2.10)

- Write the configuration over USB to RTU.

- Run SCADAPack Workbench

- From the Start Page, create a New Project of type SCADAPack 300E TCP/IP for an Ethernet connection to your PC.

- Give the project a name and select OK.

- Right-click the Project name shown in the Solution Explorer and select Import > Import Exchange File.

- Browse to the workbench file, RetainedCounterTimer.SCADAPack300E.Res1PumpControl_v01.7z, included in this sample and import. Select Cancel when done to exit the Import dialog.

- Open the Deployment page:

For Ethernet connections, select the ‘T’ connection graphic to open the LAN connection properties. Enter the IP Address of your RTU.

- Select Build > Clean Solution

- Select Build > Build Solution

- Download Solution to the RTU.

## FB Documentation

This sample uses 4 digital inputs to demonstrate the three FB types described below. An I/O simulator with toggle switches such as the 5691 (P/N: TBUX297450) allows you to start and stop timers and count boolean input changes. You may also use the Debugger Lock feature to lock these digital input variables and write their state directly.

dnpCounter FB

- Toggle the addOne input to add one to the counter.

- Toggle the reset input to reset the counter to zero.

- The counterValue output must connect to a DINT Output Variable so that the counter value is retained in the DNP database.

- The constant connected to the counterPoint input is found in the folder tree under DataTypes > Defined Words. These are constants that get defined only after the Output variables have been attached to their I/O Devices and a Project Build is been done at least once. These constants are automatically set to the point location on the I/O Device where the Output variable is placed.

dnpTimer FB

- Set the timerOn input to TRUE to advance the timer; set to FALSE to stop the timer.

- Toggle the reset input to reset the timer to zero.

- The timerHrs output provides the timer value in hours as a floating point. This output must connect to a REAL Output Variable so that the timer value is retained in the DNP database.

- The timer is also provided in the format of a TIME variable from the timerVar output. (Note that TIME variables roll over after ~49 days, whereas the timerHrs output is always retained.)

- The constant connected to the timerPoint input is found in the folder tree under DataTypes > Defined Words. These are constants that get defined only after the Output variables have been attached to their I/O Devices and a Project Build is been done at least once. These constants are automatically set to the point location on the I/O Device where the Output variable is placed.

dnpTimerCntr FB

This function block is ideal for recording a motor or pump run time and starts counter. While a DNP3 SCADA host can also track this data, sometimes it is needed in the RTU as a trigger for controlling pump alternation. (Note that these two values may also be determined by the host using a DNP3 historical trace for the pump or motor.)

- Set the timerOn input to TRUE to advance the timer; set to FALSE to stop the timer. Each time the timerOn input changes from FALSE to TRUE, the counterStarts output is incremented.

- Toggle the reset input to reset the timer and the counter both to zero.

- The timerHrs output provides the timer value in hours as a floating point. This output must connect to a REAL Output Variable so that the timer value is retained in the DNP database.

- The timer is also provided in the format of a TIME variable from the timerVar output. (Note that TIME variables roll over after ~49 days, whereas the timerHrs output is always retained.)

- The counterStarts output provides the count for every time the timer is restarted from stopped.

- The constants connected to the timerPoint input the counterPoint input are found in the folder tree under DataTypes > Defined Words. These are constants that get defined only after the Output variables have been attached to their I/O Devices and a Project Build is been done at least once. These constants are automatically set to the point location on the I/O Device where the Output variable is placed.

## How to Use these FBs in your Programs

This example shows how to use the dnpCounter FB in a FBD program.

- Import the dnpCounter FB by right-clicking the resource where you want to add the FB and select Import Exchange File as shown below:

- Select the FB exchange file (RetainedCounterTimer.SCADAPack300E.Res1PumpControl.dnpCounter.7z) included with this sample and import. The FB will import into your project folder Lib > Function Blocks.

- Insert the FB into your program similar to the example below. Leave the counterPoint input unconnected for now.

- The counterValue output must be a DINT Output Variable, such as counter1 in the example above.

- Connect your DINT Output Variable to an I/O Device so that it gets written to the DNP3 database as shown below:

- Build the solution (even if there are still errors) in order to generate a constant that will equal the DNP point where your Output Variable (e.g. counter1) is connected. You will find the constant associated with your output variable with the prefix “POINT_” under the Data Types > Defined Words as shown below:

- Use this constant as your counterPoint input as shown in the FB below. This will tell the dnpCounter FB from what point to retrieve the counter’s retained value whenever your program restarts.

The constant’s value is maintained automatically for you, should you need to move the output variable to a different point on the I/O device.