# How to Operate this Sample Program

### This sample includes:

- SCADAPack Workbench project – writes data to a peer DNP3 device whenever an Analog Input changes by 5%.

- E Configuration – Two configurations are provided: one for each peer. DNP3 address 0 runs the Workbench project and writes to the peer with DNP3 address 10.  These configurations are the default configuration with additional points for peer communication data. See the Point Browser page to view the points involved. Example configurations are provided for two peers both using 334E RTUs:

  - For an Ethernet connection to your PC, you will need to enable the “ISaGRAF/TCP” service and assign an IP address to your RTU on the TCP/IP page in the E Configurator.

  - For a Serial connection to your PC, you will need to enable the ISaGRAF protocol on the RTU com port you connect to.

### Connections:

- Connect your PC to your SCADAPack E RTUs using your choice of an Ethernet connection or serial connection.

- Connect a null modem serial cable between Com2 on both RTUs. (Note that Com2 is configured for DNP3 protocol on both RTUs.)

- Connect USB cable from PC to RTU.

### Setup:

- Run the E Configurator and open the configuration file included in this sample for each RTU.

  - Write the configuration over USB to each RTU.

- Run SCADAPack Workbench

  - From the Start Page, create a New Project of type SCADAPack 300E TCP/IP for an Ethernet connection to your PC, or SCADAPack 300E Serial for a serial connection. (For the SCADAPack ES, select the desired connection type.)

  - Give the project a name and select OK.

  - Expand the project folder shown in the Solution Explorer until Resource1 and Resource2 are visible.

  - Delete both Resource1 and Resource2. The sample resource will be imported to replace these.

  - Right-click the Project name shown in the Solution Explorer and select Import > Import Exchange File.

  - Browse to the workbench file, <name>.7z, included in this sample and import. Select Cancel when done to exit the Import dialog.

  - Select Build > Clean Solution

  - Select Build > Build Solution

  - Open the Deployment page:

    - For Ethernet connections, select the ‘T’ connection graphic to open the LAN connection properties. Enter the IP Address of your RTU.

    - For Serial connections, select the serial pipe graphic to open the serial connection properties. Under Port enter the serial port for your PC.

  - Download Solution to the RTU that was loaded with the Peer address 0 configuration.

### Demonstration:

The folder Program Explanation included in this sample explains the code sections in detail so that they can be modified to suit your application.

- This sample sends only write commands to a peer at address 10. The write is sent only when one of the analog points changes by 5% or more. There is also a default write every 30 secs.

- This sample is more efficient because it only sends commands when the value changes. It also avoids the need for one peer to read values from another. Instead the peer that is the source of data writes to the other peer only when the data changes.

- Only one point is checked for changes. If more points need to be checked, this code section can be copied for that point.