## Revisions
EM4900 Series Modbus Pointmap and BACnet Objects
Rev History
Rev. A | 2017-06-01 | Initial

## General
LEGEND
R/W: | R = Read-Only
R/W = Read from float or integer format, Write to integer format only
W = Write-Only
NV: | NV = Value is stored in non-volatile memory
V = Value is volatile
SQD ID 1517x: | Y = Parameter is valid for this ID
N = Parameter is invalid for this ID
Scale Reg: | V = Voltage
W = Power
E = Energy
I = Current
<val> = scale is fixed at value shown. If no value shown, it is assumed to be 0.
Modbus Addresses
There are 2 Modbus addresses associated with the EM4900 Configuration - one address for each set of 14 meters
The primary Modbus address is set with the main PCB DIPswitches; The secondary address is always the primary addess + 1.
There are additional Modbus addresses assigned for each configured meter; see Common tab Modbus Address Per Meter Offset
The Common Map is repeated in it's entirety for both configuration addresses.
The Logical Map is repeated in it's entirety for each Modbus address assigned for each configured meter.
Supported Commands
Read Holding Register (03h)
Preset Single Register (06h)
Preset Multiple Registers (10h)
Report Slave ID (11h)
This will include the following info in the "Additional Data" area:
When Modbus Address Per Meter is disabled:
"Schneider Electric Branch Circuit Monitor Model EM49xxx, S/N=0x12345678, Location="<location string>"
"Shcneider Electric Model EM49xxx Branch Circuit Monitor, S/N=0x12345678, Location="<location string>""
When Modbus Address Per Meter is enabled, the two base Modbus addresses will respond as above, all other Modbus addresses assigned to circuits will respond with the following:
"Shcneider Electirc EM49xxx, Logical Meter xx of Panel x, S/N=0x12345678, Location="<location string>""
Report Device ID (2Bh)
Scattered Read (64h)
Integer vs. Floating Point Registers
Integer format registers represent the data as 16 bit signed integer values. Float format registers represent the same data as 32-bit floating point values.
Floats
All floating point variables are read-only.
Floating point registers are packed as follows:
Float | MSB | BYTE3 | BYTE2 | LSB
Modbus MSW | MSB | LSB
Modbus LSW |  |  | MSB | LSB
Example:
For a floating point value of 3.14159, the encoded 32-bit float value is 0x40490FD0.
Modbus MSW = 0x4049
Modbus LSW = 0x0FD0
Integers
Integer format registers must be used in conjunction with their associated Scale registers.
The Scale Registers represent the exponent of the associated values and are used in conjunction with the integer registers to create the
final floating-point results.
Example:
integer register = 27
scale register = -2
final result = 27 * 10^(-2) = 0.27
Note: If a Scale register is not listed for a parameter, it is assumed to be 0.
32-bit integer values, such as KWH, are packed as follows:
32-bit integer | MSB | BYTE3 | BYTE2 | LSB
Modbus MSW | MSB | LSB
Modbus LSW |  |  | MSB | LSB
Example:
For a 32-bit value of 0x12345678.
Modbus MSW = 0x1234
Modbus LSW = 0x5678
Note that the Scale register for Energy (E) is applied only to the final 32-bit result.
For the Current Scales (I), Power Scales (W) and Energy Scales (E) for 1 phase, 2 phase and/or 3 phase Modbus Point Maps,
make sure you are using the correct Scale value
Example:
integer register #1336 (Current Meter 1) = 10
scale register #1000 = -1
final result = 10 * 10^(-1) = 1.0
Model Differences
Invalid channels report the following values:
Integer registers: 0x8000 (32768)
Float registers: 0x7FC00000 (NaN)
| Section | #Registers
| Common | 218
| Logical Map by Meter | Latching Alarm Counters - Phase 3
| TOTAL | 218
Below maps the Device ID to Model Series:
15172 = Model A, current and power on all channels plus voltage
15172 = Model E, current and power on all channels plus voltage with Ethernet Gateway in Metal Case (pointmap is identical to Model A)

## Common
[8 empty] | Modbus |  |  |  |  | BACnet
Channel | Model (A,E) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Description | Object Name | Object ID | Units | COV Increment | BACnet Description | Range | Default
Manufacturer Info
| E,A | R | NV | 1 |  |  |  | Serial Number MSW | Serial Number MSW | AI51 | No-Units | 1 | Serial Number MSW
| E,A | R | NV | 2 |  |  |  | Serial Number LSW | Serial Number LSW | AI52 | No-Units | 1 | Serial Number LSW
| E,A | R | NV | 3 |  |  |  | Firmware Revision RS | Firmware Revision RS | AI53 | No-Units | 1 | Firmware Revision RS
| E,A | R | NV | 4 |  |  |  | Firmware Revision OS | Firmware Revision OS | AI54 | No-Units | 1 | Firmware Revision OS
| E,A | R | NV | 5 |  |  |  | Device ID: | Device ID: | AI55 | No-Units | 1 | 15170=C; 15171=B; 15172=A
15175 = Logical Meter
15172 = Configuration Panel
General User Setup
Logical Meter Assignment will be cleared if Configuration Register is Changed, set Configuration first
| E,A | R/W | NV | 6 |  |  |  | Configuration (bit 0 is LSB): | Configuration (bit 0 is LSB): | AV1 | No-Units | 1 | Configuration (bit 0 is LSB): |  | 2
Value 2 = register should not be changed, leave at default 2
| E,A | R/W | NV | 7 |  |  |  | Location String | [6 empty] | "Panel #<NUM>"
|  |  |  | through |  |  |  | These 64 registers provide for up to 128 packed ASCII text
|  |  |  | 70 |  |  |  | characters (with terminator)
It is also used in the Report_ID response
Lowest numbered register holds the 1st 2 characters of the string
Encoding is 2nd character in MSB, 1st in LSB
Example for "PDU#3":
Reg 7: 0x4450 (DP)
Reg 8: 0x2355 (#U)
Reg 9: 0x0033 (<term>3)
All other Regs: N/A
Demand Setup
Setup for Present KW Demand, Max KW Demand, Present Current Demand, Max Current Demand
All | E,A | R/W | NV | 71 |  |  |  | Number of Sub-Intervals per Demand Interval | # of Sub-Intervals per Demand Int. | AV2 | No-Units | 1 | Number of Sub-Intervals per Interval | 1-6 | 1
Sets the number of sub-intervals that make a single demand interval.
For block demand, set this to 1.
All | E,A | R/W | NV | 72 |  |  |  | Sub-Interval Length in seconds. For sync-to-comms, set this to 0. | Sub-Interval Length in seconds. | AV3 | No-Units | 1 | Sub-Interval Length in seconds. | 0, 10-32767 | 900 (15minutes)
Alarm Timers (seconds)
These timers control entry into a latching alarm state. A return to a non-alarm state is instantaneous.
All channels use the same global timers.
Latching Alarm On Time applies to all Latching Alarms.
The paraMeter measurement rate is expected to be around 2.5 secs, which will limit the effective resolution of these timers.
All | E,A | R/W | NV | 165 |  |  |  | High-High Latching Alarm Time Delay | High-High Latching Alarm Time Delay | AV96 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | E,A | R/W | NV | 166 |  |  |  | High Latching Alarm Time Delay | High Latching Alarm Time Delay | AV97 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | E,A | R/W | NV | 167 |  |  |  | Low Latching Alarm Time Delay | Low Latching Alarm Time Delay | AV98 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | E,A | R/W | NV | 168 |  |  |  | Low-Low Latching Alarm Time Delay | Low-Low Latching Alarm Time Delay | AV99 | Seconds | 1 | Alarm event duration threshold | 0-32767 | 10
All | E,A | R/W | NV | 169 |  |  |  | Latching Alarm ON Time (when current is above Low-Low | Latching Alarm ON Time | AV100 | Seconds | 1 | From initial current to alarms enabled | 0-32767 | 10
alarm & ON Time elapses then ON state is declared for
all latching alarms, ON State enables Alarm Time Delays)
All | E,A | R/W | NV | 170 |  |  |  | Latching Alarms time until OFF state declared (current is below | Latching Alarms time until OFF state | AV101 | Seconds | 1 | time until OFF state declared | 0-32767 | 30
Low-Low alarm and a ON state was declared)
Alarm Thresholds
All values are expressed as %breaker-size.
All channels use these same global values.
An entry of 0% for any threshold disables that alarm for all channels.
All Thresholds are scaled by -1 to increase the precision by 1 decimal point
Hysteresis only applies to Non-Latching Alarms
All | E,A | R/W | NV | 171 |  |  | -1 | High-High Latching Alarm Threshold | High-High Latching Alarm Threshold | AV102 | Percent | 1 | % of breaker size | 0-1000 | 700
All | E,A | R/W | NV | 172 |  |  | -1 | High Alarm Latching Alarm Threshold | High Alarm Latching Alarm Threshold | AV103 | Percent | 1 | % of breaker size | 0-1000 | 600
All | E,A | R/W | NV | 173 |  |  | -1 | Low Alarm Latching Alarm Threshold | Low Alarm Latching Alarm Threshold | AV104 | Percent | 1 | % of breaker size | 0-1000 | 75
All | E,A | R/W | NV | 174 |  |  | -1 | Low Low Latching Alarm Threshold | Low Low Latching Alarm Threshold | AV105 | Percent | 1 | % of breaker size | 0-1000 | 25
All | E,A | R/W | NV | 175 |  |  | -1 | Non-Latching High Threshold | Non-Latching High Threshold | AV106 | Percent | 1 | % of breaker size | 0-1000 | 600
All | E,A | R/W | NV | 176 |  |  | -1 | Non-Latching Low Threshold | Non-Latching Low Threshold | AV107 | Percent | 1 | % of breaker size | 0-1000 | 50
All | E,A | R/W | NV | 177 |  |  | -1 | Non-Latching Hysteresis (0-100% percent of setpoint) | Non-Latching Hysteresis (0-100%) | AV108 | Percent | 1 | Non-Latching Hysteresis (% of setpoint) | 0-1000 | 50
Alarm Status
All | E,A | R | NV | 220 |  |  |  | Global Latching Alarm Status | Global Latching Alarm Status | AI56 | No-Units | 1 | (HHL;HL;LL;LLL;ON;Rsv;Rsv;Rsv;HVL;LVL)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-7: Reserved for future use (reads 0)
Bit 8: High Voltage Latching Alarm
Bit 9: Low Voltage Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
| E,A | R |  | 221 |  |  |  | Global Non-Latching Alarm Status | Global Non-Latching Alarm Status | AI57 | No-Units | 1 | (HL;LL;Rsv;Rsv;Rsv;Rsv;Rsv;Rsv;HVL;LVL)
Bit 0: High Non-Latching Alarm
Bit 1: Low Non-Latching Alarm
Bit 2-7: Reserved for future use (reads 0)
Bit 8: High Voltage Non-Latching Alarm
Bit 9: Low Voltage Non-Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
| E,A | R | NV | 222 |  |  |  | Global Most-Recent Latching Alarm Channel | Global Most-Recent Latching Alarm Ch | AI58 | No-Units | 1 | # of Most-Recent Channel (0=none) | 0-46, 0=none
| E,A | R | NV | 223 |  |  |  | Global Most-Recent Non-Latching Alarm Channel | Global Most-Recent Non-Latch Alarm Ch | AI59 | No-Units | 1 | # of Most-Recent Channel (0=none) | 0-46, 0=none
| E,A | R |  | 224 |  |  |  | Total number of channels in alarm (based on latching alarms) | Total number of Latch ch in alarm | AI60 | No-Units | 1 | # alarm chan (non-latching alarms)
| E,A | R |  | 225 |  |  |  | Total number of channels in alarm (based on non-latching alarms) | Total number of non-Latch ch in alarm | AI61 | No-Units | 1 | # alarm chan (based on latching alarms)
All | E,A | R/W | NV | 226 |  |  |  | Non-Latching Alarm Status w/ all (reads 0)
Alarm Thresholds (cont.)
All | E,A | R/W | NV | 227 |  |  | -1 | Non-Latching High High Threshold | Non-Latching High-High Threshold |  | Percent | 1 | % of breaker size | 0-1000
All | E,A | R/W | NV | 228 |  |  | -1 | Non-Latching Low Low Threshold | Non-Latching Low-Low Threshold |  | Percent | 1 | % of breaker size | 0-1000
| E,A | R |  | 229 |  |  |  | Error Bitmap1 (placeholder - bits TBD)
| E,A | R |  | 230 |  |  |  | Error Bitmap2 (placeholder - bits TBD)
| E,A | R |  | 231 |  |  |  | Error Bitmap3 (placeholder - bits TBD)
L-L Voltage Alarm Timers (seconds)
These timers control entry into an alarm state. A return to a non-alarm state is instantaneous.
All channels use these same global timers.
Note that the paraMeter measurement update rate is 1.6 secs, which will limit the effective resolution of these timers.
| E,A,B | R/W | NV | 232 |  |  |  | Overvoltage Alarm Timer | Overvoltage Alarm Timer | AV155 | Seconds | 1 | Alarm event duration threshold | 0-32767
| E,A,B | R/W | NV | 233 |  |  |  | Undervoltage Alarm Timer | Undervoltage Alarm Timer | AV156 | Seconds | 1 | Alarm event duration threshold | 0-32767
L-L VOLTAGE ALARM THRESHOLDS
All voltage alarm thresholds are expressed as Volts.
All Line-to-Line voltage channels use the same thresholds
An entry of 0 for any threshold disables that alarm for all channels.
Hysteresis is scaled by -1 to increase the precision by 1 decimal point
Hysteresis only applies to Non-Latching Alarms
| E,A,B | R/W | NV | 234 |  |  | 244 | Overvoltage Alarm Threshold | Overvoltage Alarm Threshold | AV157 | Volts | 5 | Overvoltage level threshold (0=OFF) | 0-32767
| E,A,B | R/W | NV | 235 |  |  | 244 | Undervoltage Alarm Threshold | Undervoltage Alarm Threshold | AV158 | Volts | 5 | Undervoltage level threshold (0=OFF) | 0-32767
| E,A,B | R/W | NV | 236 |  |  | -1 | Voltage Alarm Hysteresis (percentage of setpoint) | Voltage Alarm Hysteresis | AV159 | Percent | 1 | Voltage Alarm Hysteresis (% of setpoint) | 0-1000
L-L Voltage Alarm Status
1 | E,A,B | R/W | NV | 237 |  |  |  | Voltage Alarm Status | Voltage 1 Alarm Status | AV160 | No-Units | 1 | Write 0 to alarm bits to clear alarms
Latching Alarms are cleared by writing a 0 to it's alarm bit.
A write to a Non-Latching alarm is ignored
Bit 0: High Latching Alarm
Bit 1: Low Latching Alarm
Bit 2-7: Reserved for future use (reads 0)
Bit 8: High Non-Latching Alarm
Bit 9: Low Non-Latching Alarm
Bit 10-15: Reserved for future use (reads 0)
2 | E,A,B | R/W | NV | 238 |  |  |  | Voltage Alarm Status | Voltage 2 Alarm Status | AV161 | No-Units | 1 | Write 0 to alarm bits to clear alarms
3 | E,A,B | R/W | NV | 239 |  |  |  | Voltage Alarm Status | Voltage 3 Alarm Status | AV162 | No-Units | 1 | Write 0 to alarm bits to clear alarms
Global Resets
All | E,A | W |  | 291 |  |  |  | Global Reset - Write the listed value to perform the listed reset: | Global Resets: Write value to reset | AO2 | No-Units | 1 | 10203=kWh; others…
12345 = Reset Device
24658 = Clear Logical Meters Assignments
26012 = Begin new Demand Sub-interval
26013 = Reset Demand
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
Diagnostic Registers
| E,A | R/W | NV | 535 |  |  |  | Power Up Counter | Power Up Counter | AV163 | No-Units | 1 | Power Up Counter | 0-32767 | 0
| E,A | R |  | 536 |  |  |  | Device Health | Device Health | AI39 | No-Units | 1 | Bit Map of Device Health Indicators
Bit 0: Reserved
Bit 1: Frequency Out of Range or insufficient voltage on Phase A
to determine frequency range. *Frequency Range is 40-70 Hz.
Bit 2: Phase A Voltage Clipping
Bit 3: Phase B Voltage Clipping
Bit 4: Phase C Voltage Clipping
Bit 5: Current Clipping on at least 1 channel (AUX & Meter)
Bit 6-7: Reserved
Bit 8: Strip Connection Error
Bit 9-12: Reserved
Bit 13: Current Model, Model C
Bit 14: Power Model, Model B
Bit 15: Branch Power, Model A
| E,A | R |  | 537 |  |  |  | Reserved for future use
| E,A | R |  | 538 |  |  |  | Reserved for future use
| E,A | R |  | 539 |  |  |  | Reserved for future use
| E,A | R |  | 540 |  |  |  | Reserved for future use
| E,A | R |  | 541 |  |  |  | Reserved for future use
| E,A | R |  | 542 |  |  |  | Reserved for future use
| E,A | R |  | 543 |  |  |  | Product ID | Product ID | AI46 | No-Units | 1 | bit Map of Model configuration
Bit 0: Default Solid-Core
Bit 1: Default Split-Core
Bit 2-3: Reserved
Bit 4: Default 1/3 Volt (MCM2)
Bit 5-7: Reserved
Bit 8: Security
Bit 9: Aux Connectors Unpopulated
Bit 10: Modbus Address Per-Meter Capable
Bit 11: Logical Meters Capable
Bit 12: Custom V-Phase Capable
Bit 13: Reserved
Bit 14: Reserved
Bit 15: Reserved (Model A,E)
VOLTAGE INPUTS
| E,A,B | R |  | 553 | 694 | 695 | -1 | V1 Phase Angle (reference phase, always 0) | Voltage Phase Angle - V1 | AI533 | degrees-phase | 10 | Voltage Phase Angle - Aux ph1 (Ch 43)
| E,A,B | R |  | 554 | 696 | 697 | -1 | V2 Phase Angle (in relation to V1) | Voltage Phase Angle - V2 | AI534 | degrees-phase | 10 | Voltage Phase Angle - Aux ph2 (Ch 44)
| E,A,B | R |  | 555 | 698 | 699 | -1 | V3 Phase Angle (in relation to V1) | Voltage Phase Angle - V3 | AI535 | degrees-phase | 10 | Voltage Phase Angle - Aux ph3 (Ch 45)
Real Time Clock
Time is always in UTC
| E,A | R/W |  | 558 |  |  |  | Year (as years since 2000, ie 14 = 2014) | Set using Time_Synchronization service, if enabled |  |  |  |  | 0-2095 | 0
| E,A | R/W |  | 559 |  |  |  | Month (MSB) Day (LSB) 0x0201 = Feb 1st | Set using Time_Synchronization service, if enabled |  |  |  |  | 1-31,1-12 | 0x0101
| E,A | R/W |  | 560 |  |  |  | Hour (MSB) Minute (LSB) 0x0D1E = 1:30 PM | Set using Time_Synchronization service, if enabled |  |  |  |  | 0-23,0-59 | 0x0000
| E,A | R/W |  | 561 |  |  |  | Milliseconds - RTC starts on write to this register | Set using Time_Synchronization service, if enabled |  |  |  |  | 0-59000 | 0
Demand/Snapshot Time Stamp
Time is always in UTC
| E,A | R |  | 562 |  |  |  | Year (as years since 2000, ie 14 = 2014) | [5 empty] | 0-2095 | 0
| E,A | R |  | 563 |  |  |  | Month (MSB) Day (LSB) 0x0201 = Feb 1st | [5 empty] | 1-31,1-12 | 0x0101
| E,A | R |  | 564 |  |  |  | Hour (MSB) Minute (LSB) 0x0D1E = 1:30 PM | [5 empty] | 0-23,0-59 | 0x0000
| E,A | R |  | 565 |  |  |  | Milliseconds | [5 empty] | 0-59000 | 0
Firmware Build Numbers
| E,A,B,C | R |  | 562 |  |  |  | Build Date MSW (YY/MM/DD)
| E,A,B,C | R |  | 563 |  |  |  | Build Date LSW (YYMMDD)
| E,A,B,C | R |  | 564 |  |  |  | Build Time MSW (HHMMSS)
| E,A,B,C | R |  | 565 |  |  |  | Build Time LSW (HHMMSS)
VOLTAGE INPUTS (cont.)
| E,A | R |  | 566 | 702 | 703 | -1 | THD Voltage Phase A-N | [5 empty] | 0-1000
| E,A | R |  | 567 | 704 | 705 | -1 | THD Voltage Phase B-N | [5 empty] | 0-1000
| E,A | R |  | 568 | 706 | 707 | -1 | THD Voltage Phase C-N | [5 empty] | 0-1000
| E,A | R |  | 569 | 708 | 709 | -1 | THD Voltage Phase A-B | [5 empty] | 0-1000
| E,A | R |  | 570 | 710 | 711 | -1 | THD Voltage Phase B-C | [5 empty] | 0-1000
| E,A | R |  | 571 | 712 | 713 | -1 | THD Voltage Phase C-A | [5 empty] | 0-1000
Modbus Address Per Meter Offset
all | E,A | R/W | NV | 62016 |  |  |  | Offset of the start of the Modbus addresses assigned to the panel's logical Meters (when Modbus Address Per Meter is enabled), relative to the base meter Modbus address. (e.g. if the base meter Modbus address is 10 and this offset for panel 1 is set to 2, the Modbus address of Panel 1 Logical Meter 1 would be 12, Panel 1 Logical Meter 2 would be 13, etc.). 0 = Default (2 for Panel 1, 50 for panel 2)
User Defined Settings
all | E,A,B,C | R/W | NV | 62017 |  |  |  | User Defined Settings Status Register Bit 0: Enable User CT Phase Assignment Bit 1: Phase Angle Ref. (0 - V1, 1 - Assigned V-phase) Bit 2: Signed Power (Split-Core Only) Bit 3: Signed Power Factor (sign denotes lead/lag) Bit 4: Disable 2PH/3PH Pointmap Bit 5: Disable Second Panel Modbus Address Bit 6: Use Trig. Identity for 2PH KVA/PF Calculations Bit 7: Use RTC for Demand Sync. Bit 8: Enable Modbus Address Per Meter (E & A models only) Bit 9: Reserved Bit 10: Reserved Bit 11: Enable THD (E & A models only) Bit 12: Reverse Signed Power on Branches (Split-core Only) Bit 13-15: Reserved | User Defined Status Register | AV164 | No-Units | 1 | 1 in bit 0 enables CT phase assignment |  | 0
Logical Meter (Breaker) Assignment
Logical Meter Assignment will be cleared if Configuration Register is Changed, set Configuration first
Logical Meters should be unassigned before a block write. Global Resets Clear Logical Meters Assignments command can be used for this.
1 | E,A | R/W | NV | 62068 |  |  |  | Meter # for Branch Channel 1 | Logical Meter for Branch Channel 1 | AV210 | No-Units | 1 | Logical Meter Number for Branch Channel 1 | 0 - unassigned 0-46 | 0
2 | E,A | R/W | NV | 62069 |  |  |  | Meter # for Branch Channel 2 | Logical Meter for Branch Channel 2 | AV211 | No-Units | 1 | Logical Meter Number for Branch Channel 2 | 0-46 | 0
3 | E,A | R/W | NV | 62070 |  |  |  | Meter # for Branch Channel 3 | Logical Meter for Branch Channel 3 | AV212 | No-Units | 1 | Logical Meter Number for Branch Channel 3 | 0-46 | 0
4 | E,A | R/W | NV | 62071 |  |  |  | Meter # for Branch Channel 4 | Logical Meter for Branch Channel 4 | AV213 | No-Units | 1 | Logical Meter Number for Branch Channel 4 | 0-46 | 0
5 | E,A | R/W | NV | 62072 |  |  |  | Meter # for Branch Channel 5 | Logical Meter for Branch Channel 5 | AV214 | No-Units | 1 | Logical Meter Number for Branch Channel 5 | 0-46 | 0
6 | E,A | R/W | NV | 62073 |  |  |  | Meter # for Branch Channel 6 | Logical Meter for Branch Channel 6 | AV215 | No-Units | 1 | Logical Meter Number for Branch Channel 6 | 0-46 | 0
7 | E,A | R/W | NV | 62074 |  |  |  | Meter # for Branch Channel 7 | Logical Meter for Branch Channel 7 | AV216 | No-Units | 1 | Logical Meter Number for Branch Channel 7 | 0-46 | 0
8 | E,A | R/W | NV | 62075 |  |  |  | Meter # for Branch Channel 8 | Logical Meter for Branch Channel 8 | AV217 | No-Units | 1 | Logical Meter Number for Branch Channel 8 | 0-46 | 0
9 | E,A | R/W | NV | 62076 |  |  |  | Meter # for Branch Channel 9 | Logical Meter for Branch Channel 9 | AV218 | No-Units | 1 | Logical Meter Number for Branch Channel 9 | 0-46 | 0
10 | E,A | R/W | NV | 62077 |  |  |  | Meter # for Branch Channel 10 | Logical Meter for Branch Channel 10 | AV219 | No-Units | 1 | Logical Meter Number for Branch Channel 10 | 0-46 | 0
11 | E,A | R/W | NV | 62078 |  |  |  | Meter # for Branch Channel 11 | Logical Meter for Branch Channel 11 | AV220 | No-Units | 1 | Logical Meter Number for Branch Channel 11 | 0-46 | 0
12 | E,A | R/W | NV | 62079 |  |  |  | Meter # for Branch Channel 12 | Logical Meter for Branch Channel 12 | AV221 | No-Units | 1 | Logical Meter Number for Branch Channel 12 | 0-46 | 0
13 | E,A | R/W | NV | 62080 |  |  |  | Meter # for Branch Channel 13 | Logical Meter for Branch Channel 13 | AV222 | No-Units | 1 | Logical Meter Number for Branch Channel 13 | 0-46 | 0
14 | E,A | R/W | NV | 62081 |  |  |  | Meter # for Branch Channel 14 | Logical Meter for Branch Channel 14 | AV223 | No-Units | 1 | Logical Meter Number for Branch Channel 14 | 0-46 | 0
15 | E,A | R/W | NV | 62082 |  |  |  | Meter # for Branch Channel 15 | Logical Meter for Branch Channel 15 | AV224 | No-Units | 1 | Logical Meter Number for Branch Channel 15 | 0-46 | 0
16 | E,A | R/W | NV | 62083 |  |  |  | Meter # for Branch Channel 16 | Logical Meter for Branch Channel 16 | AV225 | No-Units | 1 | Logical Meter Number for Branch Channel 16 | 0-46 | 0
17 | E,A | R/W | NV | 62084 |  |  |  | Meter # for Branch Channel 17 | Logical Meter for Branch Channel 17 | AV226 | No-Units | 1 | Logical Meter Number for Branch Channel 17 | 0-46 | 0
18 | E,A | R/W | NV | 62085 |  |  |  | Meter # for Branch Channel 18 | Logical Meter for Branch Channel 18 | AV227 | No-Units | 1 | Logical Meter Number for Branch Channel 18 | 0-46 | 0
19 | E,A | R/W | NV | 62086 |  |  |  | Meter # for Branch Channel 19 | Logical Meter for Branch Channel 19 | AV228 | No-Units | 1 | Logical Meter Number for Branch Channel 19 | 0-46 | 0
20 | E,A | R/W | NV | 62087 |  |  |  | Meter # for Branch Channel 20 | Logical Meter for Branch Channel 20 | AV229 | No-Units | 1 | Logical Meter Number for Branch Channel 20 | 0-46 | 0
21 | E,A | R/W | NV | 62088 |  |  |  | Meter # for Branch Channel 21 | Logical Meter for Branch Channel 21 | AV230 | No-Units | 1 | Logical Meter Number for Branch Channel 21 | 0-46 | 0
22 | E,A | R/W | NV | 62089 |  |  |  | Meter # for Branch Channel 22 | Logical Meter for Branch Channel 22 | AV231 | No-Units | 1 | Logical Meter Number for Branch Channel 22 | 0-46 | 0
23 | E,A | R/W | NV | 62090 |  |  |  | Meter # for Branch Channel 23 | Logical Meter for Branch Channel 23 | AV232 | No-Units | 1 | Logical Meter Number for Branch Channel 23 | 0-46 | 0
24 | E,A | R/W | NV | 62091 |  |  |  | Meter # for Branch Channel 24 | Logical Meter for Branch Channel 24 | AV233 | No-Units | 1 | Logical Meter Number for Branch Channel 24 | 0-46 | 0
25 | E,A | R/W | NV | 62092 |  |  |  | Meter # for Branch Channel 25 | Logical Meter for Branch Channel 25 | AV234 | No-Units | 1 | Logical Meter Number for Branch Channel 25 | 0-46 | 0
26 | E,A | R/W | NV | 62093 |  |  |  | Meter # for Branch Channel 26 | Logical Meter for Branch Channel 26 | AV235 | No-Units | 1 | Logical Meter Number for Branch Channel 26 | 0-46 | 0
27 | E,A | R/W | NV | 62094 |  |  |  | Meter # for Branch Channel 27 | Logical Meter for Branch Channel 27 | AV236 | No-Units | 1 | Logical Meter Number for Branch Channel 27 | 0-46 | 0
28 | E,A | R/W | NV | 62095 |  |  |  | Meter # for Branch Channel 28 | Logical Meter for Branch Channel 28 | AV237 | No-Units | 1 | Logical Meter Number for Branch Channel 28 | 0-46 | 0
29 | E,A | R/W | NV | 62096 |  |  |  | Meter # for Branch Channel 29 | Logical Meter for Branch Channel 29 | AV238 | No-Units | 1 | Logical Meter Number for Branch Channel 29 | 0-46 | 0
30 | E,A | R/W | NV | 62097 |  |  |  | Meter # for Branch Channel 30 | Logical Meter for Branch Channel 30 | AV239 | No-Units | 1 | Logical Meter Number for Branch Channel 30 | 0-46 | 0
31 | E,A | R/W | NV | 62098 |  |  |  | Meter # for Branch Channel 31 | Logical Meter for Branch Channel 31 | AV240 | No-Units | 1 | Logical Meter Number for Branch Channel 31 | 0-46 | 0
32 | E,A | R/W | NV | 62099 |  |  |  | Meter # for Branch Channel 32 | Logical Meter for Branch Channel 32 | AV241 | No-Units | 1 | Logical Meter Number for Branch Channel 32 | 0-46 | 0
33 | E,A | R/W | NV | 62100 |  |  |  | Meter # for Branch Channel 33 | Logical Meter for Branch Channel 33 | AV242 | No-Units | 1 | Logical Meter Number for Branch Channel 33 | 0-46 | 0
34 | E,A | R/W | NV | 62101 |  |  |  | Meter # for Branch Channel 34 | Logical Meter for Branch Channel 34 | AV243 | No-Units | 1 | Logical Meter Number for Branch Channel 34 | 0-46 | 0
35 | E,A | R/W | NV | 62102 |  |  |  | Meter # for Branch Channel 35 | Logical Meter for Branch Channel 35 | AV244 | No-Units | 1 | Logical Meter Number for Branch Channel 35 | 0-46 | 0
36 | E,A | R/W | NV | 62103 |  |  |  | Meter # for Branch Channel 36 | Logical Meter for Branch Channel 36 | AV245 | No-Units | 1 | Logical Meter Number for Branch Channel 36 | 0-46 | 0
37 | E,A | R/W | NV | 62104 |  |  |  | Meter # for Branch Channel 37 | Logical Meter for Branch Channel 37 | AV246 | No-Units | 1 | Logical Meter Number for Branch Channel 37 | 0-46 | 0
38 | E,A | R/W | NV | 62105 |  |  |  | Meter # for Branch Channel 38 | Logical Meter for Branch Channel 38 | AV247 | No-Units | 1 | Logical Meter Number for Branch Channel 38 | 0-46 | 0
39 | E,A | R/W | NV | 62106 |  |  |  | Meter # for Branch Channel 39 | Logical Meter for Branch Channel 39 | AV248 | No-Units | 1 | Logical Meter Number for Branch Channel 39 | 0-46 | 0
40 | E,A | R/W | NV | 62107 |  |  |  | Meter # for Branch Channel 40 | Logical Meter for Branch Channel 40 | AV249 | No-Units | 1 | Logical Meter Number for Branch Channel 40 | 0-46 | 0
41 | E,A | R/W | NV | 62108 |  |  |  | Meter # for Branch Channel 41 | Logical Meter for Branch Channel 41 | AV250 | No-Units | 1 | Logical Meter Number for Branch Channel 41 | 0-46 | 0
42 | E,A | R/W | NV | 62109 |  |  |  | Meter # for Branch Channel 42 | Logical Meter for Branch Channel 42 | AV251 | No-Units | 1 | Logical Meter Number for Branch Channel 42 | 0-46 | 0
Custom Phase Map Support
1 | E,A | R/W | NV | 62116 |  |  |  | Voltage Phase for Branch Channel 1 | Voltage Phase for Branch Channel 1 | AV165 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 0 - Phase A 1 - Phase B 2 - Phase C | 0
2 | E,A | R/W | NV | 62117 |  |  |  | Voltage Phase for Branch Channel 2 | Voltage Phase for Branch Channel 2 | AV166 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
3 | E,A | R/W | NV | 62118 |  |  |  | Voltage Phase for Branch Channel 3 | Voltage Phase for Branch Channel 3 | AV167 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
4 | E,A | R/W | NV | 62119 |  |  |  | Voltage Phase for Branch Channel 4 | Voltage Phase for Branch Channel 4 | AV168 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
5 | E,A | R/W | NV | 62120 |  |  |  | Voltage Phase for Branch Channel 5 | Voltage Phase for Branch Channel 5 | AV169 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
6 | E,A | R/W | NV | 62121 |  |  |  | Voltage Phase for Branch Channel 6 | Voltage Phase for Branch Channel 6 | AV170 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
7 | E,A | R/W | NV | 62122 |  |  |  | Voltage Phase for Branch Channel 7 | Voltage Phase for Branch Channel 7 | AV171 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
8 | E,A | R/W | NV | 62123 |  |  |  | Voltage Phase for Branch Channel 8 | Voltage Phase for Branch Channel 8 | AV172 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
9 | E,A | R/W | NV | 62124 |  |  |  | Voltage Phase for Branch Channel 9 | Voltage Phase for Branch Channel 9 | AV173 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
10 | E,A | R/W | NV | 62125 |  |  |  | Voltage Phase for Branch Channel 10 | Voltage Phase for Branch Channel 10 | AV174 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
11 | E,A | R/W | NV | 62126 |  |  |  | Voltage Phase for Branch Channel 11 | Voltage Phase for Branch Channel 11 | AV175 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
12 | E,A | R/W | NV | 62127 |  |  |  | Voltage Phase for Branch Channel 12 | Voltage Phase for Branch Channel 12 | AV176 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
13 | E,A | R/W | NV | 62128 |  |  |  | Voltage Phase for Branch Channel 13 | Voltage Phase for Branch Channel 13 | AV177 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
14 | E,A | R/W | NV | 62129 |  |  |  | Voltage Phase for Branch Channel 14 | Voltage Phase for Branch Channel 14 | AV178 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
15 | E,A | R/W | NV | 62130 |  |  |  | Voltage Phase for Branch Channel 15 | Voltage Phase for Branch Channel 15 | AV179 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
16 | E,A | R/W | NV | 62131 |  |  |  | Voltage Phase for Branch Channel 16 | Voltage Phase for Branch Channel 16 | AV180 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
17 | E,A | R/W | NV | 62132 |  |  |  | Voltage Phase for Branch Channel 17 | Voltage Phase for Branch Channel 17 | AV181 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
18 | E,A | R/W | NV | 62133 |  |  |  | Voltage Phase for Branch Channel 18 | Voltage Phase for Branch Channel 18 | AV182 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
19 | E,A | R/W | NV | 62134 |  |  |  | Voltage Phase for Branch Channel 19 | Voltage Phase for Branch Channel 19 | AV183 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
20 | E,A | R/W | NV | 62135 |  |  |  | Voltage Phase for Branch Channel 20 | Voltage Phase for Branch Channel 20 | AV184 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
21 | E,A | R/W | NV | 62136 |  |  |  | Voltage Phase for Branch Channel 21 | Voltage Phase for Branch Channel 21 | AV185 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
22 | E,A | R/W | NV | 62137 |  |  |  | Voltage Phase for Branch Channel 22 | Voltage Phase for Branch Channel 22 | AV186 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
23 | E,A | R/W | NV | 62138 |  |  |  | Voltage Phase for Branch Channel 23 | Voltage Phase for Branch Channel 23 | AV187 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
24 | E,A | R/W | NV | 62139 |  |  |  | Voltage Phase for Branch Channel 24 | Voltage Phase for Branch Channel 24 | AV188 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
25 | E,A | R/W | NV | 62140 |  |  |  | Voltage Phase for Branch Channel 25 | Voltage Phase for Branch Channel 25 | AV189 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
26 | E,A | R/W | NV | 62141 |  |  |  | Voltage Phase for Branch Channel 26 | Voltage Phase for Branch Channel 26 | AV190 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
27 | E,A | R/W | NV | 62142 |  |  |  | Voltage Phase for Branch Channel 27 | Voltage Phase for Branch Channel 27 | AV191 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
28 | E,A | R/W | NV | 62143 |  |  |  | Voltage Phase for Branch Channel 28 | Voltage Phase for Branch Channel 28 | AV192 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
29 | E,A | R/W | NV | 62144 |  |  |  | Voltage Phase for Branch Channel 29 | Voltage Phase for Branch Channel 29 | AV193 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
30 | E,A | R/W | NV | 62145 |  |  |  | Voltage Phase for Branch Channel 30 | Voltage Phase for Branch Channel 30 | AV194 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
31 | E,A | R/W | NV | 62146 |  |  |  | Voltage Phase for Branch Channel 31 | Voltage Phase for Branch Channel 31 | AV195 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
32 | E,A | R/W | NV | 62147 |  |  |  | Voltage Phase for Branch Channel 32 | Voltage Phase for Branch Channel 32 | AV196 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
33 | E,A | R/W | NV | 62148 |  |  |  | Voltage Phase for Branch Channel 33 | Voltage Phase for Branch Channel 33 | AV197 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
34 | E,A | R/W | NV | 62149 |  |  |  | Voltage Phase for Branch Channel 34 | Voltage Phase for Branch Channel 34 | AV198 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
35 | E,A | R/W | NV | 62150 |  |  |  | Voltage Phase for Branch Channel 35 | Voltage Phase for Branch Channel 35 | AV199 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
36 | E,A | R/W | NV | 62151 |  |  |  | Voltage Phase for Branch Channel 36 | Voltage Phase for Branch Channel 36 | AV200 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
37 | E,A | R/W | NV | 62152 |  |  |  | Voltage Phase for Branch Channel 37 | Voltage Phase for Branch Channel 37 | AV201 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
38 | E,A | R/W | NV | 62153 |  |  |  | Voltage Phase for Branch Channel 38 | Voltage Phase for Branch Channel 38 | AV202 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
39 | E,A | R/W | NV | 62154 |  |  |  | Voltage Phase for Branch Channel 39 | Voltage Phase for Branch Channel 39 | AV203 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
40 | E,A | R/W | NV | 62155 |  |  |  | Voltage Phase for Branch Channel 40 | Voltage Phase for Branch Channel 40 | AV204 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
41 | E,A | R/W | NV | 62156 |  |  |  | Voltage Phase for Branch Channel 41 | Voltage Phase for Branch Channel 41 | AV205 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
42 | E,A | R/W | NV | 62157 |  |  |  | Voltage Phase for Branch Channel 42 | Voltage Phase for Branch Channel 42 | AV206 | No-Units | 1 | 0=phase-1/A; 1=phase-2/B; 2=phase-3/C | 0-2 | 0
This product supports the full EM4900 pointmap, but Aux inputs are unused
total registers in this section
218

## Logical Meters Setup
SETUP OF LOGICAL METERS
Logical meters are created by assigning the Logical Meter number to the CT channel in the Logicalible Meter Assignment registers
Logical meters, like physical breakers, are limited to 1, 2, or 3 CT channels that must be adjacent
Writing a 0 to a CT channel's Logical Assignment removes it from any Logical meter
To keep from violating the adjacency rule, the middle CT channel can not be removed from a 3-phase logical meter. Start by removing from either end.
Logical meters can be assigned via block write
All channels should be unassigned before issuing a block write. This can be done with a the Global Clear Logical Meters Assignment command.
Logical meters can be numbered in any order
EXAMPLE LOGICAL METERS SETUPS
Logical Meter Assignment - Example 1
| reg. | CT channel | Value (Logical Meter)
| 62068 | Branch Channel 1 | 1 | [18 empty] | Single Row
| 62069 | Branch Channel 2 | 2 | Logical Meter 1 | Logical Meter 2 | Logical Meter 3 |  | Logical Meter 4 | Logical Meter 5 |  |  | Logical Meter 6 | Logical Meter 7 | Logical Meter 8 | Logical Meter 9 | Logical Meter 10 | Logical Meter 11 | Logical Meter 12 | Logical Meter 13 |  | Logical Meter 14 | Logical Meter 15 | Logical Meter 16 |  | Logical Meter 17 |  | Logical Meter 18 | Logical Meter 19 | Logical Meter 20 | Logical Meter 21 | Logical Meter 22 |  |  | Logical Meter 23 |  |  | Logical Meter 24 | Logical Meter 25 | Logical Meter 26 | Logical Meter 27 |  |  | Logical Meter 29
| 62070 | Branch Channel 3 | 3
| 62071 | Branch Channel 4 | 3
| 62072 | Branch Channel 5 | 4
| 62073 | Branch Channel 6 | 5
| 62074 | Branch Channel 7 | 5
| 62075 | Branch Channel 8 | 5
| 62076 | Branch Channel 9 | 6
| 62077 | Branch Channel 10 | 7
| 62078 | Branch Channel 11 | 8 | ■□ | ■□ | ■□ |  | ■□ | ■□ |  |  | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ |  | ■□ | ■□ | ■□ |  | ■□ |  | ■□ | ■□ | ■□ | ■□ | ■□ |  |  | ■□ |  |  | ■□ | ■□ | ■□ | ■□ |  |  | ■□
| 62079 | Branch Channel 12 | 9
| 62080 | Branch Channel 13 | 10
| 62081 | Branch Channel 14 | 11
| 62082 | Branch Channel 15 | 12
| 62083 | Branch Channel 16 | 13
| 62084 | Branch Channel 17 | 13
| 62085 | Branch Channel 18 | 14
| 62086 | Branch Channel 19 | 15
| 62087 | Branch Channel 20 | 16
| 62088 | Branch Channel 21 | 16
| 62089 | Branch Channel 22 | 17
| 62090 | Branch Channel 23 | 17
| 62091 | Branch Channel 24 | 18
| 62092 | Branch Channel 25 | 19
| 62093 | Branch Channel 26 | 20
| 62094 | Branch Channel 27 | 21
| 62095 | Branch Channel 28 | 22
| 62096 | Branch Channel 29 | 22
| 62097 | Branch Channel 30 | 22
| 62098 | Branch Channel 31 | 23
| 62099 | Branch Channel 32 | 23
| 62100 | Branch Channel 33 | 23
| 62101 | Branch Channel 34 | 24
| 62102 | Branch Channel 35 | 25
| 62103 | Branch Channel 36 | 26
| 62104 | Branch Channel 37 | 27
| 62105 | Branch Channel 38 | 27
| 62106 | Branch Channel 39 | 27
| 62107 | Branch Channel 40 | 28
| 62108 | Branch Channel 41 | 28
| 62109 | Branch Channel 42 | 28
Logical Meter Assignment - Example 2
| reg. | CT channel | Value (Logical Meter)
| 62068 | Branch Channel 1 | 1 | [18 empty] | Single Row
| 62069 | Branch Channel 2 | 1 | Logical Meter 1 |  |  | Logical Meter 2 |  |  | Logical Meter 3 |  |  | Logical Meter 4 |  |  | Logical Meter 5 |  |  | Logical Meter 6 |  |  | Logical Meter 7 |  |  | Logical Meter 8 |  |  | Logical Meter 9 |  |  | Logical Meter 10 |  |  | Logical Meter 11 |  |  | Logical Meter 12 |  |  | Logical Meter 13 |  |  | Logical Meter 14
| 62070 | Branch Channel 3 | 1
| 62071 | Branch Channel 4 | 2
| 62072 | Branch Channel 5 | 2
| 62073 | Branch Channel 6 | 2
| 62074 | Branch Channel 7 | 3
| 62075 | Branch Channel 8 | 3
| 62076 | Branch Channel 9 | 3
| 62077 | Branch Channel 10 | 4
| 62078 | Branch Channel 11 | 4 | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□ |  |  | ■□
| 62079 | Branch Channel 12 | 4
| 62080 | Branch Channel 13 | 5
| 62081 | Branch Channel 14 | 5
| 62082 | Branch Channel 15 | 5
| 62083 | Branch Channel 16 | 6
| 62084 | Branch Channel 17 | 6
| 62085 | Branch Channel 18 | 6
| 62086 | Branch Channel 19 | 7
| 62087 | Branch Channel 20 | 7
| 62088 | Branch Channel 21 | 7
| 62089 | Branch Channel 22 | 8
| 62090 | Branch Channel 23 | 8
| 62091 | Branch Channel 24 | 8
| 62092 | Branch Channel 25 | 9
| 62093 | Branch Channel 26 | 9
| 62094 | Branch Channel 27 | 9
| 62095 | Branch Channel 28 | 10
| 62096 | Branch Channel 29 | 10
| 62097 | Branch Channel 30 | 10
| 62098 | Branch Channel 31 | 11
| 62099 | Branch Channel 32 | 11
| 62100 | Branch Channel 33 | 11
| 62101 | Branch Channel 34 | 12
| 62102 | Branch Channel 35 | 12
| 62103 | Branch Channel 36 | 12
| 62104 | Branch Channel 37 | 13
| 62105 | Branch Channel 38 | 13
| 62106 | Branch Channel 39 | 13
| 62107 | Branch Channel 40 | 14
| 62108 | Branch Channel 41 | 14
| 62109 | Branch Channel 42 | 14
Logical Meter Assignment - Example 3
| reg. | CT channel | Value (Logical Meter)
| 62068 | Branch Channel 1 | 1 | [18 empty] | Single Row
| 62069 | Branch Channel 2 | 1 | Logical Meter 1 |  | Logical Meter 2 |  | Logical Meter 3 |  | Logical Meter 4 |  | Logical Meter 5 |  | Logical Meter 6 |  | Logical Meter 7 |  | Logical Meter 8 |  | Logical Meter 9 |  | Logical Meter 10 |  | Logical Meter 11 |  | Logical Meter 12 |  | Logical Meter 13 |  | Logical Meter 14 |  | Logical Meter 15 |  | Logical Meter 16 |  | Logical Meter 17 |  | Logical Meter 18 |  | Logical Meter 19 |  | Logical Meter 20 |  | Logical Meter 21
| 62070 | Branch Channel 3 | 2
| 62071 | Branch Channel 4 | 2
| 62072 | Branch Channel 5 | 3
| 62073 | Branch Channel 6 | 3
| 62074 | Branch Channel 7 | 4
| 62075 | Branch Channel 8 | 4
| 62076 | Branch Channel 9 | 5
| 62077 | Branch Channel 10 | 5
| 62078 | Branch Channel 11 | 6 | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□ |  | ■□
| 62079 | Branch Channel 12 | 6
| 62080 | Branch Channel 13 | 7
| 62081 | Branch Channel 14 | 7
| 62082 | Branch Channel 15 | 8
| 62083 | Branch Channel 16 | 8
| 62084 | Branch Channel 17 | 9
| 62085 | Branch Channel 18 | 9
| 62086 | Branch Channel 19 | 10
| 62087 | Branch Channel 20 | 10
| 62088 | Branch Channel 21 | 11
| 62089 | Branch Channel 22 | 11
| 62090 | Branch Channel 23 | 12
| 62091 | Branch Channel 24 | 12
| 62092 | Branch Channel 25 | 13
| 62093 | Branch Channel 26 | 13
| 62094 | Branch Channel 27 | 14
| 62095 | Branch Channel 28 | 14
| 62096 | Branch Channel 29 | 15
| 62097 | Branch Channel 30 | 15
| 62098 | Branch Channel 31 | 16
| 62099 | Branch Channel 32 | 16
| 62100 | Branch Channel 33 | 17
| 62101 | Branch Channel 34 | 17
| 62102 | Branch Channel 35 | 18
| 62103 | Branch Channel 36 | 18
| 62104 | Branch Channel 37 | 19
| 62105 | Branch Channel 38 | 19
| 62106 | Branch Channel 39 | 20
| 62107 | Branch Channel 40 | 20
| 62108 | Branch Channel 41 | 21
| 62109 | Branch Channel 42 | 21
Logical Meter Assignment - Example 4
| reg. | CT channel | Value (Logical Meter)
| 62068 | Branch Channel 1 | 1 | [18 empty] | Single Row
| 62069 | Branch Channel 2 | 2 | Logical Meter 1 | Logical Meter 2 | Logical Meter 3 | Logical Meter 4 | Logical Meter 5 | Logical Meter 6 | Logical Meter 7 | Logical Meter 8 | Logical Meter 9 | Logical Meter 10 | Logical Meter 11 | Logical Meter 12 | Logical Meter 13 | Logical Meter 14 | Logical Meter 15 | Logical Meter 16 | Logical Meter 17 | Logical Meter 18 | Logical Meter 19 | Logical Meter 20 | Logical Meter 21 | Logical Meter 22 | Logical Meter 23 | Logical Meter 24 | Logical Meter 25 | Logical Meter 26 | Logical Meter 27 | Logical Meter 28 | Logical Meter 29 | Logical Meter 30 | Logical Meter 31 | Logical Meter 32 | Logical Meter 33 | Logical Meter 34 | Logical Meter 35 | Logical Meter 36 | Logical Meter 37 | Logical Meter 38 | Logical Meter 39 | Logical Meter 40 | Logical Meter 41 | Logical Meter 42
| 62070 | Branch Channel 3 | 3
| 62071 | Branch Channel 4 | 4
| 62072 | Branch Channel 5 | 5
| 62073 | Branch Channel 6 | 6
| 62074 | Branch Channel 7 | 7
| 62075 | Branch Channel 8 | 8
| 62076 | Branch Channel 9 | 9
| 62077 | Branch Channel 10 | 10
| 62078 | Branch Channel 11 | 11 | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□ | ■□
| 62079 | Branch Channel 12 | 12
| 62080 | Branch Channel 13 | 13
| 62081 | Branch Channel 14 | 14
| 62082 | Branch Channel 15 | 15
| 62083 | Branch Channel 16 | 16
| 62084 | Branch Channel 17 | 17
| 62085 | Branch Channel 18 | 18
| 62086 | Branch Channel 19 | 19
| 62087 | Branch Channel 20 | 20
| 62088 | Branch Channel 21 | 21
| 62089 | Branch Channel 22 | 22
| 62090 | Branch Channel 23 | 23
| 62091 | Branch Channel 24 | 24
| 62092 | Branch Channel 25 | 25
| 62093 | Branch Channel 26 | 26
| 62094 | Branch Channel 27 | 27
| 62095 | Branch Channel 28 | 28
| 62096 | Branch Channel 29 | 29
| 62097 | Branch Channel 30 | 30
| 62098 | Branch Channel 31 | 31
| 62099 | Branch Channel 32 | 32
| 62100 | Branch Channel 33 | 33
| 62101 | Branch Channel 34 | 34
| 62102 | Branch Channel 35 | 35
| 62103 | Branch Channel 36 | 36
| 62104 | Branch Channel 37 | 37
| 62105 | Branch Channel 38 | 38
| 62106 | Branch Channel 39 | 39
| 62107 | Branch Channel 40 | 40
| 62108 | Branch Channel 41 | 41
| 62109 | Branch Channel 42 | 42

## Logical Map by Meter
[8 empty] | Modbus |  |  |  |  | BACnet
Channel | Model (A,B,C) | R/W | NV | Int Reg | Float Reg MSW | Float Reg LSW | Scale Reg | Modbus Description | Object Name | Object ID | Units | COV Increment | BACnet Description | Range | Default
Panel & Branch Assignment
BACnet objets are incremented by 1 to get to the next Logical Meter, Object ID listed is base value for Meter #1
Logical Circuits are changed by incrementing by 1000, i.e. 10xxx is Circuit #1, 11xxx is Circuit #2, 12xxx is Circuit #3 etc.
| E,A,B,C | R | NV | 10000 |  |  |  | Panel & Circuit | Logical Meter Number (Panel&Circuit) | AI1 | No-Units | 0.01 | 1-46=pnl1(1-46);257-302=pnl2;0=unassigned | 0-2
| E,A,B,C | R | NV | 10001 |  |  |  | Number of Channels | Number of Channels in Logical Circuit | AI2 | No-Units | 0 | Number of Channels Assigned to Logical Meter 1 | 0-3
1 | E,A,B,C | R | NV | 10002 |  |  |  | Panel & Channel | Logical Ckt: CT 1 - Panel & Chan | AI3 | No-Units | 0 | 1-46=pnl1(1-46);257-302=pnl2;0=n/u | 0-1, 0-46
2 | E,A,B,C | R | NV | 10003 |  |  |  | Panel & Channel | Logical Ckt: CT 2 - Panel & Chan | AI4 | No-Units | 0 | 1-46=pnl1(1-46);257-302=pnl2;0=n/u | 0-1, 0-46
3 | E,A,B,C | R | NV | 10004 |  |  |  | Panel & Channel | Logical Ckt: CT 3 - Panel & Chan | AI5 | No-Units | 0 | 1-46=pnl1(1-46);257-302=pnl2;0=n/u | 0-1, 0-46
Circuits Inputs - Total
Total | E,A,B | R | NV | 10005 | 10101 | 10102 | 10049 | Total KWh (MSW) | kWh Energy: Total of all phases | AI15 | kWh | 0 | Real Energy - Total of active phases
Total | E,A,B | R | NV | 10006 |  |  |  | Total KWh (LSW)
Total | E,A,B | R |  | 10013 | 10109 | 10110 | 10051 | Total KW | kW: Total of all phases | AI19 | kW | 1 | Inst Real Power - Total of active phases
Total | E,A,B | R |  | 10015 | 10113 | 10114 | 10051 | Total KVA | kVA: Total of all phases | AI23 | kVA | 1 | Instantaneous Apparent Power - Total of active phases
Total | E,A,B | R |  | 10016 | 10115 | 10116 | -3 | Total PF | Power Factor: Total of all phases | AI27 | PF | 0.01 | Inst Power Factor - Average of active phases | 0.0 - 1.0
Total | E,A,B,C | R |  | 10018 | 10119 | 10120 | 10052 | Average Current | Amps: Avg of all phases | AI31 | Amperes | 5 | Inst Current - Average of active phases
Total | E,A,B | R |  | 10019 | 10121 | 10122 | 10051 | Present KW Demand | kW Present Demand:Total of all phases | AI35 | kW | 1 | Real Power Present Demand - Total of active phases
Total | E,A,B,C | R |  | 10022 | 10127 | 10128 | 10052 | Present Current Demand | Amps Present Demand:Avg of all phases | AI39 | Amperes | 5 | Present Current Demand - Average of active phases
Total | E,A,B | R | NV | 10023 | 10129 | 10130 | 10051 | Max KW Demand | kW Max Demand:Total of all phases | AI43 | kW | 1 | Real Power Max Demand - Total of active phases
Total | E,A,B,C | R |  | 10026 | 10135 | 10136 | 10052 | Max Current Demand | Amps Max Demand: Avg of all phases | AI47 | Amperes | 1 | Max Current Demand - Average of active phases
Total | E,A,B | R | NV | 10027 | 10137 | 10138 | 10051 | Max KW | kW: Max Total of all phases | AI51 | kW | 1 | Max Instantaneous Real Power - Total of active phases
Total | E,A,B,C | R |  | 10030 | 10143 | 10144 | 10052 | Max Current | Max Amps: Avg of all phases | AI55 | Amperes | 1 | Max Instantaneous Current - Average of active phases
Total | E,A,B | R |  | 10031 | 10145 | 10146 | 10053 | Voltage, L-L, Average of 3 Phases | VOLTS L-L: Avg of all phases | AI7 | Volts | 5 | Voltage L-L - Average of active phases (NaN if less than 2 CTs used)
Total | E,A,B | R |  | 10032 | 10147 | 10148 | 10053 | Voltage, L-N, Average of 3 Phases | VOLTS L-N: Avg of all phases | AI11 | Volts | 5 | Voltage L-N - Average of active phases
Total | E,A,B | R |  | 10033 | 10149 | 10150 | -2 | Frequency (derived from Phase A) | Frequency | AI6 | Hertz | 0.01 | Frequency (derived from Phase 1) | 40-70
Total | E,A | R |  | 10034 | 10151 | 10152 | -1 | THD Current, Average of 3 Phases | [5 empty] | 0-1000
Total | E,A | R |  | 10035 | 10153 | 10154 | -1 | THD Voltage L-L, Average of 3 Phases | [5 empty] | 0-1000
Total | E,A | R |  | 10036 | 10155 | 10156 | -1 | THD Voltage L-N, Average of 3 Phases | [5 empty] | 0-1000
Total | E,A,B | R | NV | 10037 | 10157 | 10158 | 10049 | Snapshot KWh (MSW) | kWh Snapshot Logical Meter 1 | AI1134 | kWh | 0 | Energy Snapshot Logical Meter 1
Total | E,A,B | R | NV | 10038 |  |  |  | Snapshot KWh (LSW) | kWh Snapshot - Total of all phases | AI59 | kWh | 0 | Energy Snapshot - Total of active phases
Total | E,A,B | R | NV | 10049 |  |  |  | Energy Scale
Total | E,A,B | R | NV | 10051 |  |  |  | Power Scale
Total | E,A,B,C | R | NV | 10052 |  |  |  | Current Scale
Total | E,A,B | R | NV | 10053 |  |  |  | Voltage Scale Register
Circuit Resets
All | E,A,B,C | W |  | 10057 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset: | Logical Circuit Reset (1 of 6 values) | AO1 | No-Units |  | 10203=kWh; 29877=Max Amps&KW; 20097=Max Dmnd; 31010=Latching Alarms
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps)
All | E,A,B,C | R/W | NV | 10058 |  |  |  | Circuit CT Size | Logical Circuit CT Size | AV1 | Amperes | 5 | Logical Meter CTs Amperage Rating (-32768 if all CTs used are not the same value) | 0-32767 | 100
Breaker Sizes (Amps)
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
All | E,A,B,C | R/W | NV | 10059 |  |  |  | Circuit Breaker Size | Logical Circuit Breaker Size | AV5 | Amperes | 5 | Logical Meter Breaker Size in Amps (-32768 if all phases used are not the same value) | 0-32767 | 20
Circuit Alarm Status
All | E,A,B,C | R/W | NV | 10060 |  |  |  | Circuit Latching Alarm Status | Logical Circuit Latching Alarm Status | AV9 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Latching Alarms are cleared by writing a 0 to its alarm bit |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
All | E,A,B,C | R |  | 10061 |  |  |  | Circuit Non-Latching Alarm Status | Logical Ckt Non-Latching Alarm Status | AI63 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Bit 0: Reserved for High High Non-Latching Alarm (reads 0) |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Panel & Branch Assignment - Phase 1
1 | E,A,B,C | R | NV | 10204 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 1
1 | E,A,B | R | NV | 10205 | 10301 | 10302 | 10249 | KWh (MSW) | kWh Energy: CT 1 | AI16 | kWh | 1 | Real Energy - phase 1
1 | E,A,B | R | NV | 10206 |  |  |  | KWh (LSW)
1 | E,A,B | R |  | 10213 | 10309 | 10310 | 10251 | KW | kW: CT 1 | AI20 | kW | 1 | Instantaneous Real Power - CT 1
1 | E,A,B | R |  | 10215 | 10313 | 10314 | 10251 | KVA | kVA: CT 1 | AI24 | kVA | 1 | Instantaneous Apparent Power - CT 1
1 | E,A,B | R |  | 10216 | 10315 | 10316 | -3 | PF | Power Factor: CT 1 | AI28 | PF | 0.01 | Instantaneous Power Factor - CT 1 | 0.0 - 1.0
1 | E,A,B |  |  | 10217 | 10317 | 10318 | -1 | Current Angle | Phase Angle CT 1 | AI67 | degrees-angular | 5 | Current Phase Angle in Degrees - CT 1
1 | E,A,B,C | R |  | 10218 | 10319 | 10320 | 10252 | Current | Amps: CT 1 | AI32 | Amperes | 5 | Instantaneous Current - CT 1
1 | E,A,B | R |  | 10219 | 10321 | 10322 | 10251 | Present KW Demand | kW Present Demand: CT 1 | AI36 | kW | 1 | Real Power Present Demand - CT 1
1 | E,A,B,C | R |  | 10222 | 10327 | 10328 | 10252 | Present Current Demand | Amps Present Demand: CT 1 | AI40 | Amperes | 5 | Present Current Demand - CT 1
1 | E,A,B | R | NV | 10223 | 10329 | 10330 | 10251 | Max KW Demand | kW Max Demand: CT 1 | AI44 | kW | 1 | Real Power Max Demand - CT 1
1 | E,A,B,C | R | NV | 10226 | 10335 | 10336 | 10252 | Max Current Demand | Amps Max Demand: CT 1 | AI48 | Amperes | 5 | Max Current Demand - CT 1
1 | E,A,B | R | NV | 10227 | 10337 | 10338 | 10251 | Max KW | kW: CT 1 Max | AI52 | kW | 1 | Max Instantaneous Real Power- CT 1
1 | E,A,B,C | R | NV | 10230 | 10343 | 10344 | 10252 | Max Current | Max Amps: CT 1 | AI56 | Amperes | 5 | Max Instantaneous Current - CT 1
1 | E,A,B | R |  | 10231 | 10345 | 10346 | 10253 | Voltage, L-L | VOLTS CT 1 - CT 2 | AI8 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 1 and phase assigned to CT 2
1 | E,A,B | R |  | 10232 | 10347 | 10348 | 10253 | Voltage, L-N | VOLTS CT 1-N | AI12 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 1 and Neutral
1 | E,A,B | R |  | 10233 | 10349 | 10350 | -2 | Frequency (derived from Phase A) | Frequency | AI6 | Hertz | 0.01 | Frequency (derived from Phase 1) | 40-70
1 | E,A | R |  | 10234 | 10351 | 10352 | -1 | THD Current | [5 empty] | 0-1000
1 | E,A | R |  | 10235 | 10353 | 10354 | -1 | THD Voltage L-L | [5 empty] | 0-1000
1 | E,A | R |  | 10236 | 10355 | 10356 | -1 | THD Voltage L-N | [5 empty] | 0-1000
1 | E,A,B | R |  | 10237 | 10357 | 10358 | 10249 | KWh Snapshot (MSW) | kWh Snapshot CT 1 | AI60 | kWh | 0 | Energy Snapshot - CT 1
1 | E,A,B | R |  | 10238 |  |  |  | KWh Snapshot (LSW)
1 | E,A,B | R | NV | 10249 |  |  |  | Energy Scale
1 | E,A,B | R | NV | 10251 |  |  |  | Power Scale
1 | E,A,B,C | R | NV | 10252 |  |  |  | Current Scale
1 | E,A,B | R | NV | 10253 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 1
1 | E,A,B,C | W |  | 10257 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset: | Channel 1 Reset | AO2 | No-Units |  | 10203=kWh; 29877=Max Current & Max kW
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 1
All | E,A,B,C | R/W | NV | 10258 |  |  |  | Circuit CT Size | CT 1 Size | AV2 | Amperes | 5 | CT 1 Amperage Rating | 0-32767 | 100
Breaker Sizes (Amps) - Phase 1
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
1 | E,A,B,C | R/W | NV | 10259 |  |  |  | Chanel Breaker Size | CT 1 Breaker Size | AV6 | Amperes | 5 | CT 1 Breaker Size in Amps | 0-32767 | 20
Circuit Alarm Status - Phase 1
1 | E,A,B,C | R/W | NV | 10260 |  |  |  | Channel Latching Alarm Status | CT 1 Latching Alarm Status | AV10 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Latching Alarms are cleared by writing a 0 to its alarm bit |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
1 | E,A,B,C | R |  | 10261 |  |  |  | Channel Non-Latching Alarm Status | CT 1 Non-Latching Alarm Status | AI64 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Bit 0: Reserved for High High Non-Latching Alarm (reads 0) |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 1
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
1 | E,A,B,C | R |  | 10262 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | E,A,B,C | R |  | 10263 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | E,A,B,C | R |  | 10264 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | E,A,B,C | R |  | 10265 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
1 | E,A,B,C | R |  | 10266 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
Panel & Branch Assignment - Phase 2
1 | E,A,B,C | R | NV | 10404 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 2
2 | E,A,B | R | NV | 10405 | 10501 | 10502 | 10449 | KWh (MSW) | kWh Energy: CT 2 | AI17 | kWh | 1 | Real Energy - phase 2 (NaN if CT is not used)
2 | E,A,B | R | NV | 10406 |  |  |  | KWh (LSW)
2 | E,A,B | R |  | 10413 | 10509 | 10510 | 10451 | KW | kW: CT 2 | AI21 | kW | 1 | Instantaneous Real Power - CT 2 (NaN if CT is not used)
2 | E,A,B | R |  | 10415 | 10513 | 10514 | 10451 | KVA | kVA: CT 2 | AI25 | kVA | 1 | Instantaneous Apparent Power - CT 2 (NaN if CT is not used)
2 | E,A,B | R |  | 10416 | 10515 | 10516 | -3 | PF | Power Factor: CT 2 | AI29 | PF | 0.01 | Instantaneous Power Factor - CT 2 (NaN if CT is not used) | 0.0 - 1.0
2 | E,A,B |  |  | 10417 | 10517 | 10518 | -1 | Current Angle | Phase Angle CT 2 | AI68 | degrees-angular | 5 | Current Phase Angle in Degrees - CT 2 (NaN if CT is not used)
2 | E,A,B,C | R |  | 10418 | 10519 | 10520 | 10452 | Current | Amps: CT 2 | AI33 | Amperes | 5 | Instantaneous Current - CT 2 (NaN if CT is not used)
2 | E,A,B | R |  | 10419 | 10521 | 10522 | 10451 | Present KW Demand | kW Present Demand: CT 2 | AI37 | kW | 1 | Real Power Present Demand - CT 2 (NaN if CT is not used)
2 | E,A,B,C | R |  | 10422 | 10527 | 10528 | 10452 | Present Current Demand | Amps Present Demand: CT 2 | AI41 | Amperes | 5 | Present Current Demand - CT 2 (NaN if CT is not used)
2 | E,A,B | R | NV | 10423 | 10529 | 10530 | 10451 | Max KW Demand | kW Max Demand: CT 2 | AI45 | kW | 1 | Real Power Max Demand - CT 2 (NaN if CT is not used)
2 | E,A,B,C | R | NV | 10426 | 10535 | 10536 | 10452 | Max Current Demand | Amps Max Demand: CT 2 | AI49 | Amperes | 5 | Max Current Demand - CT 2 (NaN if CT is not used)
2 | E,A,B | R | NV | 10427 | 10537 | 10538 | 10451 | Max KW | kW: CT 2 Max | AI53 | kW | 1 | Max Instantaneous Real Power- CT 2 (NaN if CT is not used)
2 | E,A,B,C | R | NV | 10430 | 10543 | 10544 | 10452 | Max Current | Max Amps: CT 2 | AI57 | Amperes | 5 | Max Instantaneous Current - CT 2 (NaN if CT is not used)
2 | E,A,B | R |  | 10431 | 10545 | 10546 | 10453 | Voltage, L-L | VOLTS CT 2 - CT 3 | AI9 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 2 and phase assigned to CT 3 (NaN if CT is not used)
2 | E,A,B | R |  | 10432 | 10547 | 10548 | 10453 | Voltage, L-N | VOLTS CT 2-N | AI13 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 2 and Neutral (NaN if CT is not used)
2 | E,A,B | R |  | 10433 | 10549 | 10550 | -2 | Frequency (derived from Phase A) | Frequency | AI6 | Hertz | 0.01 | Frequency (derived from Phase 1) | 40-70
2 | E,A | R |  | 10434 | 10551 | 10552 | -1 | THD Current | [5 empty] | 0-1000
2 | E,A | R |  | 10435 | 10553 | 10554 | -1 | THD Voltage L-L | [5 empty] | 0-1000
2 | E,A | R |  | 10436 | 10555 | 10556 | -1 | THD Voltage L-N | [5 empty] | 0-1000
2 | E,A,B | R |  | 10437 | 10557 | 10558 | 10449 | KWh Snapshot (MSW) | kWh Snapshot CT 2 | AI61 | kWh | 0 | Energy Snapshot - CT 2 (NaN if CT is not used)
2 | E,A,B | R |  | 10438 |  |  |  | KWh Snapshot (LSW)
2 | E,A,B | R | NV | 10449 |  |  |  | Energy Scale
2 | E,A,B | R | NV | 10451 |  |  |  | Power Scale
2 | E,A,B,C | R | NV | 10452 |  |  |  | Current Scale
2 | E,A,B | R | NV | 10453 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 2
2 | E,A,B,C | W |  | 10457 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset: | Channel 2 Reset | AO3 | No-Units |  | 10203=kWh; 29877=Max Current & Max kW
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 2
All | E,A,B,C | R/W | NV | 10458 |  |  |  | Circuit CT Size | CT 2 Size | AV3 | Amperes | 5 | CT 2 Amperage Rating (-32768 if CT is not used) | 0-32767 | 100
Breaker Sizes (Amps) - Phase 2
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
2 | E,A,B,C | R/W | NV | 10459 |  |  |  | Chanel Breaker Size | CT 2 Breaker Size | AV7 | Amperes | 5 | CT 2 Breaker Size in Amps (-32768 if CT is not used) | 0-32767 | 20
Circuit Alarm Status - Phase 2
2 | E,A,B,C | R/W | NV | 10460 |  |  |  | Channel Latching Alarm Status | CT 2 Latching Alarm Status | AV11 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Latching Alarms are cleared by writing a 0 to its alarm bit |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
2 | E,A,B,C | R |  | 10461 |  |  |  | Channel Non-Latching Alarm Status | CT 2 Non-Latching Alarm Status | AI65 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Bit 0: Reserved for High High Non-Latching Alarm (reads 0) |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 2
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
2 | E,A,B,C | R |  | 10462 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | E,A,B,C | R |  | 10463 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | E,A,B,C | R |  | 10464 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | E,A,B,C | R |  | 10465 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
2 | E,A,B,C | R |  | 10466 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
Panel & Branch Assignment - Phase 3
1 | E,A,B,C | R | NV | 10604 |  |  |  | Panel & Channel | [5 empty] | 0-2, 0-46
Circuit Inputs - Phase 3
3 | E,A,B | R | NV | 10605 | 10701 | 10702 | 10649 | KWh (MSW) | kWh Energy: CT 3 | AI18 | kWh | 1 | Real Energy - phase 3 (NaN if CT is not used)
3 | E,A,B | R | NV | 10606 |  |  |  | KWh (LSW)
3 | E,A,B | R |  | 10613 | 10709 | 10710 | 10651 | KW | kW: CT 3 | AI22 | kW | 1 | Instantaneous Real Power - CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10615 | 10713 | 10714 | 10651 | KVA | kVA: CT 3 | AI26 | kVA | 1 | Instantaneous Apparent Power - CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10616 | 10715 | 10716 | -3 | PF | Power Factor: CT 3 | AI30 | PF | 0.01 | Instantaneous Power Factor - CT 3 (NaN if CT is not used) | 0.0 - 1.0
3 | E,A,B |  |  | 10617 | 10717 | 10718 | -1 | Current Angle | Phase Angle CT 3 | AI69 | degrees-angular | 5 | Current Phase Angle in Degrees - CT 3 (NaN if CT is not used)
3 | E,A,B,C | R |  | 10618 | 10719 | 10720 | 10652 | Current | Amps: CT 3 | AI34 | Amperes | 5 | Instantaneous Current - CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10619 | 10721 | 10722 | 10651 | Present KW Demand | kW Present Demand: CT 3 | AI38 | kW | 1 | Real Power Present Demand - CT 3 (NaN if CT is not used)
3 | E,A,B,C | R |  | 10622 | 10727 | 10728 | 10652 | Present Current Demand | Amps Present Demand: CT 3 | AI42 | Amperes | 5 | Present Current Demand - CT 3 (NaN if CT is not used)
3 | E,A,B | R | NV | 10623 | 10729 | 10730 | 10651 | Max KW Demand | kW Max Demand: CT 3 | AI46 | kW | 1 | Real Power Max Demand - CT 3 (NaN if CT is not used)
3 | E,A,B,C | R | NV | 10626 | 10735 | 10736 | 10652 | Max Current Demand | Amps Max Demand: CT 3 | AI50 | Amperes | 5 | Max Current Demand - CT 3 (NaN if CT is not used)
3 | E,A,B | R | NV | 10627 | 10737 | 10738 | 10651 | Max KW | kW: CT 3 Max | AI54 | kW | 1 | Max Instantaneous Real Power- CT 3 (NaN if CT is not used)
3 | E,A,B,C | R | NV | 10630 | 10743 | 10744 | 10652 | Max Current | Max Amps: CT 3 | AI58 | Amperes | 5 | Max Instantaneous Current - CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10631 | 10745 | 10746 | 10653 | Voltage, L-L | VOLTS CT 1 - CT 3 | AI10 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 1 and phase assigned to CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10632 | 10747 | 10748 | 10653 | Voltage, L-N | VOLTS CT 3-N | AI14 | Volts | 5 | Instantaneous Voltage between phase assigned to CT 3 and Neutral (NaN if CT is not used)
3 | E,A,B | R |  | 10633 | 10749 | 10750 | -2 | Frequency (derived from Phase A) | Frequency | AI6 | Hertz | 0.01 | Frequency (derived from Phase 1) | 40-70
3 | E,A | R |  | 10634 | 10751 | 10752 | -1 | THD Current | [5 empty] | 0-1000
3 | E,A | R |  | 10635 | 10753 | 10754 | -1 | THD Voltage L-L | [5 empty] | 0-1000
3 | E,A | R |  | 10636 | 10755 | 10756 | -1 | THD Voltage L-N | [5 empty] | 0-1000
3 | E,A,B | R |  | 10637 | 10757 | 10758 | 10649 | KWh Snapshot (MSW) | kWh Snapshot CT 3 | AI62 | kWh | 0 | Energy Snapshot - CT 3 (NaN if CT is not used)
3 | E,A,B | R |  | 10638 |  |  |  | KWh Snapshot (LSW)
3 | E,A,B | R | NV | 10649 |  |  |  | Energy Scale
3 | E,A,B | R | NV | 10651 |  |  |  | Power Scale
3 | E,A,B,C | R | NV | 10652 |  |  |  | Current Scale
3 | E,A,B | R | NV | 10653 |  |  |  | Voltage Scale Register
Circuit Resets - Phase 3
3 | E,A,B,C | W |  | 10657 |  |  |  | Circuit Reset - Write the listed value to perform the listed reset: | Channel 3 Reset | AO4 | No-Units |  | 10203=kWh; 29877=Max Current & Max kW
0 = No Action
31010 = Reset all Latching Alarms
10203 = Clear all KWH values to zero
29877 = Clear all Max Current and Max KW values to zero
20097 = Clear all Max Demand values to zero
CT Sizes (Amps) - Phase 3
All | E,A,B,C | R/W | NV | 10658 |  |  |  | Circuit CT Size | CT 3 Size | AV4 | Amperes | 5 | CT 3 Amperage Rating (-32768 if CT is not used) | 0-32767 | 100
Breaker Sizes (Amps) - Phase 3
Setting the breaker size to "0" will disable all alarms for that channel.
Breaker sizes are in Amps
3 | E,A,B,C | R/W | NV | 10659 |  |  |  | Chanel Breaker Size | CT 3 Breaker Size | AV8 | Amperes | 5 | CT 3 Breaker Size in Amps (-32768 if CT is not used) | 0-32767 | 20
Circuit Alarm Status - Phase 3
3 | E,A,B,C | R/W | NV | 10660 |  |  |  | Channel Latching Alarm Status | CT 3 Latching Alarm Status | AV12 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Latching Alarms are cleared by writing a 0 to its alarm bit |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 0: High High Latching Alarm
Bit 1: High Latching Alarm
Bit 2: Low Latching Alarm
Bit 3: Low Low Latching Alarm
Bit 4: Latching Alarm OFF state declared (1=OFF; ON state must have been achieved prior)
Bit 5-15: Reserved for future use (reads 0)
3 | E,A,B,C | R |  | 10661 |  |  |  | Channel Non-Latching Alarm Status | CT 3 Non-Latching Alarm Status | AI66 | No-Units | 1 | bitmap: (0=HHL;1=HL;2=LL;3=LLL;4=State[1=OFF*];
[8 empty] | Bit 0: Reserved for High High Non-Latching Alarm (reads 0) |  |  |  |  | 5-6=Rsv;7=HH:8=H;9=L;10=LL;11-15=Rsv)
Bit 1: High Non-Latching Alarm
Bit 2: Low Non-Latching Alarm
Bit 3: Reserved for Low Low Non-Latching Alarm (reads 0)
Bit 4-15: Reserved for future use (reads 0)
Latching Alarm Counters - Phase 3
Latching Alarm Counters are incremented each time their associated Alarm Status Bit has latched
All Counters will rollover to the value of 1
Values are set to 0 over a power cycle
3 | E,A,B,C | R |  | 10662 |  |  |  | High High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | E,A,B,C | R |  | 10663 |  |  |  | High Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | E,A,B,C | R |  | 10664 |  |  |  | Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | E,A,B,C | R |  | 10665 |  |  |  | Low Low Latching Alarm Counter | [5 empty] | 0-10922 | 0
3 | E,A,B,C | R |  | 10666 |  |  |  | Latching Alarm OFF state Counter | [5 empty] | 0-10922 | 0
total registers in this section
482