## Revision Info
Active Filter External Modbus Register Definitions
API version: | v2.0
Document Rev.: | Rev. A
History
RC1 | Added registers for 4WIRE
RC2 | Renamed phases to L1, L2, L3
Changed names of some registers to be more descriptive and agreeable with other document
RC3 | Source THDu names changed to show line-to-line
Fixed wrong name for address 2152 (Zero Sequence Source Current)

## Device identification
Device identification 16 bit registers (RO)
Parameter | Data Type | Data | Modbus Device Register | Address
Product Identifier | uint16 | AHF=17173 EVC=17174 4WIRE=17175 | 407001 | 7000
FW[X,X] | uint16 | - | 407002 | 7001
FW[X,’.’] | uint16 | - | 407003 | 7002
FW[Y,Y] | uint16 | - | 407004 | 7003
FW[Y,‘.’] | uint16 | - | 407005 | 7004
FW[Z,Z] | uint16 | - | 407006 | 7005
FW[Z,0x00] | uint16 | - | 407007 | 7006
Product Family [‘C’,’o’] | uint16 | - | 407008 | 7007
Product Family [‘n’,’t’] | uint16 | - | 407009 | 7008
Product Family [‘r’,’o’] | uint16 | - | 407010 | 7009
Product Family [‘l’,’l’] | uint16 | - | 407011 | 7010
Product Family [‘e’,’r’] | uint16 | - | 407012 | 7011
User Application[‘O’,’t’] | uint16 | - | 407013 | 7012
User Application[‘h’,’e’] | uint16 | - | 407014 | 7013
User Application[‘r’,0x00] | uint16 | - | 407015 | 7014

## Control Commands
Control Commands (WO)
Parameter | Data Type | Format | Unit | Modbus Device Register | Address
Run/Stop Command | uint16 | 1: RUN | - | 401001 | 1000
0: STOP
Reset/Acknowledge Alert | uint16 | Write 0 or 1 to RESET/ACK | - | 401002 | 1001
Target THD | float32 |  | - | 401003 | 1002
Target THD type factor | uint16 | 0=THDi 1=THDv | - | 401005 | 1004
PF cos(phi) | float32 | ( positive=lag, negative = lead) | - | 401006 | 1005
Reactive Target | float32 |  | amps or VAR | 401008 | 1007
Reactive Target Type | uint16 | 0=Amps 1=VAR. This parameter can only be changed when the unit is OFF. Changing this parameter also causes the "Reactive Target Command" to be reset to 0 | - | 401010 | 1009
Voltage Regulation Set Point | float32 |  | volts | 401011 | 1010
Harmonic Enable | uint16 | 0=Disable, 1=Enable (Only supported on AHF units. Write has no effect otherwise) | - | 401013 | 1012
Reactive Mode | uint16 | 0 = Reactive Mode OFF | - | 401014 | 1013
1 = PF Mode ON
2 = V-Reg Mode ON (Only supported on EVC Units)
3 = Reactive (Q) Target Mode ON (Only supported on EVC Units)
Load Balance Enable | uint16 | 0=Disable, 1=Enable (3WIRE) 0=Disable, Bit 1=Negative Seq Enable Bit 2 = Zero Seq Enable (4 WIRE) | - | 401015 | 1014
Note: Read of these registers will return invalid data for each type as follows: 0xFFFF (uint16), NaN (float32)

## Events & Notifications
Events (RO)
Event | Data Type | Data Format | Modbus Device Register | Address
AC Line Not Qualified Validity | bool | 0 = invalid, 1=valid | 406001.00 | 6000, 0
Over Current Condition Detected Validity | bool | 0 = invalid, 1=valid | 406001.01 | 6000, 1
DC Bus Trip Validity | bool | 0 = invalid, 1=valid | 406001.02 | 6000, 2
Filter Trip Validity | bool | 0 = invalid, 1=valid | 406001.03 | 6000, 3
Firmware Trip Validity | bool | 0 = invalid, 1=valid | 406001.04 | 6000, 4
IGBT Trip Validity | bool | 0 = invalid, 1=valid | 406001.05 | 6000, 5
Gate Drive Trip Validity | bool | 0 = invalid, 1=valid | 406001.06 | 6000, 6
HMI Communication Loss Validity | bool | 0 = invalid, 1=valid | 406001.07 | 6000, 7
Auto Detection Out of Range Validity | bool | 0 = invalid, 1=valid | 406001.08 | 6000, 8
Over Temperature Validity | bool | 0 = invalid, 1=valid | 406001.09 | 6000, 9
Under Temperature Validity | bool | 0 = invalid, 1=valid | 406001.10 | 6000, 10
Current Sensor Inoperable Validity | bool | 0 = invalid, 1=valid | 406001.11 | 6000, 11
Power Supply Out of Range Validity | bool | 0 = invalid, 1=valid | 406001.12 | 6000, 12
MOV Requires Service Validity | bool | 0 = invalid, 1=valid | 406001.13 | 6000, 13
AC Line Not Qualified | bool | 0 = not active, 1=active | 406002.00 | 6001, 0
Over Current Condition Detected | bool | 0 = not active, 1=active | 406002.01 | 6001, 1
DC Bus Trip | bool | 0 = not active, 1=active | 406002.02 | 6001, 2
Filter Trip | bool | 0 = not active, 1=active | 406002.03 | 6001, 3
Firmware Trip | bool | 0 = not active, 1=active | 406002.04 | 6001, 4
IGBT Trip | bool | 0 = not active, 1=active | 406002.05 | 6001, 5
Gate Drive Trip | bool | 0 = not active, 1=active | 406002.06 | 6001, 6
HMI Communication Loss | bool | 0 = not active, 1=active | 406002.07 | 6001, 7
Auto Detection Out of Range | bool | 0 = not active, 1=active | 406002.08 | 6001, 8
Over Temperature | bool | 0 = not active, 1=active | 406002.09 | 6001, 9
Under Temperature | bool | 0 = not active, 1=active | 406002.10 | 6001, 10
Current Sensor Inoperable | bool | 0 = not active, 1=active | 406002.11 | 6001, 11
Power Supply Out of Range | bool | 0 = not active, 1=active | 406002.12 | 6001, 12
MOV Requires Service | bool | 0 = not active, 1=active | 406002.13 | 6001, 13
High Frequency Voltage Distortion Condition Validity | bool | 0 = invalid, 1=valid | 406003.1 | 6002, 1
Int.Transformer Over Temperature Validity | bool | 0 = invalid, 1=valid | 406003.2 | 6002, 2
Parallel Wiring Mismatch Validity | bool | 0 = invalid, 1=valid | 406003.3 | 6002, 3
Contactor Trip Event Validity | bool | 0 = invalid, 1=valid | 406003.4 | 6002, 4
Protection Firmware Trip Validity | bool | 0 = invalid, 1=valid | 406003.5 | 6002, 5
Fan Failure Validity | bool | 0 = invalid, 1=valid | 406003.6 | 6002, 6
High Frequency Voltage Distortion Condition | bool | 0 = not active, 1=active | 406004.1 | 6003, 1
Internal Transformer Over temperature | bool | 0 = not active, 1=active | 406004.2 | 6003, 2
Parallel Wiring Mismatch | bool | 0 = not active, 1=active | 406004.3 | 6003, 3
Contactor Trip Event | bool | 0 = not active, 1=active | 406004.4 | 6003, 4
Protection Firmware Trip | bool | 0 = not active, 1=active | 406004.5 | 6003, 5
Fan Failure | bool | 0 = not active, 1=active | 406004.6 | 6003, 6
Notifications (RO)
Notification | Data Type | Data Format | Modbus Device Register | Address
Automatic Thermal Derating Validity | bool | 0 = invalid, 1=valid | 406005.00 | 6004, 0
Low Order Harmonics Off Validity | bool | 0 = invalid, 1=valid | 406005.01 | 6004, 1
Unit Max Capacity Validity | bool | 0 = invalid, 1=valid | 406005.02 | 6004, 2
CT Is Clipping Validity | bool | 0 = invalid, 1=valid | 406005.03 | 6004, 3
Parallel ID conflict Validity | bool | 0 = invalid, 1=valid | 406005.13 | 6004,13
Parallel System Setup Mismatch Validity | bool | 0 = invalid, 1=valid | 406005.14 | 6004,14
Parallel Power Wiring Mismatch Validity | bool | 0 = invalid, 1=valid | 406005.15 | 6004,15
Automatic Thermal Derating | bool | 0 = not active, 1=active | 406006.00 | 6005, 0
Low Order Harmonics Off | bool | 0 = not active, 1=active | 406006.01 | 6005, 1
Unit Max Capacity | bool | 0 = not active, 1=active | 406006.02 | 6005, 2
CT Is Clipping | bool | 0 = not active, 1=active | 406006.03 | 6005, 3
Parallel ID conflict | bool | 0 = not active, 1=active | 406006.13 | 6005,13
Parallel System Setup Mismatch | bool | 0 = not active, 1=active | 406006.14 | 6005,14
Parallel Power Wiring Mismatch | bool | 0 = not active, 1=active | 406006.15 | 6005,15
New Unit Rating Applied Validity | bool | 0 = invalid, 1=valid | 406007.00 | 6006, 0
Unit Rating Mismatch Validity | bool | 0 = invalid, 1=valid | 406007.01 | 6006, 1
Firmware Version Mismatch Validity | bool | 0 = invalid, 1=valid | 406007.02 | 6006, 2
Parallel Version Mismatch Validity | bool | 0 = invalid, 1=valid | 406007.03 | 6006, 3
No Master Available Validity | bool | 0 = invalid, 1=valid | 406007.04 | 6006, 4
No CTs Configured Validity | bool | 0 = invalid, 1=valid | 406007.05 | 6006, 5
Line Not Qualified Validity | bool | 0 = invalid, 1=valid | 406007.06 | 6006, 6
Invalid configuration Validity | bool | 0 = invalid, 1=valid | 406007.07 | 6006, 7
HF Filter Contactor Trip Validity | bool | 0 = invalid, 1=valid | 406007.08 | 6006, 8
Unit Output is disabled Validity | bool | 0 = invalid, 1=valid | 406007.09 | 6006, 9
Power Save On Validity | bool | 0 = invalid, 1=valid | 406007.10 | 6006, 10
Unit Auto-Starting Validity | bool | 0 = invalid, 1=valid | 406007.11 | 6006, 11
Control Board Initialization In Progress Validity | bool | 0 = invalid, 1=valid | 406007.12 | 6006, 12
Contactor Not Closed Validity | bool | 0 = invalid, 1=valid | 406007.13 | 6006, 13
Waiting for Restart Validity | bool | 0 = invalid, 1=valid | 406007.14 | 6006, 14
New Unit Rating Applied | bool | 0 = not active, 1=active | 406008.00 | 6007, 0
Unit Rating Mismatch | bool | 0 = not active, 1=active | 406008.01 | 6007, 1
Firmware Version Mismatch | bool | 0 = not active, 1=active | 406008.02 | 6007, 2
Parallel Version Mismatch | bool | 0 = not active, 1=active | 406008.03 | 6007, 3
No Master Available | bool | 0 = not active, 1=active | 406008.04 | 6007, 4
No CTs Configured | bool | 0 = not active, 1=active | 406008.05 | 6007, 5
Line Not Qualified | bool | 0 = not active, 1=active | 406008.06 | 6007, 6
Invalid configuration | bool | 0 = not active, 1=active | 406008.07 | 6007, 7
HF FIlter Contactor Trip | bool | 0 = not active, 1=active | 406008.08 | 6007, 8
Unit Output is disabled | bool | 0 = not active, 1=active | 406008.09 | 6007, 9
Power Save On | bool | 0 = not active, 1=active | 406008.10 | 6007, 10
Unit Auto-Starting | bool | 0 = not active, 1=active | 406008.11 | 6007, 11
Control Board Initialization In Progress | bool | 0 = not active, 1=active | 406008.12 | 6007, 12
Contactor Not Closed | bool | 0 = not active, 1=active | 406008.13 | 6007, 13
Waiting for Restart | bool | 0 = not active, 1=active | 406008.14 | 6007, 14

## Measurements & Status
Unit Measurements (RO)
Parameter | Data Type | Data Format | Units | Modbus Device Register | Modbus Device Address
Total Load L1 | float32 |  | A | 402001 | 2000
Total Load L2 | float32 |  | A | 402003 | 2002
Total Load L3 | float32 |  | A | 402005 | 2004
Load Harmonics L1 | float32 |  | A | 402007 | 2006
Load Harmonics L2 | float32 |  | A | 402009 | 2008
Load Harmonics L3 | float32 |  | A | 402011 | 2010
Output Harm L1 | float32 |  | A | 402013 | 2012
Output Harm L2 | float32 |  | A | 402015 | 2014
Output Harm L3 | float32 |  | A | 402017 | 2016
Output Fundamental L1 | float32 |  | A | 402019 | 2018
Output Fundamental L2 | float32 |  | A | 402021 | 2020
Output Fundamental L3 | float32 |  | A | 402023 | 2022
Total Output L1 | float32 |  | A | 402025 | 2024
Total Output L2 | float32 |  | A | 402027 | 2026
Total Output L3 | float32 |  | A | 402029 | 2028
Source Current L1 | float32 |  | A | 402031 | 2030
Source Current L2 | float32 |  | A | 402033 | 2032
Source Current L3 | float32 |  | A | 402035 | 2034
Reactive Load Current | float32 |  | A | 402037 | 2036
Reactive Output Current | float32 |  | A | 402039 | 2038
Negative Sequence Load Current | float32 |  | A | 402041 | 2040
Negative Sequence Output Current | float32 |  | A | 402043 | 2042
Fundamental Current Req. L1 | float32 |  | A | 402045 | 2044
Fundamental Current Req L2 | float32 |  | A | 402047 | 2046
Fundamental Current Req. L3 | float32 |  | A | 402049 | 2048
Input Source Voltage (L-L) | float32 |  | V | 402051 | 2050
Input Source Frequency | float32 |  | Hz | 402053 | 2052
DC Bus Top | float32 |  | V | 402055 | 2054
DC Bus Bottom | float32 |  | V | 402057 | 2056
Control Board Temp | float32 |  | C | 402059 | 2058
IGBT L1 Temp | float32 |  | C | 402061 | 2060
IGBT L2 Temp | float32 |  | C | 402063 | 2062
IGBT L3 Temp | float32 |  | C | 402065 | 2064
Inlet Temp | float32 |  | C | 402067 | 2066
Unit Top Temp | float32 |  | C | 402069 | 2068
Inductor Temp | float32 |  | C | 402071 | 2070
Source THDi L1 | float32 |  | - | 402073 | 2072
Source THDi L2 | float32 |  | - | 402075 | 2074
Source THDi L3 | float32 |  | - | 402077 | 2076
Load THDi L1 | float32 |  | - | 402079 | 2078
Load THDi L2 | float32 |  | - | 402081 | 2080
Load THDi L3 | float32 |  | - | 402083 | 2082
Source THDv L1-L2 | float32 |  | - | 402085 | 2084
Source THDv L2-L3 | float32 |  | - | 402087 | 2086
Source THDv L3-L1 | float32 |  | - | 402089 | 2088
Load Fundamental Current L1 | float32 |  | A | 402091 | 2090
Load Fundamental Current L2 | float32 |  | A | 402093 | 2092
Load Fundamental Current L3 | float32 |  | A | 402095 | 2094
Source Fundamental Current L1 | float32 |  | A | 402097 | 2096
Source Fundamental Current L2 | float32 |  | A | 402099 | 2098
Source Fundamental Current L3 | float32 |  | A | 402101 | 2100
Fundamental Voltage L1-L2 | float32 |  | V | 402103 | 2102
Fundamental Voltage L2-L3 | float32 |  | V | 402105 | 2104
Fundamental Voltage L3-L1 | float32 |  | V | 402107 | 2106
Source Fundamental KVA | float32 |  | VA | 402109 | 2108
Source Fundamental KW | float32 |  | W | 402111 | 2110
Source Fundamental KVAR | float32 |  | VAR | 402113 | 2112
Load Fundamental KVA | float32 |  | VA | 402115 | 2114
Load Fundamental KW | float32 |  | W | 402117 | 2116
Load Fundametal KVAR | float32 |  | VAR | 402119 | 2118
Output Fundamental KVAR | float32 |  | VAR | 402121 | 2120
Displacement PF Source | float32 |  | - | 402123 | 2122
Displacement PF Load | float32 |  | - | 402125 | 2124
Total Load Neutral | float32 |  | A | 402127 | 2126
Load Harmonics Neutral | float32 |  | A | 402129 | 2128
Output Harm Neutral | float32 |  | A | 402131 | 2130
Output Fundamental Neutral | float32 |  | A | 402133 | 2132
Total Output Neutral | float32 |  | A | 402135 | 2134
Source Current Neutral | float32 |  | A | 402137 | 2136
Zero Sequence Load Current | float32 |  | A | 402139 | 2138
Zero Sequence Output Current | float32 |  | A | 402141 | 2140
Load Fundamental Current Neutral | float32 |  | A | 402143 | 2142
Source Fundamental Current Neutral | float32 |  | A | 402145 | 2144
Fundamental Current Req. Neutral | float32 |  | A | 402147 | 2146
Reactive Source Current | float32 |  | A | 402149 | 2148
Negative Sequence Source Current | float32 |  | A | 402151 | 2150
Zero Sequence Source Current | float32 |  | A | 402153 | 2152
Unit Top Temp Left | float32 |  | A | 402155 | 2154
Filter Resistor Temp | float32 |  | A | 402157 | 2156
Lifetime Unit Information (RO)
Parameter | Data Type |  | Units | Register | Address
Uptime | uint32 |  | s | 402501 | 2500
Total On Time | uint32 |  | s | 402503 | 2502
Total Run Time | uint32 |  | s | 402505 | 2504
Average Output L1 | float32 |  | A | 402507 | 2506
Average Output L2 | float32 |  | A | 402509 | 2508
Average Output L3 | float32 |  | A | 402511 | 2510
Parallel System Status (RO)
Parameter | Data Type |  | Units | Register | Address
System Available Capacity | float32 |  | A | 403001 | 3000
System Active Capacity | float32 |  | A | 403003 | 3002
System Output | float32 |  | A | 403005 | 3004
System Master ID | uint16 |  | - | 403007 | 3006
System Priority | uint16 |  | - | 403008 | 3007
Max output current of Unit ID 1 | float32 |  | A | 403009 | 3008
Max output current of Unit ID 2 | float32 |  | A | 403011 | 3010
Max output current of Unit ID 3 | float32 |  | A | 403013 | 3012
Max output current of Unit ID 4 | float32 |  | A | 403015 | 3014
Max output current of Unit ID 5 | float32 |  | A | 403017 | 3016
Max output current of Unit ID 6 | float32 |  | A | 403019 | 3018
Max output current of Unit ID 7 | float32 |  | A | 403021 | 3020
Max output current of Unit ID 8 | float32 |  | A | 403023 | 3022
Max output current of Unit ID 9 | float32 |  | A | 403025 | 3024
Max output current of Unit ID 10 | float32 |  | A | 403027 | 3026
Max output current of Unit ID 11 | float32 |  | A | 403029 | 3028
Max output current of Unit ID 12 | float32 |  | A | 403031 | 3030
Max output current of Unit ID 13 | float32 |  | A | 403033 | 3032
Max output current of Unit ID 14 | float32 |  | A | 403035 | 3034
Max output current of Unit ID 15 | float32 |  | A | 403037 | 3036
Max output current of Unit ID 16 | float32 |  | A | 403039 | 3038
Max output current of Unit ID 17 | float32 |  | A | 403041 | 3040
Max output current of Unit ID 18 | float32 |  | A | 403043 | 3042
Max output current of Unit ID 19 | float32 |  | A | 403045 | 3044
Max output current of Unit ID 20 | float32 |  | A | 403047 | 3046
Max output current of Unit ID 21 | float32 |  | A | 403049 | 3048
Max output current of Unit ID 22 | float32 |  | A | 403051 | 3050
Max output current of Unit ID 23 | float32 |  | A | 403053 | 3052
Max output current of Unit ID 24 | float32 |  | A | 403055 | 3054
Max output current of Unit ID 25 | float32 |  | A | 403057 | 3056
Paralel Status of Unit 1 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403059 | 3058
Paralel Status of Unit 2 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403060 | 3059
Paralel Status of Unit 3 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403061 | 3060
Paralel Status of Unit 4 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403062 | 3061
Paralel Status of Unit 5 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403063 | 3062
Paralel Status of Unit 6 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403064 | 3063
Paralel Status of Unit 7 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403065 | 3064
Paralel Status of Unit 8 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403066 | 3065
Paralel Status of Unit 9 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403067 | 3066
Paralel Status of Unit 10 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403068 | 3067
Paralel Status of Unit 11 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403069 | 3068
Paralel Status of Unit 12 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403070 | 3069
Paralel Status of Unit 13 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403071 | 3070
Paralel Status of Unit 14 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403072 | 3071
Paralel Status of Unit 15 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403073 | 3072
Paralel Status of Unit 16 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403074 | 3073
Paralel Status of Unit 17 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403075 | 3074
Paralel Status of Unit 18 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403076 | 3075
Paralel Status of Unit 19 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403077 | 3076
Paralel Status of Unit 20 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403078 | 3077
Paralel Status of Unit 21 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403079 | 3078
Paralel Status of Unit 22 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403080 | 3079
Paralel Status of Unit 23 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403081 | 3080
Paralel Status of Unit 24 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403082 | 3081
Paralel Status of Unit 25 | uint16 | 0=Offline, 1=Running, 2=Standby, 3=Stopped, 4=Event | - | 403083 | 3082

## Unit Configuration
Unit Class
Unit Class | uint16 | 0 = Active Harmonic Filter (AHF), 1= Electronic VAR Compensator (EVC) | - | 404100 | 4099
Unit Configurations (RO) | [5 empty] | Operating conditions (RO)
Parameter | Data Type | Data Format | Unit | Modbus Device Register | Address | Parameter | Data Type | Data Format | Modbus Device Register | Address
Unit Rating | float32 |  | A | 404001 | 4000 | System ON Valid | bool | 0 = invalid, 1=valid | 405001, 0 | 5000, 0
Derating Factor | float32 | Effective derating factor | - | 404003 | 4002 | Output Enabled Valid | bool | 0 = invalid, 1=valid | 405001, 1 | 5000, 1
Nominal Voltage | float32 |  | V | 404005 | 4004 | SIM Enabled Valid | bool | 0 = invalid, 1=valid | 405001, 2 | 5000, 2
Nominal Freq | float32 |  | Hz | 404007 | 4006 | Harm Mode En Valid | bool | 0 = invalid, 1=valid | 405001, 3 | 5000, 3
CT Configuration | uint16 | 0 = No CT, 1= 2 CTs, 2= 3 CTs | - | 404009 | 4008 | Load Balance (NS) Enabled Valid | bool | 0 = invalid, 1=valid | 405001, 4 | 5000, 4
CT Ratio | uint16 | e.g 3000 for (3000:5 CT or 3000:1 CT) | - | 404010 | 4009 | Load Balance (ZS) Enabled Valid | bool | 0 = invalid, 1=valid | 405001, 11 | 5000, 11
CT Secondary Rating | uint16 | 1 for 5A secondary CT, 0 for 1A secondary CT | - | 404011 | 4010 | System ON | bool | 0= OFF, 1= ON | 405002, 0 | 5001, 0
CT 1 Connection | uint16 | 0-5 (L1+, L1-, L2+, L2-, L3+, L3-), 31 = None | - | 404012 | 4011 | Output Enabled | bool | 0=OFF, 1=ON | 405002, 1 | 5001, 1
CT 2 Connection | uint16 | 0-5 (L1+, L1-, L2+, L2-, L3+, L3-), 31 = None | - | 404013 | 4012 | SIM Mode Enabled | bool | 0= OFF, 1= ON | 405002, 2 | 5001, 2
CT 3 Connection | uint16 | 0-5 (L1+, L1-, L2+, L2-, L3+, L3-), 31 = None | - | 404014 | 4013 | Harm Mode En | bool | 0= OFF, 1= ON | 405002, 3 | 5001, 3
CT 1 Cal | float32 |  | - | 404015 | 4014 | Load Balance (NS) Enabled | bool | k | 405002, 4 | 5001, 4
CT 2 Cal | float32 |  | - | 404017 | 4016 | Load Balance (ZS) Enabled | bool | 0= OFF, 1= ON | 405002, 11 | 5001, 11
CT 3 Cal | float32 |  | - | 404019 | 4018
Harmonic Priority | float32 |  | - | 404021 | 4020 | Other Configurations (RO)
Fundamental Priority | float32 |  | - | 404023 | 4022 | CT Position Valid | bool | 0 = invalid, 1=valid | 405001, 5 | 5000, 5
Reactive Mode | uint16 | 0=Disabled, 1=PF mode, 2=Vreg, 3=Reactive | - | 404025 | 4024 | AutoStart En.Valid | bool | 0 = invalid, 1=valid | 405001, 6 | 5000, 6
PF Target Value | float32 |  | - | 404026 | 4025 | Auto Detect En.Valid | bool | 0 = invalid, 1=valid | 405001, 7 | 5000, 7
Voltage Regulation Set Point | float32 |  | V | 404028 | 4027 | Parallel Rotation En. Valid | bool | 0 = invalid, 1=valid | 405001, 8 | 5000, 8
Voltage Regulator Gain | float32 |  | - | 404030 | 4029 | React Target Mode Valid | bool | 0 = invalid, 1=valid | 405001, 9 | 5000, 9
Reactive Target | float32 |  | A/VAR | 404032 | 4031 | Target THD type Valid | bool | 0 = invalid, 1=valid | 405001, 10 | 5000, 10
External Trans Grid Side Voltage Ratio | uint16 | e.g 690 for 690:470 transformer | - | 404034 | 4033 | CT Position | bool | 0=GRID, 1=LOAD | 405002, 5 | 5001, 5
External Trans Unit Side Voltage Ratio | uint16 | e.g 470 for 690:470 transformer | - | 404035 | 4034 | Auto Start En. | bool | 0=OFF, 1=ON | 405002, 6 | 5001, 6
External Trans Phase | uint16 | 0=0 deg, 1=30 deg, 2 = 60 deg, … | - | 404036 | 4035 | Auto Detect En. | bool | 0=OFF, 1=ON | 405002, 7 | 5001, 7
Parallel Configuration | uint16 | 0=Single Unit, 1=Network, 2=Legacy | - | 404037 | 4036 | Parallel Rotation Enabled | bool | 0=OFF, 1=ON | 405002, 8 | 5001, 8
Parallel Unit ID | uint16 |  | - | 404038 | 4037 | React Target Type | bool | 0=Amp, 1=VAR | 405002, 9 | 5001, 9
Parallel Priority Group | uint16 |  | - | 404039 | 4038 | Target THD type | bool | 0=THDi 1=THDv | 405002, 10 | 5001, 10
Parallel Rotation Time | float32 |  | s | 404040 | 4039
Auto Start Delay Time | float32 |  | s | 404042 | 4041
Fault Restart Delay Time | float32 |  | s | 404044 | 4043 | FW/SW Versions (RO)
Power Save On | float32 |  | - | 404046 | 4045 | Control DSP Version | uint16[5] | Character String XX.YY.ZZZZ | 409001 | 9000
Power Save Off | float32 |  | - | 404048 | 4047 | Reserved | uint16[11] | Character String | 409006 | 9005
Target THD | float32 |  | - | 404050 | 4049 | Protection DSP Version | uint16[5] | Character String XX.YY.ZZZZ | 409017 | 9016
[6 empty] | Reserved | uint16[11] | Character String | 409022 | 9021
[6 empty] | HMI Version | uint16[5] | Character String XX.YY.ZZZZ | 409033 | 9032
[6 empty] | Reserved | uint16[11] | Character String | 409038 | 9037

## Harmonic Spectrum
Parameter(s) | # elements | Data type | Unit | Access | Modbus Device Register |  | Descriptions
[5 empty] | Start | End
Spectrum Acquisition Command | 1 | uint16 | N/A | WO | 410001 | 410001 | This register is a Write-Only register and controls Spectrum acquisition and selects which data to record.
Write an integer between 1 and 9 to trigger a recording. Depending on the value, corresponding channel below will be recorded
[7 empty] | Control | Signal recorded | Signal Desc.
[7 empty] | 1 | VL1-L2 | L1-L2 Input Voltage
[7 empty] | 2 | VL2-L3 | L2-L3 Input Voltage
[7 empty] | 3 | VL3-L1 | L3-L1 Input Voltage
[7 empty] | 4 | Iload1 | Load Current of Phase L1
[7 empty] | 5 | Iload2 | Load Current of Phase L2
[7 empty] | 6 | Iload3 | Load Current of Phase L3
[7 empty] | 7 | Isrc1 | Source Current of Phase L1
[7 empty] | 8 | Isrc2 | Source Current of Phase L2
[7 empty] | 9 | Isrc3 | Source Current of Phase L3
After retrieving the measurement and no more measurements are to be taken, set this register back to 0, so the function can be used for another acquisition.
After retrieving the measurement and more measurements are to be taken, set this register back to next desired acquisition channel to immediately start a new acquisition.
Spectrum Acquisition State | 1 | uint16 | N/A | RO | 410002 | 411002 | This Read-Only register indicates the state of the Spectrum acquisition function
When this register equals 0. the Spectrum function is free; client can request new acquisition by writing to the command register.
During acquisition, this register will contain the channel number currently being acquired.
When acquisition is done, this register will contain a number which is the negative (2's complement) of the channel number last acquired.
In summary, provided State=0, start a new measurement by writing 1-9 to the Command register
Then wait until State is equal to the negative of the channel number, before reading the data.
e.g. if last command was 5, then wait for State becoming -5, before reading the channel.
If another channel needs to be captured, set the command to the channel to immediately start a new acquisition.
If no more channels need to be captured, set the command to 0 to free interface for other devices.
Spectrum Acquisition Sequence Number | 1 | uint16 |  | RO | 410003 | 410003 | This register contains a free-running 32-bit counter that gets incremented by 1, every time a new measurement acquisition is started and is completed (i.e. ready to be read).
Use this register to further bullet-proof multi-client access system, in order to detect possibility of near simultaneous command from more than one clients.
Harmonic Spectrum Data | [6 empty] | When an acquisition completes, harmonic spectrum data can be found in the following registers:
Note: First harmonic (H1) frequency corresponds to the fundamental AC input voltage frequency (e.g. 50Hz or 60Hz)
Harmonic Spectrum Magnitudes H1 to H51 | 51 | float32 | amps/volts | RO | 410004 | 410104 | These 51 x 32-bit registers contain magnitude data in 32-bit floating point amps or volts
of the signal selected by the Command register (410001) defined above for Harmonic 1 to Harmonic 51
Magnitude H1 | 1 | float32 | amps/volts | RO | 410004 | 410005
Magnitude H2 | 1 | float32 | amps/volts | RO | 410006 | 410007
... | ... | ... | ... | ... | ...
Magnitude H51 | 1 | float32 | amps/volts | RO | 410104 | 410105
Harmonic Spectrum Phase Angles H1 to H51 | 51 | float32 | degree | RO | 410106 | 410206 | These 51 x 32-bit registers contain phase angle data in 32 bit floating point degree
of the signal selected by the Command register (410001) defined above for Harmonic 1 to Harmonic 51
Phase Angle H1 | 1 | float32 | degree | RO | 410106 | 410107
Phase Angle H2 | 1 | float32 | degree | RO | 410108 | 410109
... | ... | ... | ... | ... | ...
Phase angle H51 | 1 | float32 | degree | RO | 410206 | 410207

## Scope Waveform
Parameter(s) | # elements | Data type | Unit | Access | Modbus Device Register |  | Descriptions
[5 empty] | Start | End
Waveform Acquisition Command | 1 | uint16 | N/A | WO | 411001 | 411001 | This register is a Write-Only register and controls waveform acquisition and selects which data to record.
Write an integer between 1 and 9 to trigger a recording. Depending on the value, corresponding channel below will be recorded
[7 empty] | Control | Signal recorded | Signal Desc.
[7 empty] | 1 | VL1-L2 | L1-L2 Input Voltage
[7 empty] | 2 | VL2-L3 | L2-L3 Input Voltage
[7 empty] | 3 | VL3-L1 | L3-L1 Input Voltage
[7 empty] | 4 | Iload1 | Load Current of Phase L1
[7 empty] | 5 | Iload2 | Load Current of Phase L2
[7 empty] | 6 | Iload3 | Load Current of Phase L3
[7 empty] | 7 | Isrc1 | Source Current of Phase L1
[7 empty] | 8 | Isrc2 | Source Current of Phase L2
[7 empty] | 9 | Isrc3 | Source Current of Phase L3
[7 empty] | 10 | Iout1 | Output Current of Phase L1
[7 empty] | 11 | Iout2 | Output Current of Phase L2
[7 empty] | 12 | Iout2 | Output Current of Phase L3
[7 empty] | 13 | Iref1 | Reference Current of Phase L1
[7 empty] | 14 | Iref2 | Reference Current of Phase L2
[7 empty] | 15 | Iref3 | Reference Current of Phase L3
[7 empty] | 16 | VDCBus | DC Bus Voltage
After retrieving the measurement and no more measurements are to be taken, set this register back to 0, so the function can be used for another acquisition.
After retrieving the measurement and more measurements are to be taken, set this register back to next desired acquisition channel to immediately start a new acquisition.
Waveform Acquisition State | 1 | uint16 | N/A | RO | 411002 | 411002 | This Read-Only register indicates the state of the waveform acquisition function
When this register equals 0. the waveform function is free; client can request new acquisition by writing to the command register.
During acquisition, this register will contain the channel number currently being acquired.
When acquisition is done, this register will contain a number which is the negative (2's complement) of the channel number last acquired.
In summary, provided State=0, start a new measurement by writing 1-9 to the Command register
Then wait until State is equal to the negative of the channel number, before reading the data.
e.g. if last command was 5, then wait for State becoming -5, before reading the channel.
If another channel needs to be captured, set the command to the channel to immediately start a new acquisition.
If no more channels need to be captured, set the command to 0 to free interface for other devices.
Waveform Acquisition Sequence Number | 1 | uint16 |  | RO | 411003 | 411003 | This register contains a free-running 32-bit counter that gets incremented by 1, every time a new measurement acquisition is started and is completed (i.e. ready to be read).
Use this register to further bullet-proof multi-client access system, in order to detect possibility of near simultaneous command from more than one clients.
Waveform Data 1 to 256 | 256 | float32 | amps or volts | RO | 411004 | 411514 | When an acquisition completes, these 256 x 32-bit registers will contain current (A) or voltage (V) data
in 32-bit floating-point format of the signal selected by the Command register (411001) defined in the above table.
Data1 | 1 | float32 | amps or volts | RO | 411004 | 411005 | The data is sampled at the rate of 128 times the AC input voltage frequency
Data2 | 1 | float32 | amps or volts | RO | 411006 | 411007 | For example in 50Hz system, the data sample time is 156.25 usec (1/50/128)
Data3 | 1 | float32 | amps or volts | RO | 411008 | 411009 | The entire 256 data therefore represent 2 cycle worth of waveform data
Data4 | 1 | float32 | amps or volts | RO | 411010 | 411011
Data5 | 1 | float32 | amps or volts | RO | 411012 | 411013
... | ... | ... | ... | ... | ... | ...
... | ... | ... | ... | ... | ... | ...
Data255 | 1 | float32 | amps or volts | RO | 411512 | 411513
Data256 | 1 | float32 | amps or volts | RO | 411514 | 411515

## Legacy
THE FOLLOWING REGISTER DEFINITIONS CORRESPOND TO LEGACY PRODUCT AND ARE DEPRECIATED.
They should not be used in new applications. They may be removed in future firmware revisions
System Measurements (RO)
Parameter | Data Type | Data Format | Modbus Device Register | Address
AC Line Voltage | UINT | 16Bits – volts (RMS) | 400001 | 0
Total Load A | UINT | 16Bits – amperes (RMS) | 400002 | 1
Total Load B | UINT | 16Bits – amperes (RMS) | 400003 | 2
Total Load C | UINT | 16Bits – amperes (RMS) | 400004 | 3
Output Harmonics A | UINT | 16Bits – amperes (RMS) | 400005 | 4
Output Harmonics B | UINT | 16Bits – amperes (RMS) | 400006 | 5
Output Harmonics C | UINT | 16Bits – amperes (RMS) | 400007 | 6
Load Harmonics A | UINT | 16Bits – amperes (RMS) | 400008 | 7
Load Harmonics B | UINT | 16Bits – amperes (RMS) | 400009 | 8
Load Harmonics C | UINT | 16Bits – amperes (RMS) | 400010 | 9
Reactive (PF) Load | INT | 16Bits – amperes (RMS) | 400011 | 10
Reactive (PF) Output | INT | 16Bits – amperes (RMS) | 400012 | 11
DC Bus Voltage | INT | 16Bits – volts (DC) | 400013 | 12
Circuit Board Temp. | UINT | 16Bits – degrees Celcius | 400014 | 13
IGBT Temp (Note 1) | UINT | 16Bits– degrees Celcius | 400015 | 14
IGBT A Temp (Note 2) | UINT | 16Bits– degrees Celcius | 400015 | 14
IGBT C Temp (Note 2) | UINT | 16Bits– degrees Celcius | 400016 | 15
AC Line Frequency | UINT | 16Bits – Hertz x 100 | 400017 | 16
Output Fund. A | UINT | 16Bits – amperes (RMS) | 400018 | 17
Output Fund. B | UINT | 16Bits – amperes (RMS) | 400019 | 18
Output Fund. C | UINT | 16Bits – amperes (RMS) | 400020 | 19
Total Output A | UINT | 16Bits – amperes (RMS) | 400021 | 20
Total Output B | UINT | 16Bits – amperes (RMS) | 400022 | 21
Total Output C | UINT | 16Bits – amperes (RMS) | 400023 | 22
Grid Current A | UINT | 16Bits – amperes (RMS) | 400024 | 23
Grid Current B | UINT | 16Bits – amperes (RMS) | 400025 | 24
Grid Current C | UINT | 16Bits – amperes (RMS) | 400026 | 25
Load Negative Seq. | UINT | 16Bits – amperes (RMS) | 400027 | 26
Output Negative Seq. | UINT | 16Bits – amperes (RMS) | 400028 | 27
Fund. Current Req’d A | UINT | 16Bits – amperes (RMS) | 400029 | 28
Fund. Current Req’d B | UINT | 16Bits – amperes (RMS) | 400030 | 29
Fund. Current Req’d C | UINT | 16Bits – amperes (RMS) | 400031 | 30
Harmonic Analysis (RO)
Parameter | Data Type | Data Format | Modbus Device Register | Address
Selected Order for analysis (n_select). | UINT | 1 to 49 | 400061 | 60
Vab magnitude at | UINT | 16Bits – volts | 400062 | 61
n_select – th harmonic
Vab angle at | UINT | 16Bits – degree | 400063 | 62
n_select – th harmonic
Vbc magnitude at | UINT | 16Bits – volts | 400064 | 63
n_select – th harmonic
Vbc angle at | UINT | 16Bits – degree | 400065 | 64
n_select – th harmonic
Iload A magnitude at | UINT | 16Bits – amps | 400066 | 65
n_select – th harmonic
Iload A angle at | UINT | 16Bits – degree | 400067 | 66
n_select – th harmonic
Iload B magnitude at | UINT | 16Bits – amps | 400068 | 67
n_select – th harmonic
Iload B angle at | UINT | 16Bits – degree | 400069 | 68
n_select – th harmonic
Igrid A magnitude at | UINT | 16Bits – amps | 400070 | 69
n_select – th harmonic
Igrid A angle at | UINT | 16Bits – degree | 400071 | 70
n_select – th harmonic
Igrid B magnitude at | UINT | 16Bits – amps | 400072 | 71
n_select – th harmonic
Igrid B angle at | UINT | 16Bits – degree | 400073 | 72
n_select – th harmonic
Harmonic Analysis Command (WO)
Parameter | Data Type | Format | Modbus Device Register | Address
Requested Order for Harmonic Analysis (n_select) | UINT | 1 to 49 | 401201 | 1200
Apply requested order for analysis | UINT | 0-to-1 or 1-to-0 = APPLY | 401202 | 1201
System Information (RO)
Parameter | Data Type | Data Format | Modbus Device Register | Address
Unit Rating | UINT | 16Bits – amperes (RMS) | 400101 | 100
Int. Xfmr. – AF side voltage | UINT | 16Bits – volts | 400102 | 101
Int. Xfmr. – Grid side voltage | UINT | 16Bits – volts | 400103 | 102
Unit Configuration (RO)
Parameter | Data Type | Format | Modbus Device Register | Address
Nominal Voltage | UINT | 16Bits – volts (RMS) | 400401 | 400
Nominal Frequency | UINT | 16Bits - Hertz | 400402 | 401
No. of 50A units | UINT | 16Bits | 400403 | 402
No. of 100A units | UINT | 16Bits | 400404 | 403
No. of 300A units | UINT | 16Bits | 400405 | 404
CT Ratio | UINT | 16Bits – amperes Per 5V | 400406 | 405
CT Position | UINT | 0= LOAD, 1=GRID | 400407 | 406
Four Wire System | UINT | 0= NO, 1= YES | 400408 | 407
PF cos(phi) | INT | 0 to 100 - percent | 400409 | 408
+ or – (LAG or LEAD)
Harmonic Priority | UINT | 0 to 100 – percent | 400410 | 409
Fundamental Priority | UINT | 0 to 100 – percent | 400411 | 410
Auto Start | UINT | 0=OFF, 1=ON | 400412 | 411
Auto Start Delay | UINT | 16 bits – seconds | 400413 | 412
Fault Restart Delay | UINT | 16 bits – seconds | 400414 | 413
Power Save On | UINT | 0 to 100 – percent | 400415 | 414
Power Save Off | UINT | 0 to 100 – percent | 400416 | 415
Derating Factor | UINT | 0 to 100 – percent | 400417 | 416
Auto Detect | UINT | 0=OFF, 1=ON | 400418 | 417
Ext. Xfmr. – AF side voltage | UINT | 16Bits – volts | 400419 | 418
Ext. Xfmr. – Grid side voltage | UINT | 16Bits – volts | 400420 | 419
Ext. Xfmr. – Phase Shift | UINT | 0 to 9 | 400421 | 420
(0, -30, -60, -120, -150,
180, +150, +120, +60, +30)
Input 1 CT Connection | UINT | 0 to 5 | 400422 | 421
(A+, A-, B+, B-, C+, C-)
Input 2 CT Connection | UINT | 0 to 5 | 400423 | 422
(A+, A-, B+, B-, C+, C-)
Input 3 CT Connection | UINT | 0 to 5 | 400424 | 423
(A+, A-, B+, B-, C+, C-)
Input 1 CT Calibration | UINT | 16Bits - Gain x 1000 | 400425 | 424
Input 2 CT Calibration | UINT | 16Bits - Gain x 1000 | 400426 | 425
Input 3 CT Calibration | UINT | 16Bits - Gain x 1000 | 400427 | 426
Output Modes (RO)
Parameter | Data Type | Format | Modbus Device Register | Address
Harmonic Mode | UINT | 0= OFF, 1= ON | 400501 | 500
PF Mode | UINT | 0= OFF, 1= ON | 400502 | 501
Load Balancing Mode | UINT | 0= OFF, 1= ON | 400503 | 502
Simulation Mode | UINT | 0= OFF, 1= ON | 400504 | 503
Operating Status (RO)
Parameter | Data Type | Format | Modbus Device Register | Address
Run/Stop Status | UINT16 | 0= stop, 1=running | 400701 | 700
Enable Remote | UINT16 | 0=OFF, 1=ON | 400702 | 701
Control Commands (WO)
Parameter | Data Type | Format | Modbus Device Register | Address
Run/Stop Command | UINT16 | 0-to-1: RUN | 401001 | 1000
1-to-0: STOP
(see Note 1)
Reset/Acknowledge Alarm or Faults | UINT16 | 0-to-1 or 1-to-0 = RESET/ACK | 401002 | 1001
Parameter | Data Type | Old Definitions (in PCS) | New Definitions (in PCS+) | Modbus Device Register | Address
Critical Faults | UINT16 | BIT 0: (5V OV Fault) | BIT 0: 24V PS Fault | 40601 | 600
(faults which cause unit to stop) |  | BIT 1: (5V UV Fault) | BIT 1: 25V PS Fault
|  | BIT 2: (+15V UV Fault) | BIT 2:4.8V PS Fault
|  | BIT 3: (-15V UV Fault) | BIT 3:Current Sense PS Fault
|  | BIT 4: User Setup Fault | BIT 4: User Setup Fault
|  | BIT 5: Fault Time Out; | BIT 5: Fault Time Out;
|  | BIT 6: Auto Detect Fault | BIT 6: Auto Detect Fault
|  | BIT 7: HMI Lost Fault | BIT 7: HMI Lost Fault
|  | BIT 8: Invalid Rating | BIT 8: Invalid Rating
|  | BIT 9: Phase Rotation Fault | BIT 9: N/A in PCS+
Non Critical Fault 1 | UINT16 | BIT 0: AC Line Loss Fault | BIT 0: AC Line Loss Fault | 40602 | 601
|  | BIT 1: AC Phase Loss Fault | BIT 1: AC Phase Loss Fault
|  | BIT 2: AC Imbalance Fault | BIT 2: AC Imbalance Fault
|  | BIT 3: AC Over Voltage Fault | BIT 3: AC Over Voltage Fault
|  | BIT 4: AC Freq Error Fault | BIT 4: AC Freq Error Fault
|  | BIT 5: Sensor Fault | BIT 5: Sensor Fault
|  | BIT 6: Frequency Fault - N/A in PCS+ | BIT 6: Frequency Fault - N/A in PCS+
|  | BIT 7: IGBT A Fault | BIT 7: IGBT A Fault
|  | BIT 8: IGBT B Fault | BIT 8: IGBT B Fault
|  | BIT 9: IGBT C Fault | BIT 9: IGBT C Fault
|  | BIT 10: IGBT1 Over Temp Fault | BIT 10: IGBT1 Over Temp Fault
|  | BIT 11: IGBT2 Over Temp Fault | BIT 11: IGBT2 Over Temp Fault
|  | BIT 12: IGBT3 Over Temp Fault | BIT 12: IGBT3 Over Temp Fault
|  | BIT 13: 3 Ph Over Temp Fault | BIT 13: 3 Ph Over Temp Fault
|  | BIT 14: Filter Fault | BIT 14: Filter Fault
|  | BIT 15: Enclosure OT Fault | BIT 15: Enclosure OT Fault
Non Critical Fault 2 | UINT16 | BIT 0: DC Bus Over Voltage Fault | BIT 0: DC Bus Over Voltage Fault | 40603 | 602
|  | BIT 1: DC Bus Low Voltage Fault | BIT 1: DC Bus Low Voltage Fault
|  | BIT 2: Enclosure Under Temp Fault | BIT 2: Enclosure Under Temp Fault
|  | BIT 3: 110C Over Temp Fault | BIT 3: 110C Over Temp Fault
|  | BIT 4: Circuit Board Over Temp Fault | BIT 4: Circuit Board Over Temp Fault
Alarm Status | UINT16 | BIT 0: Max Capacity Alarm | BIT 0: Max Capacity Alarm | 40604 | 603
|  | BIT 1: Thermal Limit Override | BIT 1: Thermal Limit Override
|  | BIT 2: Low Order Harmonic Alarm | BIT 2: Low Order Harmonic Alarm