## P111
MiCOM Manual Formula
Curve | IEC Standard Inverse Time (SI) | Select Curve Type From Drop Down List
t | 15.1394 | operating time in seconds (Calculated)
k | 0.14 | Constant
P | 1 | Constant
c | 0 | Constant
G | 200 | Measured Current in A
TD | 2 | Time dial setting for IEEE Curves
Gs | 80 | Current Threshold setting
a | 0.02 | Constant
| Type of Curve | k | c | a | P
| IEC Standard Inverse Time (SI) | 0.14 | 0 | 0.02 | 1
| IEC Very Inverse Time (VI) | 13.5 | 0 | 1 | 1
| IEC Extremely Inverse Time (EI) | 80 | 0 | 2 | 1
| IEC Long Time Inverse | 120 | 0 | 1 | 1
| IEEE Moderately Invertime Time (MI) | 0.0515 | 0.114 | 0.02 | 1
| IEEE Very Inverse Time (VI) | 19.61 | 0.491 | 2 | 1
| IEEE Extremely Inverse Time (EI) | 28.2 | 0.1217 | 2 | 1
| US Time Inverse (CO8) | 5.95 | 0.18 | 2 | 1
| US Short Time Inverse (CO2 P20) | 0.02394 | 0.01694 | 0.02 | 1
| US Short Time Inverse (CO2 P40) | 0.16758 | 0.11858 | 0.02 | 1
| RI | -4.2373 | 0 | 1 | 1.4364