## ANSI-51_IEC
SEPAM Relay Trip Curve Calculator
Instructions:
1. Enter relay settings (current setting or pickup amps, time delay, and curve shape) in the yellow cells B20-B22 below.
2. Enter the planned test current in the yellow cell B24
3. The expected trip time, in seconds, shows up in the blue cell B28
Curve Shape | Curve ID | k | a | b
IEC Standard Inverse (SIT) | 1 | 0.14 | 0.02 | 2.97
IEC Very Inverse (VIT) | 2 | 13.5 | 1 | 1.5
IEC Long-Time Inverse (LIT) | 3 | 120 | 1 | 13.33
IEC Extremely Inverse (EIT) | 4 | 80 | 2 | 0.808
IEC Ultra-Inverse (UIT) | 5 | 315.2 | 2.5 | 1
Relay Settings
Current Setting (Is) | 1200 | "Threshold Current" from the SEPAM file |  |  | Current Transformer Input Impedance < 0.02
Time Delay (T) | 0.3 | Enter in Seconds |  |  | 1 A or 5 A CT (with CCA630 or CCA634) Burden < 0.02 VA at 1 A
Curve Shape (Enter ID#) | 4 | See Curve ID column above |  |  | 1 A to 6250 A Ratings < 0.5 VA at 5 A
CT Ratio | 240 |  |  |  | Rated Thermal Withstand 4 IN
Test Current | 3600 |  | 15 | Secondary Test Set Injection | 1-Second Overload 100 IN
calc k | 80 |  |  |  | Voltage Transformer Input Impedance > 100 k
calc a | 2 |  |  |  | 220 V to 250 kV Ratings Input Voltage 100 to 230/√3 V
calc b | 0.808 |  |  |  | Rated Thermal Withstand 240 V | 3.8985 | 3.7379 | 0.16064
Expected Trip Time | 3.7129 | Seconds |  |  | 1-Second Overload 480 V | 3.5272 | 3.7029 | 0.17564
Positive Trip Tolerance | 3.8985 | Seconds
Negative Trip Tolerance | 3.5272 | Seconds

## ANSI-51_IEEE
SEPAM Relay Trip Curve Calculator
Instructions:
1. Enter relay settings (current setting or pickup amps, time delay, and curve shape) in the yellow cells B20-B22 below.
2. Enter the planned test current in the yellow cell B22
3. The expected trip time, in seconds, shows up in the blue cell B27
Curve Shape | Curve ID | A | B | b | p
IEEE Moderately Inverse | 1 | 0.01 | 0.023 | 0.241 | 0.02
IEEE Very Inverse | 2 | 3.922 | 0.098 | 0.138 | 2
IEEE Extremely Inverse | 3 | 5.64 | 0.0243 | 0.081 | 2
Relay Settings
Current Setting (Is) | 1200 | "Threshold Current" from the SEPAM file
Time Delay (T) | 0.67 | Enter in Seconds |  |  |  | Current Transformer Input Impedance < 0.02
Curve Shape (Enter ID#) | 1 | See Curve ID column above |  |  |  | 1 A or 5 A CT (with CCA630 or CCA634) Burden < 0.02 VA at 1 A
CT Ratio | 1200 |  |  |  |  | 1 A to 6250 A Ratings < 0.5 VA at 5 A
Test Current Primary | 4800 |  | 4 | Secondary Test Set Injection |  | Rated Thermal Withstand 4 IN
calc A | 0.01 |  |  |  |  | 1-Second Overload 100 IN
calc B | 0.023 |  |  |  |  | Voltage Transformer Input Impedance > 100 k
calc b | 0.241 |  |  |  |  | 220 V to 250 kV Ratings Input Voltage 100 to 230/√3 V
calc p | 0.02 |  |  |  |  | Rated Thermal Withstand 240 V
Expected Trip Time | 1.0528 | Seconds |  |  |  | 1-Second Overload 480 V | 1.1054 | 1.0778 | 0.02764
Positive Trip Tolerance | 1.1054 | Seconds |  |  |  |  | 1.0002 | 1.0428 | 0.04264
Negative Trip Tolerance | 1.0002 | Seconds

## ANSI-51_IAC
SEPAM Relay Trip Curve Calculator
Instructions:
1. Enter relay settings (current setting or pickup amps, time delay, and curve shape) in the yellow cells B20-B22 below.
2. Enter the planned test current in the yellow cell B22
3. The expected trip time, in seconds, shows up in the blue cell B29
Curve Shape | Curve ID | A | B | C | D | E | b
IAC Inverse | 1 | 0.208 | 0.863 | 0.8 | -0.418 | 0.195 | 0.297
IAC Very Inverse | 2 | 0.09 | 0.795 | 0.1 | -1.288 | 7.958 | 0.165
IAC Extremely Inverse | 3 | 0.004 | 0.638 | 0.62 | 1.787 | 0.246 | 0.092
Relay Settings
Current Setting (Is) | 200 | "Threshold Current" from the SEPAM file
Time Delay (T) | 0.1 | Enter in Seconds |  |  |  |  | Current Transformer Input Impedance < 0.02
Curve Shape (Enter ID#) | 3 | See Curve ID column above |  |  |  |  | 1 A or 5 A CT (with CCA630 or CCA634) Burden < 0.02 VA at 1 A
CT Ratio | 40 | [5 empty] | 1 A to 6250 A Ratings < 0.5 VA at 5 A
Test Current | 400 |  | 10 | Secondary Test Set Injection |  |  | Rated Thermal Withstand 4 IN
calc A | 0.004 | [5 empty] | 1-Second Overload 100 IN
calc B | 0.638 | [5 empty] | Voltage Transformer Input Impedance > 100 k
calc C | 0.62 | [5 empty] | 220 V to 250 kV Ratings Input Voltage 100 to 230/√3 V
calc D | 1.787 | [5 empty] | Rated Thermal Withstand 240 V
calc E | 0.246 | [5 empty] | 1-Second Overload 480 V | 1.71 | 1.6536 | 0.056428
calc b | 0.092 | [6 empty] | 1.5471 | 1.6186 | 0.071428
Expected Trip Time | 1.6286 | Seconds
Positive Trip Tolerance | 1.71 | Seconds
Negative Trip Tolerance | 1.5471 | Seconds

## ANSI-51_RI
SEPAM Relay Trip Curve Calculator
Instructions:
1. Enter relay settings (current setting or pickup amps, time delay, and curve shape) in the yellow cells B20-B22 below.
2. Enter the planned test current in the yellow cell B24
3. The expected trip time, in seconds, shows up in the blue cell B28
Relay Settings
Current Setting (Is) | 200 | "Threshold Current" from the SEPAM file |  |  | Current Transformer Input Impedance < 0.02
Time Delay (T) | 0.1 | Enter in Seconds |  |  | 1 A or 5 A CT (with CCA630 or CCA634) Burden < 0.02 VA at 1 A
1 A to 6250 A Ratings < 0.5 VA at 5 A
CT Ratio | 40 |  |  |  | Rated Thermal Withstand 4 IN
Test Current | 400 |  | 10 | Secondary Test Set Injection | 1-Second Overload 100 IN
Voltage Transformer Input Impedance > 100 k
220 V to 250 kV Ratings Input Voltage 100 to 230/√3 V
[5 empty] | Rated Thermal Withstand 240 V | 0.14985 | 0.16771 | -0.017864
Expected Trip Time | 0.14271 | Seconds |  |  | 1-Second Overload 480 V | 0.13558 | 0.13271 | -0.0028643
Positive Trip Tolerance | 0.16771 | Seconds
Negative Trip Tolerance | 0.13271 | Seconds

## ANSI-49
ANSI 49 - Thermal Overload
Motors/Generators/Transformers
Generic Thermal Model
Ib | 2 | Base Current (Secondary) | K Calculator for an Asychronous Motor
Iph | 4 | Greatest measured phase current | Cd | 1000 | Starting Torque
K | 1 | Adjustable Factor | Cn | 500 | Rated Torque
NSF (Ii) | 4.5 | Negative sequence factor | g | 0.1 | Rated Slip
Es2 | 1.1 | Heat rise tripping set point, service factor squared | Id | 100 | Starting Current
Tau 1 | 24 | Heating time constant (minutes) | Ib | 90 | Basis Current
Tau 2 | 70 | Cooling time constant (Minutes) | K | 31.4 | Adjust factor
Es0 | 0 | Initial heat rise value
tc | 186.3389 | Time to Trip, cold (Seconds)
th
Two Constant Thermal Model
Tau 1 |  | Motor Thermal Time Constant
Tau 2 |  | Motor Cooling Time Constant
HSC |  | Hot State Current
TSC |  | Rotor/Stator thermal state change threshold
CS |  | Cold Stalling Time
WS |  | Warm Stalling Time
LRT |  | Locked Rotor Torque
SC |  | Starting Current