## Database Growth
[PME][Calculator]Database Growth Calculator
Power Monitoring Expert 8
| Annual Database Growth (GB) | 0 | GB
| Years of Data in the Database | 0 | Years
Instructions
1. Add the numbers of device types in the following table. Green cells are configurable.
2. Devices with waveforms will typically contribute approximately 10% - 20% to the total size of the database, depending on the frequency of power quality events.
| Waveform Contribution (%) | 10%
3. During normal operation the database will grow by 10% when more room is needed and should be accounted for in estimations. It can be modified or disabled in SQL Server Management Studio.
| Database Growth (%) | 10%
4. Adjust the maximum database size (if desired) that can fit on the hard drive to see how many years of data can be held in the database.
| Maximum Database Size (GB) | 50
Device Range | Device Type | Daily Growth Rate (kB) | Has Waveforms | Number of Devices | Total Daily Growth (kB) | Detect Waveforms
Utility Meter | ION8800A | 560 | Yes | 0 | 0 | 0
| ION8800A (with IEC 61000-4-30) | 745 | Yes | 0 | 0 | 0
| ION8800B | 560 | No | 0 | 0 | 0
| ION8800B (with IEC 61000-4-30) | 680 | No | 0 | 0 | 0
| ION8800C | 30 | No | 0 | 0 | 0
| ION8650A | 525 | Yes | 0 | 0 | 0
| ION8650A (with IEC 61000-4-30) | 710 | Yes | 0 | 0 | 0
| ION8650B | 525 | Yes | 0 | 0 | 0
| ION8650B (with IEC 61000-4-30) | 645 | Yes | 0 | 0 | 0
| ION8650C | 30 | No | 0 | 0 | 0
| ION8600A | 525 | Yes | 0 | 0 | 0
| ION8600B | 525 | Yes | 0 | 0 | 0
| ION8600C | 30 | No | 0 | 0 | 0
Advanced Meter | ION7650 | 565 | Yes | 0 | 0 | 0
| ION7650 (with IEC 61000-4-30) | 780 | Yes | 0 | 0 | 0
| ION7550 | 545 | Yes | 0 | 0 | 0
| CM4000 series | 800 | Yes | 0 | 0 | 0
Intermediate Meter | PM8000 | 950 | Yes | 0 | 0 | 0
| CM3000 series | 765 | Yes | 0 | 0
| PM870 | 110 | Yes | 0 | 0 | 0
| PM850 | 110 | Yes | 0 | 0 | 0
| PM820 | 85 | No | 0 | 0 | 0
| PM810 | 140 | No | 0 | 0 | 0
| PM810 (PM810LOG) | 85 | No | 0 | 0 | 0
| ION7350 | 410 | Yes | 0 | 0 | 0
| ION7330 | 195 | No | 0 | 0 | 0
| ION7300 | 0 | No | 0 | 0 | 0
Multi Circuit Meter | BCPM (42 circuits) | 1060 | No | 0 | 0 | 0
| EM4800-24 | 2900 | No | 0 | 0 | 0
| EM4800-12 | 2220 | No | 0 | 0
| EM4800-08 Wye | 1830 | No | 0 | 0
| EM4800-08 Delta | 1830 | No | 0 | 0
| EM4800-12 ckt | 950.4 | No | 0 | 0
| EM4800-24 ckt | 691.2 | No | 0 | 0
| EM4800-8 ckt Delta | 345.6 | No | 0 | 0
| EM4800-8 ckt WYE | 864 | No | 0 | 0 | 0
| EnerSure BCPM/iBCPM | 3649 | No | 0 | 0
Basic Meter | PM5350 | 225 | No | 0 | 0 | 0
| PM700 series | 45 | No | 0 | 0 | 0
| PM3200 series | 85 | No | 0 | 0 | 0
| ION6200 | 60 | No | 0 | 0 | 0
| PM200 | 45 | No | 0 | 0 | 0
| CM100_200 | 216 | No | 0 | 0
| EM3460 | 108 | No | 0 | 0
| EM3550 | 43.2 | No | 0 | 0
| EM3555 | 57.6 | No | 0 | 0
| EnerceptMeter | 172.8 | No | 0 | 0
| PM3250 | 86.4 | No | 0 | 0
| PM3255 | 108 | No | 0 | 0
| PM5100 | 144 | No | 0 | 0
| PM5300 | 158.4 | No | 0 | 0
| PM5350 Busway | 208.8 | No | 0 | 0
| PM5350_PB_IB | 208.8 | No | 0 | 0
| PM5500 | 230.4 | No | 0 | 0
| WT4000 series | 0 | No | 0 | 0
Entry Meter | EM1000 | 100.8 | No | 0 | 0 | 0
| EM1200 | 50 | No | 0 | 0 | 0
| EM4200 | 197 | No | 0 | 0
| EM6400 | 108 | No | 0 | 0 | 0
| EM6400 NG | 141 | No | 0 | 0
| EM6430 | 79.2 | No | 0 | 0
| EM6433 | 50.4 | No | 0 | 0
| EM6434 | 57.6 | No | 0 | 0
| EM6436 | 79.2 | No | 0 | 0
| EM6436 Dual | 93.6 | No | 0 | 0
| EM6438 | 36 | No | 0 | 0
| EM6459 | 57.6 | No | 0 | 0
| iEM3x50 | 36 | No | 0 | 0
| iEM3x55 | 72 | No | 0 | 0
| iEM2000 series | 70 | No | 0 | 0
| PM1200 / DM6200 | 50 | No | 0 | 0
| PM9c | 170 | No | 0 | 0
Circuit Breaker Trip Unit | Micrologic H | 350 | Yes | 0 | 0 | 0
| Micrologic P | 350 | No | 0 | 0 | 0
| Micrologic E | 295 | No | 0 | 0 | 0
| Micrologic A | 70 | No | 0 | 0 | 0
| Micrologic Compact NSX E | 170 | No | 0 | 0 | 0
| Micrologic Compact NSX A | 170 | No | 0 | 0 | 0
Protection Relays | Sepam series 80 | 565 | Yes | 0 | 0 | 0
| Sepam series 40 and 48 | 270 | Yes | 0 | 0 | 0
| Sepam series 20 | 50 | Yes | 0 | 0 | 0
| Sepam series 10 | 40 | No | 0 | 0 | 0
Power Factor Correction Devices | Accusine PCS+ | 3263 | No | 0 | 0 | 0
| Accusine PFV+ | 225 | No | 0 | 0 | 0
| VarPlus Logic | 49 | No | 0 | 0 | 0
Others | MGE Galaxy UPS | 170 | No | 0 | 0 | 0
| Symmetra MW UPS | 110 | No | 0 | 0 | 0
| Vigilohm IM20-H | 55 | No | 0 | 0 | 0
| Bender LIM-IG6 | 300 | No | 0 | 0 | 0
TOTAL |  |  |  | 0 | 0 | 0
Custom Measurement Logging
Bytes / Measurement | Number of Measurements | Logging Frequency (seconds) |  |  | Total Daily Growth (kB)
75 | 0 | 900 |  |  | 0
75 | 0 | 300 |  |  | 0
75 | 0 | 1 |  |  | 0
TOTAL | 0 |  |  |  | 0
Notes
1. Devices with IEC 61000-4-30 only have 10 minute and 2 hour logging enabled. IEC 61000-4-30 3 second logging must be enabled manually and will contribute 14.4 MB of logs per day.
2. EN50160 (weekly logging) contributes approximately 2 kB per day.
3. Some default factory device drivers do not have PC-logging enabled. PC-logging must be enabled manually using the Modbus Device Importer.