## Sheet1
MCB | Type | Tightening Torque
iC60H Circuit Breaker | 1 to 25 A | 2 Nm
iC60H Circuit Breaker | 32 to 63 A | 3.5 Nm
iC60H RCBO | N in and L in | 3.5 Nm
iC60H RCBO | L out and N out | 2 Nm
Vigi iC60 add-on RCD | 25 A | 2 Nm
Vigi iC60 add-on RCD | 40 to 63A | 3.5 Nm
iID RCCB | iID | 3.5 Nm
Electrical auxiliaries for | Indication auxiliaries | 1 Nm
iC60, iID, iDPN Vigi, RCA and ARA
Electrical auxiliaries for | Tripping auxiliaries | 1 Nm
iC60, iID, iDPN Vigi, RCA and ARA
Accessories for | Multi-cable terminal | 2 Nm
iC60, iID, iDPN Vigi, Reflex iC60, RCA, ARA, iSW
Accessories for | 50 mm² terminal Al | 10 Nm
iC60, iID, iDPN Vigi, Reflex iC60, RCA, ARA, iSW
Accessories for | Screw-on connection for ring terminal | 2 Nm
iC60, iID, iDPN Vigi, Reflex iC60, RCA, ARA, iSW
iDPN circuit breakers | DT40, i DPN, C40 | 2 Nm
iDPN circuit breakers | DT60 | 3.5 Nm
iDPN Vigi RCD | 4 to 40 A | 2 Nm
iC120H circuit breakers | 63 to 125 A | 3.5 Nm
Vigi iC120 add-on RCD | Vigi C120 | 3.5 Nm
Accessories for | Multi-cable terminal | 2 Nm
iC120, DPN, DPN Vigi, C60H-DC, SW60-DC, C60NA-DC, C60PV-DC, iSW devices
Accessories for | 50 mm² Al terminal | 10 Nm
iC120, DPN, DPN Vigi, C60H-DC, SW60-DC, C60NA-DC, C60PV-DC, iSW devices
Accessories for | Screw-on connection for ring terminal | 2 Nm
iC120, DPN, DPN Vigi, C60H-DC, SW60-DC, C60NA-DC, C60PV-DC, iSW devices
Electrical auxiliaries for | Indication and tripping auxiliaries | 1 Nm
iC120, DPN, DPN Vigi, ID, C60H-DC, SW60-DC, C60PV-DC, C60NA-DC devices
P25M Load protection Motor starter protection | P25M | 1.7 Nm
P25M Load protection Motor starter protection | Electrical auxiliaries | 1.4 Nm
iPRD surge arresters | iPRD | 3.5 Nm
iQuick PRD Withdrawable surge arrester | iQuickPRD | 2.5 Nm
iPRD-DC surge arresters | iPRD-DC | 2 Nm
REDs, REDtest Earth leakage protection Automatic recloser | REDs, REDtest N, L | 2 Nm
REDs, REDtest Earth leakage protection Automatic recloser | REDs, REDtest Aux | 0.4 Nm
RED A type 30mA Earth leakage protection Automatic recloser | RED A type 30 mA 25 to 40A | 2 Nm
Reflex iC60H Control, remote control Integrated control circuit breakers | Power Connection 10 to 25 A | 2 Nm
Reflex iC60H Control, remote control Integrated control circuit breakers | Power Connection 40 to 63A | 3.5 Nm
Reflex iC60H Control, remote control Integrated control circuit breakers | Power supply (N/P) & Inputs (Y1/Y2) | 1 Nm
Reflex iC60H Control, remote control Integrated control circuit breakers | Outputs (O/C, auto/OFF) | 0.7 Nm
ARA automatic reclosers For iC60 CB and iID RCCB | Power supply (N/P) & Inputs (Y1/Y2) | 1 Nm
ARA automatic reclosers For iC60 CB and iID RCCB | Outputs (OF/Locked) | 0.7 Nm
RCA remote controls For iC60 CB | Power supply (N/P) & Inputs (Y1/Y2) | 1 Nm
RCA remote controls For iC60 CB | Outputs (OF) | 0.7 Nm
Acti 9 smartlink | Analog connector | 0.8 Nm
Acti 9 smartlink | Power supply connector | 0.8 Nm
Acti 9 smartlink | Modbus connector | 0.8 Nm
iCT contactors | iCT Control Circuit | 0.8 Nm
iCT contactors | iCT Power Circuit 16 and 25 A | 0.8 Nm
iCT contactors | iCT Power Circuit 40 to 63 and 100 A | 3.5 Nm
iCT contactors | iACTs, iACTp, iACTc, iATEt | 0.8 Nm
iCT contactors | iACT24 Power supply (N/P) & Input (Y1/Y2) | 1 Nm
iTL impulse relays | iTL, iTLi, iTLc, iTLm, iTLs, iETL 16 A Power and Control | 1 Nm
iTL impulse relays | iTL, iETL 32 A Control | 1 Nm
iTL impulse relays | iTL, iETL 32 A Power | 1.2 Nm
iTL impulse relays | iATLs, iATLc, iATLc+s, iATLc+c, iATLm, iATEt, iATL4, iATLz | 1 Nm
iTL impulse relays | ATL24 Power supply (N/P) & Inputs (Y1/Y2) | 1 Nm
iTL+ high-performance impulse relays | TL+ | 1 Nm
iIL indicator lights | iIL | 1 Nm
iPB pushbuttons | iPB | 1 Nm
iSW switches | iSW 40 to 125 A | 3.5 Nm
iSW switches | iCF | 1 Nm
iSW switches | iSW 22 and 32 A | 1.2 Nm
iSW switches | OF iSW | 1.2 Nm
iSSW linear switches | iSSW | 1 Nm
iTR transformers | iTR | 0.5 Nm
iSO bells and iRO buzzers | iSO | 1.3 Nm
STI isolatable fuse carriers | STI | 2 Nm
SBI fuse holder with indicator light | 14 x 51 mm & 22 x 58 mm | 3.5 Nm
DIN rail selector switches iCMB, iCMD, iCME, iCMC, iCMV and iCMA | iCMB, iCMD, iCME, iCMC, iCMV and iCMA | 0.35 Nm
Timers MIN, MINs, MINp and MINt | MIN, MINs, MINp, MINt | 1.2 Nm
Time switches IHP, IH, IHH and ITA | IHP, IH, IHH and ITA | 1.2 Nm
Twilight switches IC100, IC2000P+ | IC100, IC2000P+ | 1.2 Nm
MCCB
NS630b-NS1600 | Compact NS 630a-1600a | 50 Nm with contact washer
NS1600-NS3200 | Compact NS 1600a-3200a | 50 Nm with contact washer
NSX100 | Compact NSX & Compact NSX new generation | 10 Nm
NSX160-NSX250 | Compact NSX & Compact NSX new generation | 15 Nm
NSX400-NSX630 | Compact NSX & Compact NSX new generation | 50 Nm
Compact NS | Compact NS80H | 5 Nm
Compact NS | Compact NS100 Lugs/Bars on CB | 10 Nm
Compact NS | Compact NS100 rear connections | 5 Nm
Compact NS | Compact NS160-250 Lugs/Bars on CB | 15 Nm
Compact NS | Compact NS160-250 rear connections | 5 Nm
Compact NS | Compact NS400-630 Lugs/Bars on CB | 50 Nm
Compact NS | Compact NS400-630 rear connections | 20 Nm
Compact NS | Compact NS100 with spreaders/terminal extension on CB | 10 Nm
Compact NS | Compact NS100 with spreaders/terminal extension on rear connection | 5 Nm
Compact NS | Compact NS160-250 with spreaders/terminal extension on CB | 15 Nm
Compact NS | Compact NS160-250 with spreaders/terminal extension on rear connection | 5 Nm
Compact NS | Compact NS400-630 with spreaders/terminal extension on CB | 50 Nm
Compact NS | Compact NS400/630 with spreaders/terminal extension on rear connection | 50 Nm
ACB
MTZ1 | Masperpact MTZ1 630a-1600a | 50 Nm with contact washer
MTZ2 | Masterpact MTZ2 800a-4000a | 50 Nm with contact washer
MTZ3 | Masterpact MTZ3 4000a-6300a | 50 Nm with contact washer
NW | Masterpact NW 630a-6000a | 50 Nm
NT | Masterpact NT 630A-1600a | 50 Nm
SQD |  | Single Cable torque | Multi cable torque
Easy9 MCB | Easy9 3a-25a | 2 Nm | 4 Nm
Easy9 MCB | Easy9 32a-50a | 3.5 Nm | 4 Nm
quickline/Resi9/Resi9 MCB | quickline/Resi9 3a-25a | 2 Nm | 4 Nm
quickline/Resi9 MCB | quickline/Resi9 32a-63a | 3.5 Nm | 4 Nm
ikQ MCB | iKQ 3a-25a | 2 Nm | 4 Nm
ikQ MCB | iKQ 32a-63a | 3.5 Nm | 4 Nm
Eas9 RCBO | Easy9 6a-50a | 2 Nm | 2 Nm
quickline/Resi9 RCBO | quickline/Resi9 6a-45a | 2 Nm | 2 Nm
IkQ RCBO | iKQ 6a-45a | 2 Nm | 2 Nm
I-line
SFA | SFA 16a-32a | 4 Nm
SFA | SFA 40a-100a | 9 Nm
CDAE | CDAE 16a-100a | 10 Nm
CDXAE | CDXAE 16a-100a | 10 Nm
CNAE | CNAE 16a-100a | 10 Nm
CNAE | CNAE 125a-250a | 15 Nm
CNXAE | CNXAE 16a- 100a | 10 Nm
CNXAE | CNXAE 125a-250a | 15 Nm
CHAE | CHAE 16a-100a | 10 Nm
CHAE | CHAE 125a-250a | 15 Nm
CHXAE | CHXAE 16a-100a | 10 Nm
CHXAE | CHXAE 125a-250a | 15 Nm
SLA | SLA 250a-400a | 33 Nm
SMA | SMA 300a-800a | 33 Nm
PJA | PJA 400a-1200a | 50 Nm
|  | Terminal Torque | Fuse Torque
Quadbreak Single Phase & Switched | Switch disconnector 63a | 10 Nm | 8 Nm
Quadbreak Single Phase & Switched | Switch disconnector Fuse 63a | 10 Nm | 8 Nm
Quadbreak Single Phase & Switched | Switch Disconnector 100a-160a | 25 Nm | 10 Nm
Quadbreak Single Phase & Switched | Switch disconnector Fuse 100a-160a | 25 Nm | 10 Nm
Quadbreak Single Phase & Switched | Switch disconnector 200a-250a | 40 Nm | 14 Nm
Quadbreak Single Phase & Switched | Switch disconnector Fuse 200a-250a | 40 Nm | 14 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector 63a | 10 Nm | 8 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector Fuse 63a | 10 Nm | 8 Nm
Quadbreak 3 phase with neutral Link | Switch Disconnector 100a-160a | 25 Nm | 10 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector Fuse 100a-160a | 25 Nm | 10 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector 200a-250a | 40 Nm | 14 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector Fuse 200a-250a | 40 Nm | 14 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector 315a-630a | 40 Nm | 26 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector Fuse 315a-630a | 40 Nm | 26 Nm
Quadbreak 3 phase with neutral Link | Switch disconnector 800a | 40 Nm | N/A
|  | Neutral Connection | Neutral link | Fuse Links
Twin break SP&N | Switch disconnector 20a-32a | 2 Nm | 2 Nm | 2 Nm
Twin break SP&N | Switch disconnector fuse 20a-32a | 2 Nm | 2 Nm | 2 Nm
Twin break SP&N | Switch disconnector 63a-100a | 3.5 Nm | 2 Nm | 2 Nm
Twin break SP&N | Switch disconnector fuse 63a-100a | 3.5 Nm | 2 Nm | 2 Nm
Twin break TP&N | Switch disconnector 20a-32a | 2 Nm | 2.5 Nm | 2 Nm
Twin break TP&N | Switch disconnector fuse 20a-32a | 2 Nm | 2.5 Nm | 2 Nm
Twin break TP&N | Switch disconnector 63a-100a | 3.5 Nm | 3.5 Nm | 2 Nm
Twin break TP&N | Switch disconnector fuse 63a-100a | 3.5 Nm | 3.5 Nm | 2 Nm
Twin break TP&N | Switch disconnector 125a-160a | 4.5 Nm | 4.5 Nm | 2 Nm