## Analog Inputs
SL | Object Type | Instance Id | Object Name | Unit | Default COV | Object Discription | Comments
3 | Analog Input | AI2700 | Active Energy Delvd | kWh | 100 | Active energy delivered
4 | Analog Input | AI2702 | Active Energy Rcvd | kWh | 100 | Active energy received
5 | Analog Input | AI2708 | Reactive Energy Delvd | kVARh | 100 | Reactive energy delivered
6 | Analog Input | AI2710 | Reactive Energy Rcvd | kVARh | 100 | Reactive energy received
10 | Analog Input | AI2716 | Apparent Energy Delvd | kVAh | 100 | Apparent energy delivered
11 | Analog Input | AI2718 | Apparent Energy Rcvd | kVAh | 100 | Apparent energy received
13 | Analog Input | AI3060 | Active Power - Total | kW | 10 | Active power total
14 | Analog Input | AI3068 | Reactive Power - Total | kVAR | 10 | Reactive power total
15 | Analog Input | AI3076 | Apparent Power - Total | kVA | 10 | Apparent power total
16 | Analog Input | AI3084 | Power Factor - Total |  | 0.2 | Power Factor Total
17 | Analog Input | AI3026 | Voltage - Avg L-L | Volts | 10 | Voltage L-L Avg
18 | Analog Input | AI3036 | Voltage - Avg L-N | Volts | 10 | Voltage L-N Avg
19 | Analog Input | AI3010 | Current - Avg | Amps | 50 | Current average
20 | Analog Input | AI3110 | Frequency | Hz |  | Frequency
21 | Analog Input | AI3766 | Dmd - Active Power Present | kW | 10 | Demand - Active power present
22 | Analog Input | AI3782 | Dmd - Reactive Power Present | kVAR | 10 | Demand - Reactive power present
23 | Analog Input | AI3798 | Dmd - Apparent Power Present | kVA | 10 | Demand - Apparent power present
24 | Analog Input | AI3770 | Dmd - Active Power Peak | kW | 10 | Demand - Active power peak
25 | Analog Input | AI3786 | Dmd - Reactive Power Peak | kVAR | 10 | Demand - Reactive power peak
26 | Analog Input | AI3802 | Dmd - Apparent Power Peak | kVA | 10 | Demand - Apparent power peak
27 | Analog Input | AI3814 | Dmd - Current Ph A Present | Amps | 50 | Demand - Current phase A present
28 | Analog Input | AI3830 | Dmd - Current Ph B Present | Amps | 50 | Demand - Current phase B present
29 | Analog Input | AI3846 | Dmd - Current Ph C Present | Amps | 50 | Demand - Current phase C present
30 | Analog Input | AI3862 | Dmd - Current Neutral Present | Amps | 50 | Demand - Current phase C present
31 | Analog Input | AI3818 | Dmd - Active Current Ph A Peak | Amps | 50 | Demand - Active current phase A peak
32 | Analog Input | AI3834 | Dmd - Active Current Ph B Peak | Amps | 50 | Demand - Active current phase B peak
33 | Analog Input | AI3850 | Dmd - Active Current Ph C Peak | Amps | 50 | Demand - Active current phase C peak
34 | Analog Input | AI3054 | Active Power - Ph A | kW | 10 | Active power phase A
35 | Analog Input | AI3056 | Active Power - Ph B | kW | 10 | Active power Phase B
36 | Analog Input | AI3058 | Active Power - Ph C | kW | 10 | Active power phase C
37 | Analog Input | AI3062 | Reactive Power - Ph A | kVAR | 10 | Reactive Power Phase A
38 | Analog Input | AI3064 | Reactive Power - Ph B | kVAR | 10 | Reactive Power Phase B
39 | Analog Input | AI3066 | Reactive Power - Ph C | kVAR | 10 | Reactive Power Phase C
40 | Analog Input | AI3070 | Apparent Power - Ph A | kVA | 10 | Apparent Power Phase A
41 | Analog Input | AI3072 | Apparent Power - Ph B | kVA | 10 | Apparent Power Phase B
42 | Analog Input | AI3074 | Apparent Power - Ph C | kVA | 10 | Apparent Power Phase C
43 | Analog Input | AI3078 | Power Factor - Ph A |  | 0.2 | Power Factor Phase A
44 | Analog Input | AI3080 | Power Factor - Ph B |  | 0.2 | Power Factor Phase B
45 | Analog Input | AI3082 | Power Factor - Ph C |  | 0.2 | Power Factor Phase C
46 | Analog Input | AI3020 | Voltage - A-B | Volts | 10 | Voltage A-B
47 | Analog Input | AI3022 | Voltage - B-C | Volts | 10 | Voltage B-C
48 | Analog Input | AI3024 | Voltage - C-A | Volts | 10 | Voltage C-A
49 | Analog Input | AI3028 | Voltage A-N | Volts | 10 | Voltage A-N
50 | Analog Input | AI3030 | Voltage B-N | Volts | 10 | Voltage B-N
51 | Analog Input | AI3032 | Voltage C-N | Volts | 10 | Voltage C-N
52 | Analog Input | AI3000 | Current - Ph A | Amps | 50 | Current Phase A
53 | Analog Input | AI3002 | Current - Ph B | Amps | 50 | Current Phase B
54 | Analog Input | AI3004 | Current - Ph C | Amps | 50 | Current Phase C

## Binary Inputs
SL | Object Type | Instance Id | Object Name | Unit | Object Discription | Comments
1 | Binary Input | BI38416 | Status Input 1 | NA | Status of Status Input 1 0 = on 1 = off
2 | Binary Input | BI38417 | Status Input 2 | NA | Status of Status Input 2 0 = on 1 = off
3 | Binary Input | BI38448 | Relay Output | NA | Status of Relay output 0 = on 1 = off