## Gen 1 InRow300mm
MODELS: ACSC100, ACSC101
Description | APC PN#
***USC Special Orders | QAIRDIST
1U 19" Black Modular Toolless Airflow Management Blanking Panel - Qty 10 | AR8136BLK
1U 19" Black Modular Toolless Airflow Management Blanking Panel - Qty 200 | AR8136BLK200
1U Airflow Management Blanking Panel Kit [Qty 2] Black | AR8108BLK
TERMINAL PLUG 3 POSITION SCREW [connection for contacts] | 730-0280
3 WAY VALVE - 3/4" NOMINAL [GOES WITH W0M-61028] | 875-4229A
3WAY VALVE UNION 3/4" C X M [GOES WITH 875-4229A/W0M-61028] | 875-0877
TERMINAL PLUG 8 POSITION SCREW [connection for contacts] | 715-0368
ASSY CORR BD TWF06 ROHS | 0P9028A
BAYING BRACKET NETSHELTER SX | 870-11538
BAYING BRACKET SCREW M5 X 12 FLT UCUT PHIL M5 X 12 BLK [for baying kit] | 803-5006A
BOX ASSY for DUCT KIT ACSC 5KW | 0M-61250
Bridge Partition, Data Cable 300 MM | ACAC10005
Bridge Trough, Power Cable 300 MM Cover | ACAC10008
Bridge Trough, Power Cable Shield 300 MM | ACAC10001
CABLE ASSY THERMISTOR/PROBE EMU 13 FT ASSY [PURPLE Rack Inlet] | 0J-0W2818A
CABLE ASSY THERMISTOR/PROBE EMU 8 FT ASSY [All Sensors but Rack Inlet] | 0J-0W3163A
CABLE TIE SET IR REPLACEMENTS | W0H-0125
CAP MTL PPR 400V 5% 40UF RD [compressor] | W234-1406
CAP MTL PPR 450V 50UF WITH TAP - SPARE PART | W234-0051
CAP MTL PPR 450V 55UF WITH TAP [compressor] [default][sepersedes W234-0556 ] | W234-0500
CASTER STEEL 2" RIGID DARKSTAR [rear] | 870-6620
CASTER SWIVEL 650 LBS 2.8IN OH [front][supersedes] | AR7719
CAT5 CABLE, BLACK, RJ45M TO RJ45M, 24 AWG, [25ft. Cat5e cable for grouping] | 3827BK-25
Ceiling Tile Adapter 24" - Spare Part | W870-80333
Ceiling Tile Adapter 600mm - Spare Part | W870-80336
COMP Assy, SC, ROTARY 208-230/1/60 [Toshiba conversion kit] | W0H-0170
COMP Assy, SC, ROTARY 220-240/1/50 [Toshiba conversion kit] | W0H-0171
COMP, ROTARY 208-230/1/60, SC, TOSHIBA - SPARE PART [compressor only] | W875-3825
COMP, ROTARY 220-240/1/50 SC, TOSHIBA - SPARE PART [compressor only] | W875-3826
COMPLETE 801 PCB CRAC MB [main board w/o additional cards] | W0P2340
COMPLETE 802 PCB CRAC PWR BACKPLANE [for rectifiers] | W0P2341
OHE board for ACRD | w0p2570
COMPLETE 805 PCB CRAC 2X DP [differential pressure board] | W0P2354
COMPLETE 879 PCB XA SIMM [XAS1 card] | W0P2342
COMPLETE NMC W/CAN [Network Manangement Card] | WAP9517CAN
COMPLETE PCB ASSY, Motherboard W/SIMM AND Mini-Rhodes [complete board set] | 0J-0P2670AB
Compressor Wiring Harness [FSB ] | W0W3418
Condensate Float Switch Bulk Mount 4"MNL | 0N-0279A
CONDENSATE PAN BOTTOM | 870-80022
CONDENSATE PAN GATE - FLOAT | 870-80033
CONDENSATE PUMP ASSY - 17 KW IR 120V/230V - [AutoSelect] | W0N-7166
CONDENSATE PUMP ASSY W/HOSES [formerly - 0N-0993SE] | 0J-0011
INROW CONDENSATE PUMP ASSEMBLY (24VDC) | 0N-1308
CONDENSATE PUMP FITTING BARBED [Y barb fittings] .13"X.13"X.13" [inlet for Dual Condensate Pump] | 875-4367
CONDENSATE PUMP FITTING BARBED [Y barb fittings] .19"X.19"X.19" [outlet for Dual Condensate Pump] | 875-4368
CONDENSATE PUMP TUBE PVC .125IN ID .250IN OD [18" long PVC TUBE for 875-4367] | 875-0481
CONDENSATE PUMP TUBE PVC .188IN ID .313IN OD [18" long PVC TUBE for 875-4368] | 875-0857B
CONDENSATE PUMP TUBE PVC .625IN ID .750OD [2.3 FEET [700 MM] LONG] | 875-0482
CONDENSATE PUMP WIRE ASSY CP JUMPER [for activation without the water sensor kit] | 0W3133
Condenser Coil | 875-0948
CONDENSER COIL ASSY SC5 | 0M-61169
Condenser Fan 200mm Mixed Flow [INDIVIDUAL FAN] | W490-0079
CONNECTOR SET 17KW IR SPARES for Jumper | W0H-0127
COVER PROTECTIVE ELECTRICAL THERMO SHEET [cover for the e-box] | 870-80068
Cover, Bridge Trough, Power Cable 300 MM | ACAC10008
DC RECTIFIER, 500 WATT, 54VDC - [RECTIFIER / FAN POWER SUPPLY] [NEW RELEASE][SE] | 0J-920-0090
DC RECTIFIER, 500 WATT, 54VDC - [RECTIFIER / FAN POWER SUPPLY] [OLD RELEASE] [APC] | W920-0082
DC RECTIFIER, 500 WATT, 54VDC - [RECTIFIER / FAN POWER SUPPLY] [ANCIENT RELEASE] [Honeycomb] | W1TWF0500H54B
DIVIDER-'A' DUCT KIT ACSC 5KW 48ECT BC NKRAFT | 871-3527
DIVIDER-'B' DUCT KIT ACSC 5KW 48ECT BC NKRAFT | 871-3528
Door Key - Spare Part | W870-8135
DUCTING KIT 24 INCH IR5 [0M-61250 assy pn#] | 0M-61152
ELECTRONIC EXPANSION VALVE Harness [HBGP harness] | 0W4409
ELECTRONIC EXPANSION VALVE, 3/8" ODF [HGBP] | W875-4275
EVAPORATOR COIL HALF RACK 5KW | 875-0017
EVAPORATOR FAN MODULE ASSY - 17 KW IR - 17 KW IR [EVAP] | W0M-61005
EXT PRESSURE SENSOR PORT [black sensor the filter dp tube plugs into] | 870-80061
FAN FUSE NTC COMPLETE 818 PCB CRAC | 0P2390
FILTER - IR SERIES 1/2" THK WASHABLE - SPARE PART [Standard] | W875-2010
FILTER - PRINTING IR SERIES 2 IN THK PLEATED [Non-Washable] | W0B1657
FILTER-DRIER 3/8"ODF SOLDER | W875-2085
FITTING 1/8" BARB 10-32 [FILTER FITTING TUBE CONNECTING TO FRAME] | 870-80064
FITTING 1/8" BARB TEE [for air differential pressure switch] | 870-80066
Flex Pipe Kit 1" MPT to 1" FPT Union [Between equipment and piping] 3ft. Stainless | ACAC10011
Flex Pipe Kit 1" MPT to 1" FPT Union [Between equipment and piping] 6ft Stainless | ACAC10012
Flexible Fluid Piping - 100 Feet [30.4 Meters] | ACAC20003
Flexible Fluid Piping - 300 Feet [91.4 Meters] | ACAC20002
Flexible Fluid Piping Clamp/Hanger | ACAC20007
Flexible Fluid Piping Clamp/Hanger [qty of 50] | ACAC20008
Flexible Fluid Piping Couplings [4 per pack] [875-4308 is the individual pn#] | ACAC20006
Flexible Fluid Piping Insulation - 100 Feet [30.4 Meters] | ACAC20005
Flexible Fluid Piping Insulation - 300 Feet [91.4 Meters] | ACAC20004
Flexible Fluid Piping Strut Mounted Clamp | ACAC20009
FLOAT SWITCH BULK MOUNT 1" F/O [for condensate pan] | W0N-0279
FLOAT SWITCH, BULKHEAD MOUNT [single float] | 540-0205
FLOW METER GRUNFOS [new flowmeter] | 0J-0N-0303B
FM TOOK KIT DRIVER BIT COMBO TORX T20/T30 [FOR FM TOOL FOR KIT PN# 0M-5383] | 815-0001
FM TOOL KIT Assy | 0M-5383
FM TOOL KIT HANDLE 1/4" DRIVE [FOR FM TOOL FOR KIT PN# 0M-5383] | 815-0002
FM TOOL KIT POUCH [FOR FM TOOL FOR KIT PN# 0M-5383] | 815-0003
FOOT LEVELING M10 [QTY 4] | 825-0035
Front Door Assembly - Spare Part | W0M-61085
GROMMET 1-3/4ID 1/16GW 1-15/16GD; 2-5/16OD 7/16OT [FOR EXTERNAL PIPING] | 827-0207
GROMMET 3/8ID 7/8OD 5/8GD SBR 5 [FOR EXTERNAL DRAIN] | 827-0084
GROMMET PLUG SPLIT 1/2" ID 1 3/4" OD [CAP FOR 827-0207] | 827-0233
GROMMET RUBBER 1 1/2"ID X 1 3/4"GD X 1/8"GW [for power cable at the bottom] | 827-0219
HI PRESSURE SWITHCH OPENS 550PSIG CLOSES 450PSIG - SPARE PART | W541-0087
INSERT SIDE DUAL SIDE PANEL 42U SX | 871-2935
JUMPER Line PHASE SELECT | 0W3268
LABEL HOLD FOR FAILURE ANALYSIS | 885-3997
LATCH FLUSH SLAM W/TUMBLE [FOR DOOR IN USE WITH W840-0220] | W840-0192-333
LATCH SNAP-IN PUSH-TO-CLOSE [FOR DOOR IN USE WITH W840-0192-333] | W840-0220
Leak Sensor - 20 ft [6.1 m] [ships with orange sensor [AP9326] & black Cat5e cable][300mm Only] | AP9325
PEN TOUCH-UP PAINT FOR RAVEN BLACK | 690-0108-001
PLUG HOLE "SNAP" PLSTC 2.0" HEYCO P/N 2783 [for non used piping connections top/bottom] | 827-0208
PLUG PRY-OUT BLK NYLON 15.9MM DIA HEYCO [for non used drain piping top/bottom] | 827-0097
POWERVIEW Display [a.k.a. thermostat, display, controller, interface, control pad] | WAP9233
PWR CORD IEC-C19 FEM TO L6-20P LCDI [formally - W960-0126] | W0W4787
Pwr Cord, 16A, 200-240V, C19 to L6-20 | AP9871
REAR DOOR ASSY | W0M-61004
Relay Coil 250V 25A DPNO 24DC [compressor relay] | W450-0024
RELAY DPDT 120VAC 8A PC MOUNT | 450-0302
RELAY PWR SPDT 16A/250V 20A/125V NO 24V | 450-0012A
Roof Height Adapter, SX42U to SX48U 300 MM | ACAC10007
Roof Height Adapter, SX42U to VX42U 300 MM | ACAC10003
SIDE PANEL ASSY - IR SERIES | W0M-61031
STRAIN RELIEF HEYCO SR 7N-2 [for control box] | 652-07N2
TEFLONRINGS FOR ROTO 1" - SPARE PART [for Receiver] | W875-4291
TELECOUPLNG 8P8C RJ45 STRAIGHT [ethernet telecoupler] | W750-0034
TERMINATOR ROHS EXT BATT COMM BOARD [for A-Link] | 0J-0W04161A
THERMISTOR NTC 10 OHM 4A T/R [Resistor for BMS] | 160-0104-Z
RES CF AX 150ohm 5% 350ppm 0.25W | 110-0151-Z
TRANSDUCER PRESSURE 2CP5 - SPARE PART [Same for Suction and Discharge] | W875-3400
Transformer ISOLATION1:1.3 MAX253 | 430-0244
DUCT TUBE 6 FT 10" DIA FLEX [Condenser] | 875-0922A
TUBING PVC CLEAR 0.25ID | 660-7001D
TXV 1/2"ODM X 5/8" ODF EXTENDED, R410A 3 TON - SPARE PART [W875-4357] | 0J-875-4357A
TXV VALVE 3/8"ODM X 5/8" ODF R410A 1.5 TON | w875-1002
Wire Assembly Base | W0W3287
WIRE ASSY SC5 COMPRESSOR [for FSB AT0093GB001] | W0W3418
WIRE ASSY SC5 LOWER PWR FEED MB | 0W3288A
WIRE ASSY SC5 PRESSURE SENSING | 0W3293B
WIRE ASSY SC5 PSU/CP PWR/48VDC OUT | 0W3290A
WIRE ASSY SC5 UPPER PWR FEED MB | 0W3291A
WIRE CLIP - BLACK [ HOLDS SENSORS] | 870-13220
ASSY AIR COOLED INLET/OUTLET PIPING [subassy of Ship loose piping] | 0M-61375
INSULATION BLACK ADHESIVE [KIT INSULATION ACRD1XX 10KW SHIP LOOSE] | 690-0137
KIT ACRD 10KW AIR COOLED SHIP LOOSE PIPES | 0H-0226
KIT ACRD 10KW FLUID COOLED SHIP LOOSE PIPES | 0H-0227
UNION - 1" C (TAILPIECE) X F (BODY) [FSB AT0108GB01 Inlet-outlet fitting] | w875-4353
ACRD100 Nameplate Label | 885-90369A
Note on A30: APC-MGE: compressor, fd, cap, suction & disharge pipes
Note on A31: APC-MGE: compressor, fd, cap, suction & disharge pipes
Note on A50: Raymond Mills: APC-MGE: qty 7.8 (ft) - 1/8" PVC tube for 0P2354 DP card
Note on A51: APC-MGE: qty 9 (ft) - pump outlet
Note on B61: ACRC1xx YK0844xxxxxx ACSC100/101 YK0815xxxxxx ACRD 1xx/2xx all build dates; The only requirement is that the old and new design power supplies are not to be intermixed in the same unit. That is, use in pairs of old or new, but not one of each.
Note on A90: APC-MGE:ACRC1xx YK0847xxxxxx, plus; YK0842210428, YK0842210435 & YK0842210438
Note on A104: APC-MGE: DCA Requests pack of 100
Note on A130: APC-MGE: qty .167 (ft) - pump inlet