## Register List
Category | Sub Cat 1 | Sub Cat 2 | Description | PM5500 | Register | Units | Size (INT16) | Data Type | Access | Range | Default | NV | User Notes
System Setup & Status |  |  |  | Y | 1 | --- |  | --- | --- | --- | --- | ---
| Product & Features |  |  | Y | 30 | --- |  | --- | --- | --- | --- | ---
|  |  | Meter Name | Y | 30 | --- | 20 | UTF8 | RWC | --- | PM5xxx = "Power Meter" | Y
|  |  | Meter Model | Y | 50 | --- | 20 | UTF8 | RWC | --- | PM5000 = "PM5000" PM5010 = "PM5010" PM5200 = "PM5200" PM5250 = "PM5250" PM5350 = "PM5350" PM5110 = "PM5110" PM5111 = "PM5111" PM5310 = "PM5310" PM5330 = "PM5330" PM5331 = "PM5331" PM5320 = "PM5320" PM5340 = "PM5340" PM5341 = "PM5341" PM5100 = "PM5100" EM7230 = "EM7230" EM7280 = "EM7280" EM7290 = "EM7290" PM2110 = "PM2110" PM2120 = "PM2120" PM2130 = "PM2130" PM2125 = "PM2125" EM6400NG noncom = "EM6400NG" EM6400NG = "EM6400NG" PM2210 = "PM2210" PM2220 = "PM2220" PM2230 = "PM2230" PM2225 = "PM2225" | Y
|  |  | Manufacturer | Y | 70 | --- | 20 | UTF8 | RWC | --- | "Schneider Electric" | Y
|  |  | Product ID Number | Y | 90 | --- | 1 | INT16U | RWC |  | PM5000 = 15240 PM5010 = 15241 PM5200 = 15242 PM5250 = 15243 PM5350 = 15244 15245 15246 15247 15248 15249 15250 15251 15252 15253 15254 PM5110 = 15270 PM5111 = 15271 PM5310 = 15272 PM5330 = 15273 PM5331 = 15274 PM5320 = 15275 PM5340 = 15276 PM5341 = 15277 PM5100 = 15278 EM7230 = 15255 EM7280 = 15256 EM7290 = 15257 PM2110 = 15500 PM2120 = 15501 PM2130 = 15502 PM2125 = 15503 EM6400 NG non comm = 15510 EM6400 NG = 15511 PM2210 = 15520 PM2220 = 15521 PM2230 = 15522 PM2225 = 15523 | Y | PM5350 = 15234, PM5350RB = 15283
| Manufacturing Data |  |  | Y | 120 | --- |  | --- | --- | --- | --- | ---
|  | Meter |  | Y | 120 | --- |  | --- | --- | --- | --- | ---
|  |  | Serial Number | Y | 130 | --- | 2 | INT32U | R |  | 0 | Y
|  |  | Date of Manufacture | Y | 132 | --- | 4 | DATETIME | R | --- | 0 | Y
|  |  | Hardware Revision | Y | 136 | --- | 5 | UTF8 | R | --- | 0 | Y
| Firmware Versions |  |  | Y | 1637 | --- |  | --- | --- | --- | --- | ---
|  | Operating System |  | Y | 1637 | --- |  | --- | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | 1637 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | 1638 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Y – Minor | Y | 1639 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Z – Quality | Y | 1640 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | 1642 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | 1643 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Y – Minor | Y | 1644 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Z – Quality | Y | 1645 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Date/Time of Last Firmware Download | Y | 1647 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Reset |  | Y | 1669 | --- |  | --- | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | 1669 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
|  | Language |  | Y | 1701 | --- |  | --- | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | 1701 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
| Meter Resets |  |  | Y | 1822 | --- |  | --- | --- | --- | --- | ---
|  |  | Last Unit Restart DateTime | Y | 1824 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Number of Metering System Restarts | Y | 1828 | --- | 1 | INT16U | R | --- | 0 | Y
|  |  | Number of Control Power Failures | Y | 1829 | --- | 1 | INT16U | R | --- | 0 | Y
|  |  | Date/Time of Last Control Power Failure | Y | 1830 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Duration of Last Control Power Failure | Y | 1834 | seconds | 2 | INT32U | R | --- | 0 | Y
|  |  | Cause of Last Meter Reset | Y | 1836 | --- | 1 | INT16U | R | 0 – 2 | 0 | Y | 0 = Unknown 1 = Reset command 2 = Power failure
| Timekeeping |  |  | Y | 1837 | --- |  | --- | --- | --- | --- | ---
|  | Present Date & Time (7 register format) |  | Y | 1837 | --- |  | --- | --- | --- | --- | ---
|  |  | Year | Y | 1837 | year | 1 | INT16U | R | 2000 – 2127 | 2000 | N
|  |  | Month | Y | 1838 | month | 1 | INT16U | R | 1 – 12 | 1 | N
|  |  | Day | Y | 1839 | days | 1 | INT16U | R | 1 – 31 | 1 | N
|  |  | Hour | Y | 1840 | hours | 1 | INT16U | R | 0 – 23 | 0 | N
|  |  | Minute | Y | 1841 | minutes | 1 | INT16U | R | 0 – 59 | 0 | N
|  |  | Second | Y | 1842 | seconds | 1 | INT16U | R | 0 – 59 | 0 | N
|  |  | Millisecond | Y | 1843 | msec | 1 | INT16U | R | 0 – 999 | 0 | N
|  | Present Date & Time (4 register format) |  | Y | 1845 | --- |  | --- | --- | --- | --- | ---
|  |  | Year | Y | 1845 | --- | 1 | INT16U | R | 0 – 127 | 0 | N
|  |  | Month & Day | Y | 1846 | --- | 1 | INT16U | R | 1 – 12, 1 – 31 | 0 | N
|  |  | Hour & Minute | Y | 1847 | --- | 1 | INT16U | R | 0 – 23, 0 – 59 | 0 | N
|  |  | Milliseconds | Y | 1848 | --- | 1 | INT16U | R | 0 – 59,999 | 0 | N
| Security |  |  | Y | 1880 | --- |  | --- | --- | --- | --- | ---
|  | Revenue Security |  | Y | 1920 | --- |  | --- | --- | --- | --- | ---
|  |  | Revenue Security Switch Status | Y | 1920 | --- | 1 | INT16U | R | 0 – 1 | 1 | Y | 0 = disabled, 1 = enabled
|  |  | Revenue Security Status | Y | 1921 | --- | 1 | INT16U | R | 0 – 4 | 0 | Y | 0 = inactive, 1 = active, For RMICAN 3 = inactive, 4 = active,
|  |  | Date/Time of Last Revenue Security State Change | Y | 1922 | --- | 4 | DATETIME | R |  |  | Y
Meter Setup & Status |  |  |  | Y | 2000 | --- |  | --- | --- | --- | --- | ---
| Miscellaneous Control & Status |  |  | Y | 2000 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Load Timer | Y | 2002 | seconds | 2 | INT32U | R | --- | 0 | Y | Increments when average current exceeds the Active Load Timer Setpoint.
|  |  | Meter Operation Timer | Y | 2004 | seconds | 2 | INT32U | R | --- | 0 | Y
| Metering Setup |  |  | Y | 2014 | --- |  | --- | --- | --- | --- | ---
|  | Power System |  | Y | 2014 | --- |  | --- | --- | --- | --- | ---
|  |  | Number of Phases | Y | 2014 | --- | 1 | INT16U | RWC | 1 or 3 | 3 | Y | Must match Power System Configuration Enumeration
|  |  | Number of Wires | Y | 2015 | --- | 1 | INT16U | RWC | 2 – 4 | 4 | Y | Must match Power System Configuration Enumeration
|  |  | Power System Configuration | Y | 2016 | --- | 1 | INT16U | RWC | 0 – 13 PM5350: 0 - 12 | 11 | Y | 0 = 1ph, 2w, LN 1 = 1ph, 2w, LL 2 = 1ph, 3w, LL with N 3 = 3ph, 3w, Delta, Ungrounded 4 = 3ph, 3w, Delta, Corner Grounded 5 = 3ph, 3w, Wye, Ungrounded 6 = 3ph, 3w, Wye Grounded 7 = 3ph, 3w, Wye, Resistance Grounded 8 = 3ph, 4w, Open Delta, Center-Tapped 9 = 3ph, 4w, Delta, Center-Tapped 10 = 3ph, 4w, Wye, Ungrounded 11 = 3ph, 4w, Wye Grounded 12 = 3ph, 4w, Wye, Resistance Grounded 13 = Multi-Circuit 3 circuit LN 14 = Multi-Circuit 2 Circuit LN 15 = Multi-Circuit 1 Cicuit LN 16 = Multi-Circuit 1 Circuit WYE (No neutral) 17 = Multi-Circuit 2 Circuit LL 18 = Multi-Circuit 1 Circuit LL 19 = Multi-Circuit 1 Circuit LL (w/ Neutral) 20 = Multi-Circuit WYE 21 = Multi-Circuit 2 Circuit LL DELTA 22 = Multi-Circuit 1 Circuit LL DELTA
|  |  | Nominal Frequency | Y | 2017 | Hz | 1 | INT16U | RWC | 50, 60, 400 PM5350: 50, 60 | 50 | Y | PM5350 does not support 400Hz
|  |  | Nominal Voltage | Y | 2018 | V | 2 | FLOAT32 | RWC | 0 – (2xVT Primary or 2,000,000) | 230 | Y
|  |  | Nominal Current | Y | 2020 | A | 2 | FLOAT32 | RWC | 0 – (4xCT Primary or 50,000) | 5 | Y
|  |  | Nominal Power Factor | Y | 2022 | --- | 2 | 4Q_FP_PF | RWC | +/- 0.0 – 2.0 | 0.8 | Y
|  |  | Normal Phase Rotation | Y | 2024 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | Y
|  | Instrument Transformers 1 |  | Y | 2025 | --- |  | --- | --- | --- | --- | ---
|  |  | Number VTs | Y | 2025 | --- | 1 | INT16U | RWC | Depends on Power System | 0 | Y
|  |  | VT Primary | Y | 2026 | V | 2 | FLOAT32 | RWC | VT Secondary – 1,000,000 | 120 | Y
|  |  | VT Secondary | Y | 2028 | V | 1 | INT16U | RWC | 100, 110, 115, 120 | 120 | Y
|  |  | Number CTs | Y | 2029 | --- | 1 | INT16U | RWC | Depends on Power System | 0 | Y
|  |  | CT Primary | Y | 2030 | A | 1 | INT16U | RWC | 1 – 32,767 | 5 | Y
|  |  | CT Secondary | Y | 2031 | A | 1 | INT16U | RWC | 1 , 5 | 5 | Y
|  |  | CT Primary N | Y | 2032 | A | 1 | INT16U | RWC | 1 – 32,767 | 5 | Y
|  |  | CT Secondary N | Y | 2033 | A | 1 | INT16U | RWC | 1, 5 | 5 | Y
|  |  | CT Location for 1 or 2 CT Metering | Y | 2034 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | Y | If 1 CT, value is meter terminal connected If 2 CT, value is meter terminal not connected 1 = Phase A, 2 = Phase B, 3 = Phase C
|  |  | VT Location for 1 or 2 VT Metering | Y | 2035 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | Y | Must match CT Location
|  |  | VT Connection Type | Y | 2036 | --- | 1 | INT16U | RWC | 0 –4 | 0 | Y | 0 = Direct Connect 1 = Delta (2 VT) 2 = Wye (3 VT) 3 = L-N (1 VT) 4 = L-L (1 VT) 5 = L-L W/N (2 VT)
|  |  | Remapping Indication | Y | 2037 | --- | 1 | INT16U | R | 0 – 1 | 0 | N | 0 = Default Mapping; 1 = Remapping in Use
|  |  | Logical Phase A Voltage | Y | 2038 | --- | 1 | INT16U | RWC | 10 – 31 | 10 | Y | Add 1 if reversed.
|  |  | Logical Phase B Voltage | Y | 2039 | --- | 1 | INT16U | RWC | 10 – 31 | 20 | Y | Add 1 if reversed.
|  |  | Logical Phase C Voltage | Y | 2040 | --- | 1 | INT16U | RWC | 10 – 31 | 30 | Y | Add 1 if reversed.
|  |  | Logical Phase N Voltage | Y | 2041 | --- | 1 | INT16U | RWC | 10 – 41 | 40 | Y | Add 1 if reversed.
|  |  | Logical Phase A Current | Y | 2042 | --- | 1 | INT16U | RWC | 10 – 41 | 10 | Y | Add 1 if reversed.
|  |  | Logical Phase B Current | Y | 2043 | --- | 1 | INT16U | RWC | 10 – 41 | 20 | Y | Add 1 if reversed.
|  |  | Logical Phase C Current | Y | 2044 | --- | 1 | INT16U | RWC | 10 – 41 | 30 | Y | Add 1 if reversed.
|  |  | Logical Phase N Current | Y | 2045 | --- | 1 | INT16U | RWC | 10 – 41 | 40 | Y | Add 1 if reversed.
|  | Operating Modes |  | Y | 2046 | --- |  | --- | --- | --- | --- | ---
|  |  | Peak Current Demand Over Last Year | Y | 2048 | A | 2 | FLOAT32 | RWC |  | 0 | Y | Entered by the user for use in calculation of Total Demand Distortion. 0 = Calculation performed using peak demand of 3-phase average current.
|  |  | Active Load Timer Setpoint | Y | 2050 | A | 2 | FLOAT32 | RWC | 0 – (10 * CT Ratio) | 5 | Y
| Energy Pulse Output Setup |  |  | Y | 2126 | --- |  | --- | --- | --- | --- | ---
|  |  | Alarm / Energy LED Mode | Y | 2126 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | Y | 0 = Disable, 1 = Active Alarm (default), 2 = Energy
|  | Energy Pulse Output Channel 01 |  | Y | 2130 | --- |  | --- | --- | --- | --- | ---
|  |  | Energy Channel | Y | 2130 | --- | 1 | INT16U | RWC | 0 – 18 PM5350 / PM5500: 0 - 9 | 0 | Y | 0 = Not Used 1 = Active Energy Delivered (Into Load) 2 = Active Energy Received (Out of Load) 3 = Active Energy Delivered + Received 4 = Reactive Energy Delivered 5 = Reactive Energy Received 6 = Reactive Energy Delivered + Received 7 = Apparent Energy Delivered 8 = Apparent Energy Received 9 = Apparent Energy Delivered + Received 10 = Active Energy Delivered Phase A 11 = Active Energy Delivered Phase B 12 = Active Energy Delivered Phase C 13 = Reactive Energy Delivered Phase A 14 = Reactive Energy Delivered Phase B 15 = Reactive Energy Delivered Phase C 16 = Apparent Energy Delivered Phase A 17 = Apparent Energy Delivered Phase B 18 = Apparent Energy Delivered Phase C
|  |  | Digital Output Association | Y | 2131 | --- | 1 | INT16U | RWC | 0 – 99 | 0 | Y | 0 = No association 1 - 2 = Digital Output 99 = LED A digital output shall be permitted to be associated with only 1 energy value. If the Energy Channel is not 0, a valid digital output association must be made.
|  |  | Pulse Weight | Y | 2132 | kWh, kVAh, kVAh | 2 | FLOAT32/INT32U | RWC | 1E-10 – 1E10 | 0 | Y | If the Energy Channel is not 0, a non-zero pulse weight must be entered. In PM5500 and PM5350 R2 it is an INT32U. The range is 1-9999999, the default value is 1, and the units are pulses / k_h.
|  | Energy Pulse Output Channel 02 |  | Y | 2134 | --- |  | --- | --- | --- | --- | --- | See Energy Pulse Output Channel 01
|  |  | Energy Channel | Y | 2134 | --- | 1 | INT16U | RWC | 0 – 18 | 0 | Y
|  |  | Digital Output Association | Y | 2135 | --- | 1 | INT16U | RWC | 0 – 99 | 0 | Y
|  |  | Pulse Weight | Y | 2136 | kWh, kVAh, kVAh | 2 | FLOAT32/INT32U | RWC | 1E-10 – 1E10 | 0 | Y | If the Energy Channel is not 0, a non-zero pulse weight must be entered. In PM5500 and PM5350 R2 it is an INT32U. The range is 1-9999999, the default value is 1, and the units are pulses / k_h.
|  | Energy Pulse Output Channel 03 |  | Y | 2138 | --- |  | --- | --- | --- | --- | --- | See Energy Pulse Output Channel 01
|  |  | Energy Channel | Y | 2138 | --- | 1 | INT16U | RWC | 0 – 18 | 0 | Y
|  |  | Digital Output Association | Y | 2139 | --- | 1 | INT16U | RWC | 0 – 99 | 0 | Y
|  |  | Pulse Weight | Y | 2140 | kWh, kVAh, kVAh | 2 | FLOAT32/INT32U | RWC | 1E-10 – 1E10 | 0 | Y | If the Energy Channel is not 0, a non-zero pulse weight must be entered. In PM5500 and PM5350 R2 it is an INT32U. The range is 1-9999999, the default value is 1, and the units are pulses / k_h.
Bitmapped Status Holding Registers |  |  |  | Y | 2400
| Digital Input Status Holding Registers |  |  | Y | 2400
|  | On/Off Status |  | Y | 2400 | --- |  | --- | --- | --- | --- | ---
|  |  | Digital Input Status Validity - Base Unit | Y | 2400 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000 | N
|  |  | Digital Input Status - Base Unit | Y | 2401 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000 | N
| Digital Output Status Holding Registers |  |  | Y | 2402
|  | On/Off Status |  | Y | 2402 | --- |  | --- | --- | --- | --- | ---
|  |  | Digital Output Status Validity - Base Unit | Y | 2402 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000 | N
|  |  | Digital Output Status - Base Unit | Y | 2403 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000 | N
|  | Standard Alarms |  | Y | 2420 | --- |  | --- | --- | --- | --- | ---
|  |  | Standard - 1 second Group 1 Validity | Y | 2420 | --- | 1 | BITMAP | R |  | 0 | N | See PTI document for definition
|  |  | Standard - 1 second Group 1 | Y | 2421 | --- | 1 | BITMAP | R |  | 0 | N | 0 = Not Detected; 1 = Detected
|  |  | Standard - 1 second Group 2 Validity | Y | 2422 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Standard - 1 second Group 2 | Y | 2423 | --- | 1 | BITMAP | R |  | 0 | N
|  | Custom 1 Second Alarms |  | Y | 2426 | --- |  | --- | --- | --- | --- | ---
|  | Standard High Speed Alarms |  | Y | 2428 | --- |  | --- | --- | --- | --- | ---
|  | Custom High Speed Alarms |  | Y | 2432 | --- |  | --- | --- | --- | --- | ---
|  | Disturbance Alarms |  | Y | 2434 | --- |  | --- | --- | --- | --- | ---
|  | Transient Alarms |  | Y | 2436 | --- |  | --- | --- | --- | --- | ---
|  | Waveshape Alarms |  | Y | 2438 | --- |  | --- | --- | --- | --- | ---
|  | Unary Alarms |  | Y | 2440 | --- |  | --- | --- | --- | --- | ---
|  |  | Unary Validity | Y | 2440 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Unary | Y | 2441 | --- | 1 | BITMAP | R |  | 0 | N
|  | Digital Alarms |  | Y | 2442 | --- |  | --- | --- | --- | --- | ---
|  | Binary Alarms |  | Y | 2452 | --- |  | --- | --- | --- | --- | ---
|  | Time of Day Alarms |  | Y | 2454 | --- |  | --- | --- | --- | --- | ---
|  | Logic Alarms |  | Y | 2456 | --- |  | --- | --- | --- | --- | ---
Meter Data (Basic) |  |  |  | Y | 2700 | --- |  | --- | --- | --- | --- | ---
| Energy - 32 bit floating point values |  |  | Y | 2700 | --- |  | --- | --- | --- | --- | ---
|  | Accumulated Energy - 32 bit floating point values |  | Y | 2700 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Delivered (Into Load) | Y | 2700 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received (Out of Load) | Y | 2702 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered + Received | Y | 2704 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered- Received | Y | 2706 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered | Y | 2708 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received | Y | 2710 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered + Received | Y | 2712 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered - Received | Y | 2714 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered | Y | 2716 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received | Y | 2718 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered + Received | Y | 2720 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered - Received | Y | 2722 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  | Input Metering Accumulation - 32 bit floating point values |  | Y | 2830 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Accumulation Channel 01 | Y | 2830 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Accumulation Channel 02 | Y | 2832 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Accumulation Channel 03 | Y | 2834 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Accumulation Channel 04 | Y | 2836 | --- | 2 | FLOAT32 | R | --- | 0 | N
Meter Data (Basic) |  |  |  | Y | 3000 | --- |  | --- | --- | --- | --- | ---
| 1s Metering (50/60 Cycles) |  |  | Y | 3000 | --- |  | --- | --- | --- | --- | ---
|  | Current |  | Y | 3000 | --- |  | --- | --- | --- | --- | ---
|  |  | Current A | Y | 3000 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B | Y | 3002 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C | Y | 3004 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N | Y | 3006 | A | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where there is a N current and when all wired phase currents are metered
|  |  | Current G | Y | 3008 | A | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where there is not a N current and when all wired phase currents are metered
|  |  | Current Avg | Y | 3010 | A | 2 | FLOAT32 | R |  |  | N
|  | Current Unbalance |  | Y | 3012 | --- |  | --- | --- | --- | --- | ---
|  |  | Current Unbalance A | Y | 3012 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current Unbalance B | Y | 3014 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current Unbalance C | Y | 3016 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current Unbalance Worst | Y | 3018 | % | 2 | FLOAT32 | R |  |  | N
|  | Voltage |  | Y | 3020 | --- |  | --- | --- | --- | --- | ---
|  |  | Voltage A-B | Y | 3020 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C | Y | 3022 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A | Y | 3024 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage L-L Avg | Y | 3026 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N | Y | 3028 | V | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where Van is connected
|  |  | Voltage B-N | Y | 3030 | V | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where Vbn is connected
|  |  | Voltage C-N | Y | 3032 | V | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where Vcn is connected
|  |  | Voltage L-N Avg | Y | 3036 | V | 2 | FLOAT32 | R |  |  | N | Reportable only in systems where a L-N voltage is applied
|  | Voltage Unbalance |  | Y | 3038 | --- |  | --- | --- | --- | --- | ---
|  |  | Voltage Unbalance A-B | Y | 3038 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance B-C | Y | 3040 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance C-A | Y | 3042 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance L-L Worst | Y | 3044 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance A-N | Y | 3046 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance B-N | Y | 3048 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance C-N | Y | 3050 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage Unbalance L-N Worst | Y | 3052 | % | 2 | FLOAT32 | R |  |  | N
|  | Power |  | Y | 3054 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Power A | Y | 3054 | kW | 2 | FLOAT32 | R |  |  | N
|  |  | Active Power B | Y | 3056 | kW | 2 | FLOAT32 | R |  |  | N
|  |  | Active Power C | Y | 3058 | kW | 2 | FLOAT32 | R |  |  | N
|  |  | Active Power Total | Y | 3060 | kW | 2 | FLOAT32 | R |  |  | N
|  |  | Reactive Power A | Y | 3062 | kVAR | 2 | FLOAT32 | R |  |  | N
|  |  | Reactive Power B | Y | 3064 | kVAR | 2 | FLOAT32 | R |  |  | N
|  |  | Reactive Power C | Y | 3066 | kVAR | 2 | FLOAT32 | R |  |  | N
|  |  | Reactive Power Total | Y | 3068 | kVAR | 2 | FLOAT32 | R |  |  | N
|  |  | Apparent Power A | Y | 3070 | kVA | 2 | FLOAT32 | R |  |  | N
|  |  | Apparent Power B | Y | 3072 | kVA | 2 | FLOAT32 | R |  |  | N
|  |  | Apparent Power C | Y | 3074 | kVA | 2 | FLOAT32 | R |  |  | N
|  |  | Apparent Power Total | Y | 3076 | kVA | 2 | FLOAT32 | R |  |  | N
|  | Power Factor |  | Y | 3078 | --- |  | --- | --- | --- | --- | ---
|  |  | Power Factor A | Y | 3078 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Power Factor B | Y | 3080 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Power Factor C | Y | 3082 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Power Factor Total | Y | 3084 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Displacement Power Factor A | Y | 3086 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Displacement Power Factor B | Y | 3088 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Displacement Power Factor C | Y | 3090 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  |  | Displacement Power Factor Total | Y | 3092 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | N
|  | Frequency |  | Y | 3110 | --- |  | --- | --- | --- | --- | ---
|  |  | Frequency | Y | 3110 | Hz | 2 | FLOAT32 | R | 42 – 70 |  | N
|  | Input Metering Rate Channels |  | Y | 3112 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Rate Channel 01 | Y | 3112 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Input Metering Rate Channel 02 | Y | 3114 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Input Metering Rate Channel 03 | Y | 3116 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Input Metering Rate Channel 04 | Y | 3118 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Temperature | Y | 3132 | degrees C | 2 | FLOAT32 | R |  |  | N | Internal unit temperature
|  | Miscellaneous |  | Y | 3134 | --- |  | --- | --- | --- | --- | ---
|  |  | Phase Rotation | Y | 3134 | --- | 1 | INT16U | R | 0 – 1 | 0 | N | 0 = ABC, 1 = CBA
|  |  | Power Factor Total IEC | Y | 3192 | --- | 2 | FLOAT32 | R | -1 to 1 | --- | N
|  |  | Power Factor Total Lead Lag | Y | 3194 | --- | 2 | FLOAT32 | R | -1 to 1 | --- | N
|  |  | Power Factor Total IEC | Y | 3196 | --- | 1 | INT16U | R | -1 to 1 | --- | N | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
|  |  | Power Factor Total Lead Lag | Y | 3197 | --- | 1 | INT16U | R | -1 to 1 | --- | N | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
| Energy |  |  | Y | 3200 | --- |  | --- | --- | --- | --- | ---
|  | Accumulated Energy |  | Y | 3200 | --- |  | --- | --- | --- | --- | ---
|  |  | Accumulated Energy Reset Date/Time | Y | 3200 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Active Energy Delivered (Into Load) | Y | 3204 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received (Out of Load) | Y | 3208 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered + Received | Y | 3212 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered- Received | Y | 3216 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered | Y | 3220 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received | Y | 3224 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered + Received | Y | 3228 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered - Received | Y | 3232 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered | Y | 3236 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received | Y | 3240 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered + Received | Y | 3244 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered - Received | Y | 3248 | VAh | 4 | INT64 | R | --- | 0 | Y
|  | Input Metering Accumulation |  | Y | 3554 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Accumulation Ch01 Reset D/T | Y | 3554 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Input Metering Accumulation Ch02 Reset D/T | Y | 3558 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Input Metering Accumulation Ch03 Reset D/T | Y | 3562 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Input Metering Accumulation Ch04 Reset D/T | Y | 3566 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Input Metering Accumulation Channel 01 | Y | 3570 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Accumulation Channel 02 | Y | 3574 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Accumulation Channel 03 | Y | 3578 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Accumulation Channel 04 | Y | 3582 | --- | 4 | INT64 | R | --- | 0 | Y
| Demand |  |  | Y | 3701 | --- |  | --- | --- | --- | --- | ---
|  | Demand System 1 (Power) |  | Y | 3701 | --- |  | --- | --- | --- | --- | --- | Power
|  |  | Power Demand Method | Y | 3701 | --- | 1 | INT16U | RWC | 0-11 PM5350: 0-7 | 2 | Y | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | Power Demand Interval Duration | Y | 3702 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | Y
|  |  | Power Demand Subinterval Duration | Y | 3703 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | Y | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | Power Demand Elapsed Time in Interval | Y | 3704 | seconds | 1 | INT16U | R | 0 – 3,600 | 0 | N
|  |  | Power Demand Elapsed Time in Subinterval | Y | 3705 | seconds | 1 | INT16U | R | 0 – 3,600 | 0 | N
|  |  | Power Demand Peak Reset Date/Time | Y | 3706 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand System 2 (Current) |  | Y | 3711 | --- |  | --- | --- | --- | --- | --- | Current
|  |  | Current Demand Method | Y | 3711 | --- | 1 | INT16U | RWC | 0-11 PM5350: 0-7 | 2 | Y | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | Current Demand Interval Duration | Y | 3712 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | Y
|  |  | Current Demand Subinterval Duration | Y | 3713 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | Y | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | Current Demand Elapsed Time in Interval | Y | 3714 | seconds | 1 | INT16U | R | 0 – 3,600 | 0 | N
|  |  | Current Demand Elapsed Time in Subinterval | Y | 3715 | seconds | 1 | INT16U | R | 0 – 3,600 | 0 | N
|  |  | Current Demand Peak Reset Date/Time | Y | 3716 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand System 3 (Input Metering) |  | Y | 3721 | --- |  | --- | --- | --- | --- | --- | Input Metering
|  | Demand Channel 1 (Active Power) |  | Y | 3761 | --- |  | --- | --- | --- | --- | --- | Active Power Total
|  |  | Demand System Assignment | Y | 3761 | --- | 1 | INT16U | R | 0 – 6 | 1 | Y | Power Demand
|  |  | Register Number of Metered Quantity | Y | 3762 | --- | 1 | INT16U | R | 1 – 32,767 | R_PTOT_50_60_CYC_RMS | Y | Active Power Total
|  |  | Units Code | Y | 3763 | --- | 1 | INT16U | R | 0 – 100 | 12 | Y
|  |  | Last Demand | Y | 3764 | kW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3766 | kW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3768 | kW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3770 | kW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3772 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 2 (Reactive Power) |  | Y | 3777 | --- |  | --- | --- | --- | --- | --- | Reactive Power Total
|  |  | Demand System Assignment | Y | 3777 | --- | 1 | INT16U | R | 0 – 6 | 1 | Y | Power Demand
|  |  | Register Number of Metered Quantity | Y | 3778 | --- | 1 | INT16U | R | 1 – 32,767 | R_QTOT_50_60_CYC_RMS | Y | Reactive Power Total
|  |  | Units Code | Y | 3779 | --- | 1 | INT16U | R | 0 – 100 | 15 | Y
|  |  | Last Demand | Y | 3780 | kVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3782 | kVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3784 | kVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3786 | kVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3788 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 3 (Apparent Power) |  | Y | 3793 | --- |  | --- | --- | --- | --- | --- | Apparent Power Total
|  |  | Demand System Assignment | Y | 3793 | --- | 1 | INT16U | R | 0 – 6 | 1 | Y | Power Demand
|  |  | Register Number of Metered Quantity | Y | 3794 | --- | 1 | INT16U | R | 1 – 32,767 | R_STOT_50_60_CYC_RMS | Y | Apparent Power Total
|  |  | Units Code | Y | 3795 | --- | 1 | INT16U | R | 0 – 100 | 18 | Y
|  |  | Last Demand | Y | 3796 | kVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3798 | kVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3800 | kVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3802 | kVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3804 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 4 (Current A) |  | Y | 3809 | --- |  | --- | --- | --- | --- | --- | Current , Phase A
|  |  | Demand System Assignment | Y | 3809 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y | Current Demand
|  |  | Register Number of Metered Quantity | Y | 3810 | --- | 1 | INT16U | R | 1 – 32,767 | R_IA_50_60_CYC_RMS | Y | Current, Phase A
|  |  | Units Code | Y | 3811 | --- | 1 | INT16U | R | 0 – 100 | 6 | Y
|  |  | Last Demand | Y | 3812 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3814 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3816 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3818 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3820 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 5 (Current B) |  | Y | 3825 | --- |  | --- | --- | --- | --- | --- | Current, Phase B
|  |  | Demand System Assignment | Y | 3825 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y | Current Demand
|  |  | Register Number of Metered Quantity | Y | 3826 | --- | 1 | INT16U | R | 1 – 32,767 | R_IB_50_60_CYC_RMS | Y | Current, Phase B
|  |  | Units Code | Y | 3827 | --- | 1 | INT16U | R | 0 – 100 | 6 | Y
|  |  | Last Demand | Y | 3828 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3830 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3832 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3834 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3836 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 6 (Current C) |  | Y | 3841 | --- |  | --- | --- | --- | --- | --- | Current, Phase C
|  |  | Demand System Assignment | Y | 3841 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y | Current Demand
|  |  | Register Number of Metered Quantity | Y | 3842 | --- | 1 | INT16U | R | 1 – 32,767 | R_IC_50_60_CYC_RMS | Y | Current, Phase C
|  |  | Units Code | Y | 3843 | --- | 1 | INT16U | R | 0 – 100 | 6 | Y
|  |  | Last Demand | Y | 3844 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3846 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3848 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3850 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3852 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 7 (Current N) |  | Y | 3857 | --- |  | --- | --- | --- | --- | --- | Current, Phase N
|  |  | Demand System Assignment | Y | 3857 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y | Current Demand
|  |  | Register Number of Metered Quantity | Y | 3858 | --- | 1 | INT16U | R | 1 – 32,767 | R_IN_50_60_CYC_RMS | Y | Current, Phase N
|  |  | Units Code | Y | 3859 | --- | 1 | INT16U | R | 0 – 100 | 6 | Y
|  |  | Last Demand | Y | 3860 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3862 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3864 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3866 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3868 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 8 (Current Avg) |  | Y | 3873 | --- |  | --- | --- | --- | --- | --- | Current, Average
|  |  | Demand System Assignment | Y | 3873 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y | Current Demand
|  |  | Register Number of Metered Quantity | Y | 3874 | --- | 1 | INT16U | R | 1 – 32,767 | R_IAVG_50_60_CYC_RMS | Y | Current, Average
|  |  | Units Code | Y | 3875 | --- | 1 | INT16U | R | 0 – 100 | 6 | Y
|  |  | Last Demand | Y | 3876 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3878 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3880 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3882 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3884 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 9 (Current G) |  | Y | 3889 | --- |  | --- | --- | --- | --- | --- | Current Ground
|  |  | Demand System Assignment | Y | 3889 | --- | 1 | INT16U | R | 0 – 6 | 2 | Y
|  |  | Register Number of Metered Quantity | Y | 3890 | --- | 1 | INT16U | R | 1 – 32,767 | R_IG_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 3891 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Last Demand | Y | 3892 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3894 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3896 | A | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3898 | A | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3900 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 10 (Input Metering Channel 1) |  | Y | 3905 | --- |  | --- | --- | --- | --- | --- | Input Metering
|  |  | Demand System Assignment | Y | 3905 | --- | 1 | INT16U | R | 0 – 6 | 3 | Y
|  |  | Register Number of Metered Quantity | Y | 3906 | --- | 1 | INT16U | R | 1 – 32,767 | R_INPUT_MET_RATE_01 | Y
|  |  | Units Code | Y | 3907 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Last Demand | Y | 3908 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3910 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3912 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3914 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3916 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 11 (Input Metering Channel 2) |  | Y | 3921 | --- |  | --- | --- | --- | --- | --- | Input Metering
|  |  | Demand System Assignment | Y | 3921 | --- | 1 | INT16U | R | 0 – 6 | 3 | Y
|  |  | Register Number of Metered Quantity | Y | 3922 | --- | 1 | INT16U | R | 1 – 32,767 | R_INPUT_MET_RATE_02 | Y
|  |  | Units Code | Y | 3923 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Last Demand | Y | 3924 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3926 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3928 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3930 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3932 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 12 (Input Metering Channel 3) |  | Y | 3937 | --- |  | --- | --- | --- | --- | --- | Input Metering
|  |  | Demand System Assignment | Y | 3937 | --- | 1 | INT16U | R | 0 – 6 | 3 | Y
|  |  | Register Number of Metered Quantity | Y | 3938 | --- | 1 | INT16U | R | 1 – 32,767 | R_INPUT_MET_RATE_03 | Y
|  |  | Units Code | Y | 3939 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Last Demand | Y | 3940 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3942 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3944 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3946 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3948 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 13 (Input Metering Channel 4) |  | Y | 3953 | --- |  | --- | --- | --- | --- | --- | Input Metering
|  |  | Demand System Assignment | Y | 3953 | --- | 1 | INT16U | R | 0 – 6 | 3 | Y
|  |  | Register Number of Metered Quantity | Y | 3954 | --- | 1 | INT16U | R | 1 – 32,767 | R_INPUT_MET_RATE_04 | Y
|  |  | Units Code | Y | 3955 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Last Demand | Y | 3956 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3958 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3960 | See Units Code | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3962 | See Units Code | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3964 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 14 (Active Power Phase A) |  | Y | 3969 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 3969 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 3970 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_PA_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 3971 | --- | 1 | INT16U | RWC | 0 – 100 | 12 | Y
|  |  | Last Demand | Y | 3972 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3974 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3976 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3978 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3980 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 15 (Reactive Power Phase A) |  | Y | 3985 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 3985 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 3986 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_QA_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 3987 | --- | 1 | INT16U | RWC | 0 – 100 | 15 | Y
|  |  | Last Demand | Y | 3988 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 3990 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 3992 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 3994 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 3996 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 16 (Apparent Power Phase A) |  | Y | 4001 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4001 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4002 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_SA_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4003 | --- | 1 | INT16U | RWC | 0 – 100 | 18 | Y
|  |  | Last Demand | Y | 4004 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4006 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4008 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4010 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4012 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 17 (Active Power Phase B) |  | Y | 4017 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4017 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4018 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_PB_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4019 | --- | 1 | INT16U | RWC | 0 – 100 | 12 | Y
|  |  | Last Demand | Y | 4020 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4022 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4024 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4026 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4028 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 18 (Reactive Power Phase B) |  | Y | 4033 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4033 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4034 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_QB_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4035 | --- | 1 | INT16U | RWC | 0 – 100 | 15 | Y
|  |  | Last Demand | Y | 4036 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4038 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4040 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4042 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4044 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 19 (Apparent Power Phase B) |  | Y | 4049 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4049 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4050 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_SB_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4051 | --- | 1 | INT16U | RWC | 0 – 100 | 18 | Y
|  |  | Last Demand | Y | 4052 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4054 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4056 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4058 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4060 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Demand System Assignment | Y | 4065 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4066 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_PC_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4067 | --- | 1 | INT16U | RWC | 0 – 100 | 12 | Y
|  |  | Last Demand | Y | 4068 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4070 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4072 | KW | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4074 | KW | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4076 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 21 (Reactive Power Phase C) |  | Y | 4081 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4081 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4082 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_QC_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4083 | --- | 1 | INT16U | RWC | 0 – 100 | 15 | Y
|  |  | Last Demand | Y | 4084 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4086 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4088 | KVAR | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4090 | KVAR | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4092 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Demand Channel 22 (Apparent Power Phase C) |  | Y | 4097 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System Assignment | Y | 4097 | --- | 1 | INT16U | RWC | 0 – 6 | 1 | Y | Power
|  |  | Register Number of Metered Quantity | Y | 4098 | --- | 1 | INT16U | RWC | 1 – 32,767 | R_SC_50_60_CYC_RMS | Y
|  |  | Units Code | Y | 4099 | --- | 1 | INT16U | RWC | 0 – 100 | 18 | Y
|  |  | Last Demand | Y | 4100 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Present Demand | Y | 4102 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Predicted Demand | Y | 4104 | KVA | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Peak Demand | Y | 4106 | KVA | 2 | FLOAT32 | R | --- | 0 | Y
|  |  | Peak Demand DateTime | Y | 4108 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Clock Sync Time of Day | Y | 4147 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y | Time of day to which the demand interval is to be synchronized. Applies to demand intervals configured as Clock Synchronized. Default = midnight.
|  |  | TOU/MT Mode | Y | 4190 | --- | 1 | INT16U | RWC | 0 - 2 | 0 | Y
|  |  | TOU/MT Energy Active Rate | Y | 4191 | --- | 1 | INT16U | R | 0 – 8 | 0 | Y
|  |  | TOU/MT Energy Reset Date/Time | Y | 4192 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | MT Active Energy Delivered Rates |  | Y | 4196 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Delivered Rate 1 | Y | 4196 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 2 | Y | 4200 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 3 | Y | 4204 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 4 | Y | 4208 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 5 | Y | 4212 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 6 | Y | 4216 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 7 | Y | 4220 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Delivered Rate 8 | Y | 4224 | Wh | 4 | INT64 | R | --- | 0 | Y
|  | MT Active Energy Received Rates |  | Y | 4228 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Received Rate 1 | Y | 4228 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 2 | Y | 4232 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 3 | Y | 4236 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 4 | Y | 4240 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 5 | Y | 4244 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 6 | Y | 4248 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 7 | Y | 4252 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received Rate 8 | Y | 4256 | Wh | 4 | INT64 | R | --- | 0 | Y
|  | MT Reactive Energy Delivered Rates |  | Y | 4260 | --- |  | --- | --- | --- | --- | ---
|  |  | Reactive Energy Delivered Rate 1 | Y | 4260 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 2 | Y | 4264 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 3 | Y | 4268 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 4 | Y | 4272 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 5 | Y | 4276 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 6 | Y | 4280 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 7 | Y | 4284 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered Rate 8 | Y | 4288 | VARh | 4 | INT64 | R | --- | 0 | Y
|  | MT Reactive Energy Received Rates |  | Y | 4292 | --- |  | --- | --- | --- | --- | ---
|  |  | Reactive Energy Received Rate 1 | Y | 4292 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 2 | Y | 4296 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 3 | Y | 4300 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 4 | Y | 4304 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 5 | Y | 4308 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 6 | Y | 4312 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 7 | Y | 4316 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received Rate 8 | Y | 4320 | VARh | 4 | INT64 | R | --- | 0 | Y
|  | MT Apparent Energy Delivered Rates |  | Y | 4324 | --- |  | --- | --- | --- | --- | ---
|  |  | Apparent Energy Delivered Rate 1 | Y | 4324 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 2 | Y | 4328 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 3 | Y | 4332 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 4 | Y | 4336 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 5 | Y | 4340 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 6 | Y | 4344 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 7 | Y | 4348 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered Rate 8 | Y | 4352 | VAh | 4 | INT64 | R | --- | 0 | Y
|  | MT Apparent Energy Received Rates |  | Y | 4356 | --- |  | --- | --- | --- | --- | ---
|  |  | Apparent Energy Received Rate 1 | Y | 4356 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 2 | Y | 4360 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 3 | Y | 4364 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 4 | Y | 4368 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 5 | Y | 4372 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 6 | Y | 4376 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 7 | Y | 4380 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received Rate 8 | Y | 4384 | VAh | 4 | INT64 | R | --- | 0 | Y
|  | MT Input Metering Channel 01 Rates |  | Y | 4388 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 01 Rate 1 | Y | 4388 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 2 | Y | 4392 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 3 | Y | 4396 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 4 | Y | 4400 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 5 | Y | 4404 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 6 | Y | 4408 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 7 | Y | 4412 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 01 Rate 8 | Y | 4416 | --- | 4 | INT64 | R | --- | 0 | Y
|  | MT Input Metering Channel 02 Rates |  | Y | 4420 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 02 Rate 1 | Y | 4420 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 2 | Y | 4424 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 3 | Y | 4428 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 4 | Y | 4432 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 5 | Y | 4436 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 6 | Y | 4440 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 7 | Y | 4444 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 02 Rate 8 | Y | 4448 | --- | 4 | INT64 | R | --- | 0 | Y
|  | MT Input Metering Channel 03 Rates |  | Y | 4452 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 03 Rate 1 | Y | 4452 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 2 | Y | 4456 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 3 | Y | 4460 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 4 | Y | 4464 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 5 | Y | 4468 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 6 | Y | 4472 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 7 | Y | 4476 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 03 Rate 8 | Y | 4480 | --- | 4 | INT64 | R | --- | 0 | Y
|  | MT Input Metering Channel 04 Rates |  | Y | 4484 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 04 Rate 1 | Y | 4484 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 2 | Y | 4488 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 3 | Y | 4492 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 4 | Y | 4496 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 5 | Y | 4500 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 6 | Y | 4504 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 7 | Y | 4508 | --- | 4 | INT64 | R | --- | 0 | Y
|  |  | Input Metering Channel 04 Rate 8 | Y | 4512 | --- | 4 | INT64 | R | --- | 0 | Y
|  | MT Setup Rate 1 |  | Y | 4516 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 1 | Y | 4516 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 1 | Y | 4517 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 1 | Y | 4518 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate1 | Y | 4519 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 1 | Y | 4520 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 1 | Y | 4521 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 1 | Y | 4522 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 2 |  | Y | 4523 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 2 | Y | 4523 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 2 | Y | 4524 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 2 | Y | 4525 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate2 | Y | 4526 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 2 | Y | 4527 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 2 | Y | 4528 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 2 | Y | 4529 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 3 |  | Y | 4530 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 3 | Y | 4530 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 3 | Y | 4531 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 3 | Y | 4532 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate3 | Y | 4533 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 3 | Y | 4534 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 3 | Y | 4535 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 3 | Y | 4536 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 4 |  | Y | 4537 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 4 | Y | 4537 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 4 | Y | 4538 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 4 | Y | 4539 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate4 | Y | 4540 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 4 | Y | 4541 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 4 | Y | 4542 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 4 | Y | 4543 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 5 |  | Y | 4544 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 5 | Y | 4544 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 5 | Y | 4545 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 5 | Y | 4546 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate5 | Y | 4547 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 5 | Y | 4548 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 5 | Y | 4549 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 5 | Y | 4550 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 6 |  | Y | 4551 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 6 | Y | 4551 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 6 | Y | 4552 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 6 | Y | 4553 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate6 | Y | 4554 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 6 | Y | 4555 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 6 | Y | 4556 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 6 | Y | 4557 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 7 |  | Y | 4558 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 7 | Y | 4558 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 7 | Y | 4559 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 7 | Y | 4560 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate7 | Y | 4561 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 7 | Y | 4562 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 7 | Y | 4563 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT End Day Rate 7 | Y | 4564 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  | MT Setup Rate 8 |  | Y | 4565 | --- |  | --- | --- | --- | --- | ---
|  |  | MT Day Type Rate 8 | Y | 4565 | --- | 1 | INT16U | RWC | 1 -10 | 1 | Y | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 8 | Y | 4566 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT End Time Rate 8 | Y | 4567 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Y
|  |  | MT Start Month Rate8 | Y | 4568 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
|  |  | MT Start Day Rate 8 | Y | 4569 | --- | 1 | INT16U | RWC | 0-31 | 0 | Y
|  |  | MT End Month Rate 8 | Y | 4570 | --- | 1 | INT16U | RWC | 0-12 | 0 | Y
Energy Multi Tariff and Multi Circuit - 32 bit floating point values |  |  |  | Y | 4800
|  | MT Active Energy Delivered Rates - 32 bit floating point values |  | Y | 4800 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Delivered Rate 1 | Y | 4800 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 2 | Y | 4802 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 3 | Y | 4804 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 4 | Y | 4806 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 5 | Y | 4808 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 6 | Y | 4810 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 7 | Y | 4812 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Delivered Rate 8 | Y | 4814 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Active Energy Received Rates - 32 bit floating point values |  | Y | 4816 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Received Rate 1 | Y | 4816 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 2 | Y | 4818 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 3 | Y | 4820 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 4 | Y | 4822 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 5 | Y | 4824 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 6 | Y | 4826 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 7 | Y | 4828 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received Rate 8 | Y | 4830 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Reactive Energy Delivered Rates - 32 bit floating point values |  | Y | 4832 | --- |  | --- | --- | --- | --- | ---
|  |  | Reactive Energy Delivered Rate 1 | Y | 4832 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 2 | Y | 4834 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 3 | Y | 4836 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 4 | Y | 4838 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 5 | Y | 4840 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 6 | Y | 4842 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 7 | Y | 4844 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered Rate 8 | Y | 4846 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Reactive Energy Received Rates - 32 bit floating point values |  | Y | 4848 | --- |  | --- | --- | --- | --- | ---
|  |  | Reactive Energy Received Rate 1 | Y | 4848 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 2 | Y | 4850 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 3 | Y | 4852 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 4 | Y | 4854 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 5 | Y | 4856 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 6 | Y | 4858 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 7 | Y | 4860 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received Rate 8 | Y | 4862 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Apparent Energy Delivered Rates - 32 bit floating point values |  | Y | 4864 | --- |  | --- | --- | --- | --- | ---
|  |  | Apparent Energy Delivered Rate 1 | Y | 4864 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 2 | Y | 4866 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 3 | Y | 4868 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 4 | Y | 4870 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 5 | Y | 4872 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 6 | Y | 4874 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 7 | Y | 4876 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered Rate 8 | Y | 4878 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Apparent Energy Received Rates - 32 bit floating point values |  | Y | 4880 | --- |  | --- | --- | --- | --- | ---
|  |  | Apparent Energy Received Rate 1 | Y | 4880 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 2 | Y | 4882 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 3 | Y | 4884 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 4 | Y | 4886 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 5 | Y | 4888 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 6 | Y | 4890 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 7 | Y | 4892 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received Rate 8 | Y | 4894 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Input Metering Channel 01 Rates - 32 bit floating point values |  | Y | 4896 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 01 Rate 1 | Y | 4896 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 2 | Y | 4898 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 3 | Y | 4900 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 4 | Y | 4902 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 5 | Y | 4904 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 6 | Y | 4906 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 7 | Y | 4908 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 01 Rate 8 | Y | 4910 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Input Metering Channel 02 Rates - 32 bit floating point values |  | Y | 4912 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 02 Rate 1 | Y | 4912 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 2 | Y | 4914 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 3 | Y | 4916 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 4 | Y | 4918 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 5 | Y | 4920 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 6 | Y | 4922 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 7 | Y | 4924 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 02 Rate 8 | Y | 4926 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Input Metering Channel 03 Rates - 32 bit floating point values |  | Y | 4928 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 03 Rate 1 | Y | 4928 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 2 | Y | 4930 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 3 | Y | 4932 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 4 | Y | 4934 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 5 | Y | 4936 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 6 | Y | 4938 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 7 | Y | 4940 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 03 Rate 8 | Y | 4942 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  | MT Input Metering Channel 04 Rates - 32 bit floating point values |  | Y | 4944 | --- |  | --- | --- | --- | --- | ---
|  |  | Input Metering Channel 04 Rate 1 | Y | 4944 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 2 | Y | 4946 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 3 | Y | 4948 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 4 | Y | 4950 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 5 | Y | 4952 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 6 | Y | 4954 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 7 | Y | 4956 | --- | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Input Metering Channel 04 Rate 8 | Y | 4958 | --- | 2 | FLOAT32 | R | --- | 0 | N
Command Interface |  |  |  | Y | 5000 | --- |  | --- | --- | --- | --- | ---
| Protected Command Interface |  |  | Y | 5000 | --- |  | --- | --- | --- | --- | ---
|  | Command parameters |  | Y | 5000 | --- |  | --- | --- | --- | --- | ---
|  |  | Requested Command | Y | 5000 | --- | 1 | INT16U | RW | 1 – 32767 | 0 | N
|  |  | Command Semaphore | Y | 5001 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 001 | Y | 5002 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 002 | Y | 5003 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 003 | Y | 5004 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 004 | Y | 5005 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 005 | Y | 5006 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 006 | Y | 5007 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 007 | Y | 5008 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 008 | Y | 5009 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 009 | Y | 5010 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 010 | Y | 5011 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 011 | Y | 5012 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 012 | Y | 5013 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 013 | Y | 5014 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 014 | Y | 5015 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 015 | Y | 5016 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 016 | Y | 5017 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 017 | Y | 5018 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 018 | Y | 5019 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 019 | Y | 5020 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 020 | Y | 5021 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 021 | Y | 5022 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 022 | Y | 5023 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 023 | Y | 5024 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 024 | Y | 5025 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 025 | Y | 5026 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 026 | Y | 5027 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 027 | Y | 5028 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 028 | Y | 5029 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 029 | Y | 5030 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 030 | Y | 5031 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 031 | Y | 5032 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 032 | Y | 5033 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 033 | Y | 5034 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 034 | Y | 5035 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 035 | Y | 5036 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 036 | Y | 5037 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 037 | Y | 5038 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 038 | Y | 5039 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 039 | Y | 5040 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 040 | Y | 5041 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 041 | Y | 5042 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 042 | Y | 5043 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 043 | Y | 5044 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 044 | Y | 5045 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 045 | Y | 5046 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 046 | Y | 5047 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 047 | Y | 5048 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 048 | Y | 5049 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 049 | Y | 5050 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 050 | Y | 5051 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 051 | Y | 5052 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 052 | Y | 5053 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 053 | Y | 5054 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 054 | Y | 5055 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 055 | Y | 5056 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 056 | Y | 5057 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 057 | Y | 5058 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 058 | Y | 5059 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 059 | Y | 5060 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 060 | Y | 5061 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 061 | Y | 5062 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 062 | Y | 5063 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 063 | Y | 5064 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 064 | Y | 5065 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 065 | Y | 5066 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 066 | Y | 5067 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 067 | Y | 5068 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 068 | Y | 5069 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 069 | Y | 5070 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 070 | Y | 5071 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 071 | Y | 5072 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 072 | Y | 5073 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 073 | Y | 5074 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 074 | Y | 5075 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 075 | Y | 5076 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 076 | Y | 5077 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 077 | Y | 5078 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 078 | Y | 5079 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 079 | Y | 5080 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 080 | Y | 5081 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 081 | Y | 5082 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 082 | Y | 5083 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 083 | Y | 5084 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 084 | Y | 5085 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 085 | Y | 5086 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 086 | Y | 5087 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 087 | Y | 5088 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 088 | Y | 5089 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 089 | Y | 5090 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 090 | Y | 5091 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 091 | Y | 5092 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 092 | Y | 5093 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 093 | Y | 5094 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 094 | Y | 5095 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 095 | Y | 5096 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 096 | Y | 5097 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 097 | Y | 5098 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 098 | Y | 5099 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 099 | Y | 5100 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 100 | Y | 5101 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 101 | Y | 5102 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 102 | Y | 5103 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 103 | Y | 5104 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 104 | Y | 5105 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 105 | Y | 5106 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 106 | Y | 5107 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 107 | Y | 5108 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 108 | Y | 5109 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 109 | Y | 5110 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 110 | Y | 5111 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 111 | Y | 5112 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 112 | Y | 5113 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 113 | Y | 5114 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 114 | Y | 5115 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 115 | Y | 5116 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 116 | Y | 5117 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 117 | Y | 5118 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 118 | Y | 5119 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 119 | Y | 5120 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 120 | Y | 5121 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 121 | Y | 5122 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 122 | Y | 5123 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 123 | Y | 5124 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Status | Y | 5125 | --- | 1 | INT16U | R | 0 – 32767 | 0 | N
|  |  | Command Result | Y | 5126 | --- | 1 | INT16U | R | --- | 0 | N | 0 = Valid Operation 2000 = Command Only Allowed In Calibration Setup 2001 = Command Not Allowed In Calibration Setup 2002 = Command Only Allowed For Disabled Calibration 2003 = Calibration Parameters Not Monotonic 2004 = Calibration Parameters Not Within Percent Range 2005 = Calibration Incomplete Calibration 2006 = Calibration Current Magnitude Phase Shift Mismatch 3000 = Invalid Command 3001 = Invalid Parameter 3002 = Invalid Number of Parameters 3003 = Invalid Password 3004 = Command Failed Security Check 3005 = Invalid Command Interface 3006 = Revenue Security Active 3007 = Operation Not Performed 3008 = Invalid ID 3009 = Feature Not Supported 3010 = Invalid Semaphore 6000 = Invalid Control Mode 6001 = Digital Output Disabled 8000 = File System Error
|  |  | Command Data 001 | Y | 5127 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 002 | Y | 5128 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 003 | Y | 5129 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 004 | Y | 5130 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 005 | Y | 5131 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 006 | Y | 5132 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 007 | Y | 5133 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 008 | Y | 5134 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 009 | Y | 5135 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 010 | Y | 5136 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 011 | Y | 5137 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 012 | Y | 5138 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 013 | Y | 5139 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 014 | Y | 5140 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 015 | Y | 5141 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 016 | Y | 5142 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 017 | Y | 5143 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 018 | Y | 5144 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 019 | Y | 5145 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 020 | Y | 5146 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 021 | Y | 5147 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 022 | Y | 5148 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 023 | Y | 5149 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 024 | Y | 5150 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 025 | Y | 5151 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 026 | Y | 5152 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 027 | Y | 5153 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 028 | Y | 5154 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 029 | Y | 5155 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 030 | Y | 5156 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 031 | Y | 5157 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 032 | Y | 5158 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 033 | Y | 5159 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 034 | Y | 5160 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 035 | Y | 5161 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 036 | Y | 5162 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 037 | Y | 5163 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 038 | Y | 5164 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 039 | Y | 5165 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 040 | Y | 5166 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 041 | Y | 5167 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 042 | Y | 5168 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 043 | Y | 5169 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 044 | Y | 5170 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 045 | Y | 5171 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 046 | Y | 5172 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 047 | Y | 5173 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 048 | Y | 5174 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 049 | Y | 5175 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 050 | Y | 5176 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 051 | Y | 5177 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 052 | Y | 5178 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 053 | Y | 5179 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 054 | Y | 5180 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 055 | Y | 5181 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 056 | Y | 5182 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 057 | Y | 5183 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 058 | Y | 5184 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 059 | Y | 5185 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 060 | Y | 5186 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 061 | Y | 5187 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 062 | Y | 5188 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 063 | Y | 5189 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 064 | Y | 5190 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 065 | Y | 5191 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 066 | Y | 5192 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 067 | Y | 5193 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 068 | Y | 5194 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 069 | Y | 5195 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 070 | Y | 5196 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 071 | Y | 5197 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 072 | Y | 5198 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 073 | Y | 5199 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 074 | Y | 5200 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 075 | Y | 5201 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 076 | Y | 5202 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 077 | Y | 5203 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 078 | Y | 5204 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 079 | Y | 5205 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 080 | Y | 5206 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 081 | Y | 5207 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 082 | Y | 5208 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 083 | Y | 5209 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 084 | Y | 5210 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 085 | Y | 5211 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 086 | Y | 5212 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 087 | Y | 5213 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 088 | Y | 5214 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 089 | Y | 5215 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 090 | Y | 5216 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 091 | Y | 5217 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 092 | Y | 5218 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 093 | Y | 5219 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 094 | Y | 5220 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 095 | Y | 5221 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 096 | Y | 5222 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 097 | Y | 5223 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 098 | Y | 5224 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 099 | Y | 5225 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 100 | Y | 5226 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 101 | Y | 5227 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 102 | Y | 5228 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 103 | Y | 5229 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 104 | Y | 5230 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 105 | Y | 5231 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 106 | Y | 5232 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 107 | Y | 5233 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 108 | Y | 5234 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 109 | Y | 5235 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 110 | Y | 5236 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 111 | Y | 5237 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 112 | Y | 5238 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 113 | Y | 5239 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 114 | Y | 5240 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 115 | Y | 5241 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 116 | Y | 5242 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 117 | Y | 5243 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 118 | Y | 5244 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 119 | Y | 5245 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 120 | Y | 5246 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 121 | Y | 5247 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 122 | Y | 5248 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 123 | Y | 5249 | --- | 1 | INT16U | R | --- | 0 | N
| Unprotected Command Interface |  |  | Y | 5250 | --- |  | --- | --- | --- | --- | ---
|  | Command parameters |  | Y | 5250 | --- |  | --- | --- | --- | --- | ---
|  |  | Requested Command | Y | 5250 | --- | 1 | INT16U | RW | 1 – 32767 | 0 | N
|  |  | Command Parameter 001 | Y | 5252 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 002 | Y | 5253 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 003 | Y | 5254 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 004 | Y | 5255 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 005 | Y | 5256 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 006 | Y | 5257 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 007 | Y | 5258 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 008 | Y | 5259 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 009 | Y | 5260 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 010 | Y | 5261 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 011 | Y | 5262 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 012 | Y | 5263 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 013 | Y | 5264 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 014 | Y | 5265 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 015 | Y | 5266 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 016 | Y | 5267 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 017 | Y | 5268 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 018 | Y | 5269 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 019 | Y | 5270 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 020 | Y | 5271 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 021 | Y | 5272 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 022 | Y | 5273 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 023 | Y | 5274 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 024 | Y | 5275 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 025 | Y | 5276 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 026 | Y | 5277 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 027 | Y | 5278 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 028 | Y | 5279 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 029 | Y | 5280 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 030 | Y | 5281 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 031 | Y | 5282 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 032 | Y | 5283 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 033 | Y | 5284 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 034 | Y | 5285 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 035 | Y | 5286 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 036 | Y | 5287 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 037 | Y | 5288 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 038 | Y | 5289 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 039 | Y | 5290 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 040 | Y | 5291 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 041 | Y | 5292 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 042 | Y | 5293 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 043 | Y | 5294 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 044 | Y | 5295 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 045 | Y | 5296 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 046 | Y | 5297 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 047 | Y | 5298 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 048 | Y | 5299 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 049 | Y | 5300 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 050 | Y | 5301 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 051 | Y | 5302 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 052 | Y | 5303 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 053 | Y | 5304 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 054 | Y | 5305 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 055 | Y | 5306 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 056 | Y | 5307 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 057 | Y | 5308 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 058 | Y | 5309 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 059 | Y | 5310 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 060 | Y | 5311 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 061 | Y | 5312 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 062 | Y | 5313 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 063 | Y | 5314 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 064 | Y | 5315 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 065 | Y | 5316 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 066 | Y | 5317 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 067 | Y | 5318 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 068 | Y | 5319 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 069 | Y | 5320 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 070 | Y | 5321 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 071 | Y | 5322 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 072 | Y | 5323 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 073 | Y | 5324 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 074 | Y | 5325 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 075 | Y | 5326 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 076 | Y | 5327 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 077 | Y | 5328 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 078 | Y | 5329 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 079 | Y | 5330 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 080 | Y | 5331 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 081 | Y | 5332 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 082 | Y | 5333 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 083 | Y | 5334 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 084 | Y | 5335 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 085 | Y | 5336 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 086 | Y | 5337 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 087 | Y | 5338 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 088 | Y | 5339 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 089 | Y | 5340 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 090 | Y | 5341 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 091 | Y | 5342 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 092 | Y | 5343 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 093 | Y | 5344 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 094 | Y | 5345 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 095 | Y | 5346 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 096 | Y | 5347 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 097 | Y | 5348 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 098 | Y | 5349 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 099 | Y | 5350 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 100 | Y | 5351 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 101 | Y | 5352 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 102 | Y | 5353 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 103 | Y | 5354 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 104 | Y | 5355 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 105 | Y | 5356 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 106 | Y | 5357 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 107 | Y | 5358 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 108 | Y | 5359 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 109 | Y | 5360 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 110 | Y | 5361 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 111 | Y | 5362 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 112 | Y | 5363 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 113 | Y | 5364 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 114 | Y | 5365 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 115 | Y | 5366 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 116 | Y | 5367 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 117 | Y | 5368 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 118 | Y | 5369 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 119 | Y | 5370 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 120 | Y | 5371 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 121 | Y | 5372 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 122 | Y | 5373 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Parameter 123 | Y | 5374 | --- | 1 | INT16U | RW | --- | 0 | N
|  |  | Command Status | Y | 5375 | --- | 1 | INT16U | R | 0 – 32767 | 0 | N
|  |  | Command Result | Y | 5376 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 001 | Y | 5377 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 002 | Y | 5378 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 003 | Y | 5379 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 004 | Y | 5380 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 005 | Y | 5381 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 006 | Y | 5382 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 007 | Y | 5383 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 008 | Y | 5384 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 009 | Y | 5385 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 010 | Y | 5386 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 011 | Y | 5387 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 012 | Y | 5388 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 013 | Y | 5389 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 014 | Y | 5390 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 015 | Y | 5391 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 016 | Y | 5392 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 017 | Y | 5393 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 018 | Y | 5394 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 019 | Y | 5395 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 020 | Y | 5396 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 021 | Y | 5397 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 022 | Y | 5398 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 023 | Y | 5399 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 024 | Y | 5400 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 025 | Y | 5401 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 026 | Y | 5402 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 027 | Y | 5403 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 028 | Y | 5404 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 029 | Y | 5405 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 030 | Y | 5406 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 031 | Y | 5407 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 032 | Y | 5408 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 033 | Y | 5409 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 034 | Y | 5410 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 035 | Y | 5411 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 036 | Y | 5412 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 037 | Y | 5413 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 038 | Y | 5414 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 039 | Y | 5415 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 040 | Y | 5416 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 041 | Y | 5417 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 042 | Y | 5418 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 043 | Y | 5419 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 044 | Y | 5420 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 045 | Y | 5421 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 046 | Y | 5422 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 047 | Y | 5423 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 048 | Y | 5424 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 049 | Y | 5425 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 050 | Y | 5426 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 051 | Y | 5427 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 052 | Y | 5428 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 053 | Y | 5429 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 054 | Y | 5430 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 055 | Y | 5431 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 056 | Y | 5432 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 057 | Y | 5433 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 058 | Y | 5434 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 059 | Y | 5435 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 060 | Y | 5436 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 061 | Y | 5437 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 062 | Y | 5438 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 063 | Y | 5439 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 064 | Y | 5440 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 065 | Y | 5441 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 066 | Y | 5442 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 067 | Y | 5443 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 068 | Y | 5444 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 069 | Y | 5445 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 070 | Y | 5446 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 071 | Y | 5447 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 072 | Y | 5448 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 073 | Y | 5449 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 074 | Y | 5450 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 075 | Y | 5451 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 076 | Y | 5452 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 077 | Y | 5453 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 078 | Y | 5454 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 079 | Y | 5455 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 080 | Y | 5456 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 081 | Y | 5457 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 082 | Y | 5458 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 083 | Y | 5459 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 084 | Y | 5460 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 085 | Y | 5461 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 086 | Y | 5462 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 087 | Y | 5463 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 088 | Y | 5464 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 089 | Y | 5465 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 090 | Y | 5466 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 091 | Y | 5467 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 092 | Y | 5468 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 093 | Y | 5469 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 094 | Y | 5470 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 095 | Y | 5471 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 096 | Y | 5472 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 097 | Y | 5473 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 098 | Y | 5474 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 099 | Y | 5475 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 100 | Y | 5476 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 101 | Y | 5477 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 102 | Y | 5478 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 103 | Y | 5479 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 104 | Y | 5480 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 105 | Y | 5481 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 106 | Y | 5482 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 107 | Y | 5483 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 108 | Y | 5484 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 109 | Y | 5485 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 110 | Y | 5486 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 111 | Y | 5487 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 112 | Y | 5488 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 113 | Y | 5489 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 114 | Y | 5490 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 115 | Y | 5491 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 116 | Y | 5492 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 117 | Y | 5493 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 118 | Y | 5494 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 119 | Y | 5495 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 120 | Y | 5496 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 121 | Y | 5497 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 122 | Y | 5498 | --- | 1 | INT16U | R | --- | 0 | N
|  |  | Command Data 123 | Y | 5499 | --- | 1 | INT16U | R | --- | 0 | N
| Mailbox Registers |  |  | Y | 5580 | --- |  | --- | --- | --- | --- | --- | Mailbox registers for customer use.
|  |  | Mailbox Register 001 | Y | 5580 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 002 | Y | 5581 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 003 | Y | 5582 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 004 | Y | 5583 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 005 | Y | 5584 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 006 | Y | 5585 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 007 | Y | 5586 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 008 | Y | 5587 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 009 | Y | 5588 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 010 | Y | 5589 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 011 | Y | 5590 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 012 | Y | 5591 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 013 | Y | 5592 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 014 | Y | 5593 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 015 | Y | 5594 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 016 | Y | 5595 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 017 | Y | 5596 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 018 | Y | 5597 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 019 | Y | 5598 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 020 | Y | 5599 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 021 | Y | 5600 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 022 | Y | 5601 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 023 | Y | 5602 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 024 | Y | 5603 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 025 | Y | 5604 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 026 | Y | 5605 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 027 | Y | 5606 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 028 | Y | 5607 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 029 | Y | 5608 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 030 | Y | 5609 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 031 | Y | 5610 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 032 | Y | 5611 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 033 | Y | 5612 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 034 | Y | 5613 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 035 | Y | 5614 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 036 | Y | 5615 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 037 | Y | 5616 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 038 | Y | 5617 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 039 | Y | 5618 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 040 | Y | 5619 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 041 | Y | 5620 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 042 | Y | 5621 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 043 | Y | 5622 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 044 | Y | 5623 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 045 | Y | 5624 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 046 | Y | 5625 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 047 | Y | 5626 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 048 | Y | 5627 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 049 | Y | 5628 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 050 | Y | 5629 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 051 | Y | 5630 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 052 | Y | 5631 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 053 | Y | 5632 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 054 | Y | 5633 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 055 | Y | 5634 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 056 | Y | 5635 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 057 | Y | 5636 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 058 | Y | 5637 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 059 | Y | 5638 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 060 | Y | 5639 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 061 | Y | 5640 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 062 | Y | 5641 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 063 | Y | 5642 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 064 | Y | 5643 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 065 | Y | 5644 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 066 | Y | 5645 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 067 | Y | 5646 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 068 | Y | 5647 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 069 | Y | 5648 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 070 | Y | 5649 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 071 | Y | 5650 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 072 | Y | 5651 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 073 | Y | 5652 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 074 | Y | 5653 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 075 | Y | 5654 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 076 | Y | 5655 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 077 | Y | 5656 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 078 | Y | 5657 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 079 | Y | 5658 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 080 | Y | 5659 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 081 | Y | 5660 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 082 | Y | 5661 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 083 | Y | 5662 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 084 | Y | 5663 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 085 | Y | 5664 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 086 | Y | 5665 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 087 | Y | 5666 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 088 | Y | 5667 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 089 | Y | 5668 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 090 | Y | 5669 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 091 | Y | 5670 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 092 | Y | 5671 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 093 | Y | 5672 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 094 | Y | 5673 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 095 | Y | 5674 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 096 | Y | 5675 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 097 | Y | 5676 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 098 | Y | 5677 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 099 | Y | 5678 | --- | 1 | INT16U | RW | --- | 0 | Y
|  |  | Mailbox Register 100 | Y | 5679 | --- | 1 | INT16U | RW | --- | 0 | Y
| Command Semaphore |  |  | Y | 5680 | --- | 1 | INT16U | RW | --- | --- | N
HMI |  |  |  | Y | 6000 | --- |  | --- | --- | --- | --- | ---
| Setup |  |  | Y | 6000 | --- |  | --- | --- | --- | --- | ---
|  | Basic HMI Setup |  | Y | 6000 | --- |  | --- | --- | --- | --- | ---
|  |  | HMI Contrast Setting | Y | 6001 | --- | 1 | INT16U | RWC | 1 – 9 | 5 | Y | 1 = Brightest…9 = Dimmest
|  |  | HMI Language | Y | 6003 | --- | 1 | INT16U | RWC | 0 – 12 | 0 | Y | 0 = EnglishUS 1 = EnglishUK 2 = French 3 = Spanish 4 = German 5 = Italian 6 = Polish 7 = Portuguese 8 = Turkish 9 = Chinese 10 = Russian 11 = Arabic 12 = Dutch
|  |  | HMI Date Format | Y | 6004 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | Y | 0 = MM/DD/YYYY 1 = YYYY/MM/DD 2 = DD/MM/YYYY
|  |  | HMI Time Format | Y | 6005 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | Y | 0 = 2400hr 1 = AM/PM
|  |  | HMI IEC/IEEE Mode | Y | 6006 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | Y | 0 = IEC 1 = IEEE
|  |  | HMI Screen Timeout | Y | 6007 | minutes | 1 | INT16U | RWC | 0 – 60 | 0 | Y | 0 = disabled
|  |  | HMI Backlight Timeout | Y | 6008 | minutes | 1 | INT16U | RWC | 0 – 60 | 5 | Y | 0 = disabled
|  |  | HMI Energy Resolution | Y | 6009 | --- | 1 | INT16U | RWC | 0 – 23 | 10 | Y | 0 = Auto range 10 = 000000 kilo 11 = 00000.0 kilo 12 = 0000.00 kilo 13 = 000.000 kilo 20 = 000000 mega 21 = 00000.0 mega 22 = 0000.00 mega 23 = 000.000 mega All other values will default to auto range.
|  |  | HMI Current Resolution | Y | 6010 | --- | 1 | INT16U | RWC | 0 – 23 | 0 | Y | 0 = Auto range 10 = 000000 mA 20 = 000000 A 21 = 00000.0 A 22 = 0000.00 A 23 = 000.000 A All other values will default to auto range.
|  |  | HMI Voltage Resolution | Y | 6011 | --- | 1 | INT16U | RWC | 0 – 32 | 0 | Y | 0 = Auto range 10 = 000000 V 11 = 00000.0 V 12 = 0000.00 V 13 = 000.000 V 20 = 000000 kV 21 = 00000.0 kV 22 = 0000.00 kV 23 = 000.000 kV 30 = 000000 MV 31 = 00000.0 MV 32 = 0000.00 MV All other values will default to auto range.
|  |  | HMI Power Resolution | Y | 6012 | --- | 1 | INT16U | RWC | 0 – 32 | 0 | Y | 0 = Auto range 10 = 000000 W / VAR / VA 20 = 000000 kW / kVAR / kVA 21 = 00000.0 kW / kVAR / kVA 22 = 0000.00 kW / kVAR / kVA 23 = 000.000 kW / kVAR / kVA 30 = 000000 MW / MVAR / MVA 31 = 00000.0 MW / MVAR / MVA 32 = 0000.00 MW / MVAR / MVA All other values will default to auto range.
| Misc HMI |  |  | Y | 6099 | --- |  | --- | --- | --- | --- | ---
|  | QR Code Screen |  | Y | 6099 | --- |  | --- | --- | --- | --- | ---
|  |  | QR Code Screen Enable | Y | 6099 | --- | 1 | INT16U | R | 0 –1 | 1 | Y | 0 = Disable, 1 = Enable
Communications |  |  |  | Y | 6500 | --- |  | --- | --- | --- | --- | ---
| RS-485 Base |  |  | Y | 6500 | --- |  | --- | --- | --- | --- | ---
|  | RS-485 Base Port 1 Settings |  | Y | 6500 | --- |  | --- | --- | --- | --- | ---
|  |  | RS-485 Comm Port (M/S) Protocol | Y | 6500 | --- | 1 | INT16U | RWC | 0 – 3 | 0 | Y | 0 = Modbus 1 = Jbus 2 = Modbus ASCII 8-Bit 3 = Modbus ASCII 7-Bit
|  |  | RS-485 Comm Port (M/S) Address | Y | 6501 | --- | 1 | INT16U | RWC | 1 – 255 | 1 | Y | Valid Addresses: Modbus: 1 – 247 Jbus: 1 – 255
|  |  | RS-485 Comm Port (M/S) Baud Rate | Y | 6502 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | Y | 0 = 9600 1 = 19200 2 = 38400 For PM2000,EM6400, EM72xx 0 = 4800 1 = 9600 2 = 19200 3 = 38400
|  |  | RS-485 Comm Port (M/S) Parity | Y | 6503 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | Y | 0 = Even 1 = Odd 2 = None
|  |  | RS-485 Comm Port (M/S) Modbus ASCII Default Timeout | Y | 6504 | msec | 1 | INT16U | RWC | 50 – 5000 | 1000 | Y | Timeout for end of ASCII packet when no control delimitation is detected.
|  |  | RS-485 Comm Port (M/S) Master/Slave Mode Selection | Y | 6505 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | Y | 0 = Slave 1 = Master
|  |  | RS-485 Comm Port (M/S) Packets To This Unit | Y | 6508 | --- | 1 | INT16U | R | --- | 0 | Y | Number of valid messages addressed to this unit
|  |  | RS-485 Comm Port (M/S) Packets To Other Units | Y | 6509 | --- | 1 | INT16U | R | --- | 0 | Y | Number of valid messages addressed to other units
|  |  | RS-485 Comm Port (M/S) Packets With Bad CRC | Y | 6510 | --- | 1 | INT16U | R | --- | 0 | Y | Number of messages received with bad CRC
|  |  | RS-485 Comm Port (M/S) Packets With Error | Y | 6511 | --- | 1 | INT16U | R | --- | 0 | Y | Number of messages received with errors
|  |  | RS-485 Comm Port (M/S) Packets With Illegal Opcode | Y | 6512 | --- | 1 | INT16U | R | --- | 0 | Y | Number of messages received with an illegal opcode
|  |  | RS-485 Comm Port (M/S) Number Of Exceptions | Y | 6513 | --- | 1 | INT16U | R | --- | 0 | Y | Number of exception replies
|  |  | RS-485 Comm Port (M) Time Out | Y | 6514 | --- | 1 | INT16U | R | --- | 0 | Y | Message failed due to excessive response time from the internal comm. server
|  |  | RS-485 Comm Port (M) Silent Interval Extension | Y | 6546 | chars | 1 | INT16U | RWC | 0 - 15 | 6 | Y | Silent Interval Extension
|  |  | RS-485 Comm Port (M) Response Timeout | Y | 6547 | msec | 1 | INT16U | RWC | 100 - 10000 | 3000 | Y | Response Timeout
|  |  | RS-485 Comm Port (M) Delay Between Frames | Y | 6548 | msec | 1 | INT16U | RWC | 0 - 100 | 50 | Y | Delay Between Frames
|  |  | RS-485 Comm Port (M) Broadcast Enable | Y | 6549 | --- | 1 | INT16U | RWC | 0 - 1 | 0 | Y | 0 = Disable
|  |  | RS-485 Comm Port (M/S) Number of Read Packets | Y | 6550 | --- | 1 | INT16U | R | --- | --- | Y | Number of Read Packets
|  |  | RS-485 Comm Port (M/S) Number of Write Packets | Y | 6551 | --- | 1 | INT16U | R | --- | --- | Y | Number of Write Packets
Inputs & Outputs |  |  |  | Y | 7000 | --- |  | --- | --- | --- | --- | ---
|  |  | Number of Multi-tariff Rates Active | Y | 7012 | --- | 1 | INT16U | RWC | 1 – 8 | 1 | Y
|  |  | Number of Digital Inputs Used to Control Multi-tariff | Y | 7013 | --- | 1 | INT16U | RWC | 1 – 4 | 1 | Y
| Demand Sync Setup |  |  | Y | 7020 | --- |  | --- | --- | --- | --- | ---
|  | Digital Input Associations With Demand Systems |  | Y | 7020 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System 1 (Power) | Y | 7020 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  |  | Demand System 2 (Current) | Y | 7021 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  | Digital Output Associations With Demand Systems |  | Y | 7026 | --- |  | --- | --- | --- | --- | ---
|  |  | Demand System 1 (Power) | Y | 7026 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  |  | Demand System 2 (Current) | Y | 7027 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
| Input Metering Setup |  |  | Y | 7032 | --- |  | --- | --- | --- | --- | ---
|  | Input Metering Channel 01 |  | Y | 7032 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 7032 | --- | 20 | UTF8 | RWC | --- | "Channel 01" | Y
|  |  | Pulse Weight | Y | 7052 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Consumption Units Code | Y | 7054 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Digital Input Association | Y | 7055 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  | Input Metering Channel 02 |  | Y | 7056 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 7056 | --- | 20 | UTF8 | RWC | --- | "Channel 02" | Y
|  |  | Pulse Weight | Y | 7076 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Consumption Units Code | Y | 7078 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Digital Input Association | Y | 7079 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  | Input Metering Channel 03 |  | Y | 7080 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 7080 | --- | 20 | UTF8 | RWC | --- | "Channel 03" | Y
|  |  | Pulse Weight | Y | 7100 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Consumption Units Code | Y | 7102 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Digital Input Association | Y | 7103 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  | Input Metering Channel 04 |  | Y | 7104 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 7104 | --- | 20 | UTF8 | RWC | --- | "Channel 04" | Y
|  |  | Pulse Weight | Y | 7124 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Consumption Units Code | Y | 7126 | --- | 1 | INT16U | RWC | 0 – 100 | 0 | Y
|  |  | Digital Input Association | Y | 7127 | --- | 1 | INT16U | RWC | 0 – 68 | 0 | Y
|  |  | Input Metering Mode | Y | 7272 | --- | 1 | BITMAP | RWC | 0x00 - 0xFF | 0x00 | Y | Bit 0 Channel 1 mode 0= pulse, 1= transition Bit 1 Channel 2 mode 0= pulse, 1= transition Bit 2 Channel 3 mode 0= pulse, 1= transition Bit 3 Channel 4 mode 0= pulse, 1= transition
| Digital Inputs Setup |  |  | Y | 7273 | --- |  | --- | --- | --- | --- | ---
|  | Base Unit - Digital Input DI1 |  | Y | 7273 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 7273 | --- | 1 | INT16U | R | 100 – 199 | 102 | N | First digit (1) indicates point is digital input Second digit indicates the digital input module type Second digit can be used to identify specific hardware options. 0 = Generic digital input Third digit indicates input type 1 = AC 2 = DC
|  |  | Control Mode | Y | 7274 | --- | 1 | INT16U | RWC | 0 – 5 | 0 | N | 0 = Normal (Alarm) 1 = Demand Interval Sync Pulse 2 = Multi-tariff Control 3 = Input Metering 4 = Conditional Energy Control 5 = Incremental Energy Reset
|  |  | Label | Y | 7275 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI1" | Y
|  |  | Debounce Time | Y | 7295 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Y | Must be entered in increments of 10ms.
|  | Base Unit - Digital Input DI2 |  | Y | 7297 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 7297 | --- | 1 | INT16U | R | 100 – 199 | 102 | N
|  |  | Control Mode | Y | 7298 | --- | 1 | INT16U | RWC | 0 – 5 | 0 | N
|  |  | Label | Y | 7299 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI2" | Y
|  |  | Debounce Time | Y | 7319 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Y | Must be entered in increments of 10ms.
|  | Base Unit - Digital Input DI3 |  | Y | 7321 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 7321 | --- | 1 | INT16U | R | 100 – 199 | 102 | N
|  |  | Control Mode | Y | 7322 | --- | 1 | INT16U | RWC | 0 – 5 | 0 | N
|  |  | Label | Y | 7323 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI3" | Y
|  |  | Debounce Time | Y | 7343 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Y | Must be entered in increments of 10ms.
|  | Base Unit - Digital Input DI4 |  | Y | 7345 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 7345 | --- | 1 | INT16U | R | 100 – 199 | 102 | N
|  |  | Control Mode | Y | 7346 | --- | 1 | INT16U | RWC | 0 – 5 | 0 | N
|  |  | Label | Y | 7347 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI4" | Y
|  |  | Debounce Time | Y | 7367 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Y | Must be entered in increments of 10ms.
| Digital Inputs Status |  |  | Y | 8905 | --- |  | --- | --- | --- | --- | ---
|  | On/Off Status |  | Y | 8905 | --- |  | --- | --- | --- | --- | ---
|  |  | Digital Input Status – Base Unit | Y | 8905 | --- | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000 | N
|  | Base Unit - Digital Input DI1 |  | Y | 8915 | --- |  | --- | --- | --- | --- | ---
|  |  | Count | Y | 8915 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 8917 | seconds | 2 | INT32U | R | --- | 0 | Y
|  | Base Unit - Digital Input DI2 |  | Y | 8919 | --- |  | --- | --- | --- | --- | ---
|  |  | Count | Y | 8919 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 8921 | seconds | 2 | INT32U | R | --- | 0 | Y
|  | Base Unit - Digital Input DI3 |  | Y | 8923 | --- |  | --- | --- | --- | --- | ---
|  |  | Count | Y | 8923 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 8925 | seconds | 2 | INT32U | R | --- | 0 | Y
|  | Base Unit - Digital Input DI4 |  | Y | 8927 | --- |  | --- | --- | --- | --- | ---
|  |  | Count | Y | 8927 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 8929 | seconds | 2 | INT32U | R | --- | 0 | Y
| Digital Outputs Setup |  |  | Y | 9187 | --- |  | --- | --- | --- | --- | ---
|  | Base Unit - Digital Output DO1 |  | Y | 9187 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 9187 | --- | 1 | INT16U | R | 201 – 299 | 201 | N | First digit (2) indicates point is digital output Second digit indicates module type 0 = Generic Digital output Third digit indicates output type 1 = solid state relay 2 = electromechanical relay
|  |  | Label | Y | 9188 | --- | 20 | UTF8 | RWC | --- | "Digital Output DO1" | Y
|  |  | Behavioral Mode | Y | 9209 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | Y | 0 = Normal (forced by a control mode of Energy) 1 = Timed (forced by a control mode of Demand Sync) 2 = Coil Hold
|  |  | On Time For Timed Mode | Y | 9210 | seconds | 1 | INT16U | RWC | --- | 1 | Y | The time for the output to remain energized when the output is energized in timed mode.
|  | Base Unit - Digital Output DO2 |  | Y | 9211 | --- |  | --- | --- | --- | --- | ---
|  |  | Type | Y | 9211 | --- | 1 | INT16U | R | 201 – 299 | 201 | N
|  |  | Label | Y | 9212 | --- | 20 | UTF8 | RWC | --- | "Digital Output DO2" | Y
|  |  | Behavioral Mode | Y | 9233 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | Y | 0 = Normal 1 = Timed 2 = Coil Hold
|  |  | On Time For Timed Mode | Y | 9234 | seconds | 1 | INT16U | RWC | --- | 1 | Y | The time for the output to remain energized when the output is energized in timed mode.
| Digital Outputs Status |  |  | Y | 9667 | --- |  | --- | --- | --- | --- | ---
|  | On/Off Status |  | Y | 9667 | --- |  | --- | --- | --- | --- | ---
|  |  | Digital Output Status – Base Unit | Y | 9667 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000 | Y
|  | Base Unit - Digital Output DO1 |  | Y | 9672 | --- |  | --- | --- | --- | --- | ---
|  |  | Operating Mode Status | Y | 9672 | --- | 1 | INT16U | R | 0 – 1 | 0 | N | 0 = Normal, 1 = Override Operating Mode is changed by command. Override is considered a temporary condition used for troubleshooting. The state is volatile. That is to say that if the meter resets, the digital output will revert to normal operation.
|  |  | Control Mode Status | Y | 9673 | --- | 1 | INT16U | R | 0 – 3 | 0 | N | 0 = External 1 = Demand Sync 2 = Alarm 3 = Energy (Energy control modes are not available for electromechanical relays.)
|  |  | Behavioral Mode Status | Y | 9674 | --- | 1 | INT16U | R | 0 – 2 | 0 | Y | 0 = Normal 1 = Timed 2 = Coil Hold (Behavioral Mode will be forced to Normal when in Override Operating Mode.)
|  |  | Count | Y | 9675 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 9677 | seconds | 2 | INT32U | R | --- | 0 | Y
|  | Base Unit - Digital Output DO2 |  | Y | 9680 | --- |  | --- | --- | --- | --- | ---
|  |  | Operating Mode Status | Y | 9680 | --- | 1 | INT16U | R | 0 – 1 | 0 | N
|  |  | Control Mode Status | Y | 9681 | --- | 1 | INT16U | R | 0 – 3 | 0 | N
|  |  | Behavioral Mode Status | Y | 9682 | --- | 1 | INT16U | R | 0 – 2 | 0 | Y
|  |  | Count | Y | 9683 | --- | 2 | INT32U | R | --- | 0 | Y
|  |  | On Time | Y | 9685 | seconds | 2 | INT32U | R | --- | 0 | Y
Alarms |  |  |  | Y | 11000 | --- |  | --- | --- | --- | --- | ---
| Alarm Status |  |  | Y | 11010 | --- |  | --- | --- | --- | --- | ---
|  | Detected Priority Status |  | Y | 11010 | --- |  | --- | --- | --- | --- | ---
|  |  | Detected Priority Status Bitmap | Y | 11010 | --- | 1 | BITMAP | R | 0x0000 - 0x001F | 0 | N | Bit 01 = 1 if any priority 1-3 alarm is active Bit 02 = 1 if a “High” (1) priority alarm is active Bit 03 = 1 if a “Medium” (2) priority alarm is active Bit 04 = 1 if a “Low” (3) priority alarm is active Bit 05 = 1 if a "None" (0) priority alarm is active
|  | Enabled Alarm Bitmaps |  | Y | 11040 | --- |  | --- | --- | --- | --- | ---
|  |  | Standard – 1 second 1 | Y | 11040 | --- | 1 | BITMAP | R |  | 0 | N | 0 = Disabled; 1 = Enabled
|  |  | Standard – 1 second 2 | Y | 11041 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Standard – 1 second 3 | Y | 11042 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Unary | Y | 11050 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Digital 1 | Y | 11051 | --- | 1 | BITMAP | R |  | 0 | N
|  | Detected Alarm Bitmaps |  | Y | 11059 | --- |  | --- | --- | --- | --- | ---
|  |  | Standard – 1 second Group 1 | Y | 11059 | --- | 1 | BITMAP | R |  | 0 | N | 0 = Not Detected; 1 = Detected
|  |  | Standard – 1 second Group 2 | Y | 11060 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Standard – 1 second Group 3 | Y | 11061 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Unary | Y | 11069 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Digital Group 1 | Y | 11070 | --- | 1 | BITMAP | R |  | 0 | N
|  | Unacknowledged High Priority Alarm Bitmaps |  | Y | 11078 | --- |  | --- | --- | --- | --- | ---
|  |  | Standard – 1 second 1 | Y | 11078 | --- | 1 | BITMAP | R |  | 0 | N | 0 = Acknowledged; 1 = Unacknowledged
|  |  | Standard – 1 second 2 | Y | 11079 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Standard – 1 second 3 | Y | 11080 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Unary | Y | 11088 | --- | 1 | BITMAP | R |  | 0 | N
|  |  | Digital 1 | Y | 11089 | --- | 1 | BITMAP | R |  | 0 | N
| Alarm Event Queue |  |  | Y | 11111 | --- |  | --- | --- | --- | --- | ---
|  |  | Version of Event Queue | Y | 11111 | --- | 1 | INT16U | R |  | 0 | N
|  |  | Size of Event Queue | Y | 11113 | --- | 1 | INT16U | R |  | 100 | N
|  |  | Number of Entries in Event Queue | Y | 11114 | --- | 1 | INT16U | R | 0 – 100 | 0 | Y
|  |  | Entry Number of Most Recent Event | Y | 11115 | --- | 1 | INT16U | R |  | 0 | Y | Rolls over from 65535 to 0.
|  | Entry 001 |  | Y | 11116 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11116 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11117 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11121 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11122 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11123 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11127 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 002 |  | Y | 11128 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11128 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11129 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11133 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11134 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11135 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11139 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 003 |  | Y | 11140 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11140 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11141 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11145 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11146 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11147 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11151 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 004 |  | Y | 11152 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11152 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11153 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11157 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11158 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11159 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11163 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 005 |  | Y | 11164 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11164 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11165 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11169 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11170 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11171 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11175 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 006 |  | Y | 11176 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11176 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11177 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11181 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11182 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11183 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11187 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 007 |  | Y | 11188 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11188 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11189 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11193 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11194 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11195 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11199 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 008 |  | Y | 11200 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11200 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11201 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11205 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11206 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11207 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11211 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 009 |  | Y | 11212 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11212 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11213 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11217 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11218 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11219 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11223 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 010 |  | Y | 11224 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11224 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11225 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11229 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11230 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11231 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11235 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 011 |  | Y | 11236 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11236 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11237 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11241 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11242 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11243 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11247 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 012 |  | Y | 11248 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11248 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11249 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11253 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11254 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11255 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11259 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 013 |  | Y | 11260 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11260 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11261 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11265 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11266 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11267 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11271 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 014 |  | Y | 11272 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11272 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11273 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11277 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11278 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11279 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11283 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 015 |  | Y | 11284 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11284 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11285 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11289 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11290 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11291 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11295 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 016 |  | Y | 11296 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11296 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11297 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11301 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11302 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11303 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11307 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 017 |  | Y | 11308 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11308 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11309 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11313 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11314 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11315 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11319 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 018 |  | Y | 11320 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11320 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11321 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11325 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11326 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11327 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11331 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 019 |  | Y | 11332 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11332 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11333 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11337 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11338 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11339 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11343 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 020 |  | Y | 11344 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11344 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11345 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11349 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11350 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11351 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11355 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 021 |  | Y | 11356 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11356 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11357 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11361 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11362 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11363 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11367 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 022 |  | Y | 11368 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11368 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11369 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11373 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11374 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11375 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11379 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 023 |  | Y | 11380 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11380 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11381 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11385 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11386 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11387 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11391 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 024 |  | Y | 11392 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11392 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11393 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11397 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11398 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11399 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11403 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 025 |  | Y | 11404 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11404 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11405 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11409 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11410 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11411 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11415 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 026 |  | Y | 11416 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11416 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11417 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11421 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11422 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11423 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11427 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 027 |  | Y | 11428 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11428 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11429 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11433 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11434 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11435 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11439 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 028 |  | Y | 11440 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11440 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11441 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11445 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11446 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11447 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11451 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 029 |  | Y | 11452 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11452 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11453 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11457 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11458 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11459 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11463 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 030 |  | Y | 11464 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11464 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11465 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11469 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11470 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11471 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11475 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 031 |  | Y | 11476 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11476 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11477 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11481 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11482 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11483 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11487 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 032 |  | Y | 11488 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11488 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11489 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11493 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11494 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11495 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11499 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 033 |  | Y | 11500 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11500 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11501 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11505 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11506 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11507 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11511 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 034 |  | Y | 11512 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11512 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11513 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11517 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11518 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11519 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11523 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 035 |  | Y | 11524 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11524 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11525 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11529 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11530 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11531 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11535 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 036 |  | Y | 11536 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11536 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11537 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11541 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11542 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11543 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11547 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 037 |  | Y | 11548 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11548 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11549 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11553 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11554 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11555 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11559 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 038 |  | Y | 11560 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11560 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11561 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11565 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11566 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11567 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11571 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 039 |  | Y | 11572 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11572 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11573 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11577 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11578 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11579 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11583 | --- | 1 | INT16U | R |  | N/A | N
|  | Entry 040 |  | Y | 11584 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 11584 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Date/Time | Y | 11585 | --- | 4 | DATETIME | R |  | N/A | N
|  |  | Record Type | Y | 11589 | --- | 1 | INT16U | R |  | N/A | N | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 11590 | --- | 1 | INT16U | R |  | N/A | N | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 11591 | --- | 4 | INT16U | R |  | N/A | N
|  |  | Sequence Number | Y | 11595 | --- | 1 | INT16U | R |  | N/A | N
| Alarm History Log |  |  | Y | 12316 | --- |  | --- | --- | --- | --- | ---
|  |  | Size of History Log | Y | 12316 | --- | 1 | INT16U | R |  | 25 | N
|  |  | Number of Entries in History Log | Y | 12317 | --- | 1 | INT16U | R |  | 0 | Y
|  |  | Entry Number of Most Recent Event | Y | 12318 | --- | 1 | INT16U | R |  | 0 | Y | Value rolls over from 65535 (0xFFFF) to 0.
|  | Entry 001 |  | Y | 12319 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12319 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12320 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12324 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12325 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12326 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12330 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 002 |  | Y | 12331 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12331 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12332 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12336 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12337 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12338 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12342 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 003 |  | Y | 12343 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12343 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12344 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12348 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12349 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12350 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12354 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 004 |  | Y | 12355 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12355 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12356 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12360 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12361 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12362 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12366 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 005 |  | Y | 12367 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12367 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12368 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12372 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12373 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12374 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12378 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 006 |  | Y | 12379 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12379 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12380 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12384 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12385 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12386 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12390 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 007 |  | Y | 12391 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12391 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12392 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12396 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12397 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12398 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12402 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 008 |  | Y | 12403 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12403 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12404 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12408 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12409 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12410 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12414 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 009 |  | Y | 12415 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12415 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12416 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12420 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12421 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12422 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12426 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 010 |  | Y | 12427 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12427 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12428 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12432 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12433 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12434 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12438 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 011 |  | Y | 12439 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12439 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12440 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12444 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12445 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12446 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12450 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 012 |  | Y | 12451 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12451 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12452 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12456 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12457 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12458 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12462 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 013 |  | Y | 12463 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12463 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12464 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12468 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12469 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12470 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12474 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 014 |  | Y | 12475 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12475 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12476 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12480 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12481 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12482 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12486 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 015 |  | Y | 12487 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12487 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12488 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12492 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12493 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12494 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12498 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 016 |  | Y | 12499 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12499 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12500 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12504 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12505 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12506 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12510 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 017 |  | Y | 12511 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12511 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12512 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12516 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12517 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12518 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12522 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 018 |  | Y | 12523 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12523 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12524 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12528 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12529 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12530 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12534 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 019 |  | Y | 12535 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12535 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12536 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12540 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12541 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12542 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12546 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 020 |  | Y | 12547 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12547 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12548 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12552 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12553 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12554 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12558 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 021 |  | Y | 12559 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12559 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12560 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12564 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12565 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12566 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12570 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 022 |  | Y | 12571 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12571 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12572 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12576 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12577 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12578 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12582 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 023 |  | Y | 12583 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12583 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12584 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12588 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12589 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12590 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12594 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 024 |  | Y | 12595 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12595 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12596 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12600 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12601 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12602 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12606 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 025 |  | Y | 12607 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12607 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12608 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12612 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12613 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12614 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12618 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 026 |  | Y | 12619 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12619 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12620 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12624 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12625 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12626 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12630 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 027 |  | Y | 12631 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12631 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12632 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12636 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12637 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12638 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12642 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 028 |  | Y | 12643 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12643 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12644 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12648 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12649 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12650 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12654 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 029 |  | Y | 12655 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12655 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12656 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12660 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12661 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12662 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12666 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 030 |  | Y | 12667 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12667 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12668 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12672 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12673 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12674 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12678 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 031 |  | Y | 12679 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12679 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12680 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12684 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12685 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12686 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12690 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 032 |  | Y | 12691 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12691 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12692 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12696 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12697 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12698 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12702 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 033 |  | Y | 12703 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12703 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12704 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12708 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12709 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12710 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12714 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 034 |  | Y | 12715 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12715 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12716 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12720 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12721 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12722 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12726 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 035 |  | Y | 12727 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12727 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12728 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12732 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12733 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12734 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12738 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 036 |  | Y | 12739 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12739 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12740 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12744 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12745 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12746 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12750 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 037 |  | Y | 12751 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12751 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12752 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12756 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12757 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12758 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12762 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 038 |  | Y | 12763 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12763 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12764 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12768 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12769 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12770 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12774 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 039 |  | Y | 12775 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12775 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12776 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12780 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12781 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12782 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12786 | --- | 1 | INT16U | R |  | N/A | Y
|  | Entry 040 |  | Y | 12787 | --- |  | --- | --- | --- | --- | ---
|  |  | Entry Number | Y | 12787 | --- | 1 | INT16U | R |  | N/A | Y
|  |  | Date/Time | Y | 12788 | --- | 4 | DATETIME | R |  | N/A | Y
|  |  | Record Type | Y | 12792 | --- | 1 | INT16U | R |  | N/A | Y | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | 12793 | --- | 1 | INT16U | R |  | N/A | Y | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | 12794 | --- | 4 | INT16U | R |  | N/A | Y
|  |  | Sequence Number | Y | 12798 | --- | 1 | INT16U | R |  | N/A | Y
| Alarm Counters |  |  | Y | 13519 | --- |  | --- | --- | --- | --- | ---
|  | Summary |  | Y | 13519 | --- |  | --- | --- | --- | --- | ---
|  |  | Total Counter | Y | 13519 | --- | 1 | INT16U | R | --- | 0 | Y
|  |  | Low Priority Counter | Y | 13520 | --- | 1 | INT16U | R | --- | 0 | Y
|  |  | Medium Priority Counter | Y | 13521 | --- | 1 | INT16U | R | --- | 0 | Y
|  |  | High Priority Counter | Y | 13522 | --- | 1 | INT16U | R | --- | 0 | Y
|  | 1-Second Alarms - Standard |  | Y | 13523 | --- |  | --- | --- | --- | --- | ---
|  |  | Over Current, Phase | Y | 13523 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Under Current, Phase | Y | 13524 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Current, Neutral | Y | 13525 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Current, Ground | Y | 13526 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Voltage, L-L | Y | 13527 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Under Voltage, L-L | Y | 13528 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Voltage, L-N | Y | 13529 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Under Voltage, L-N | Y | 13530 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Power, Active | Y | 13531 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Power, Reactive | Y | 13532 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Power, Apparent | Y | 13533 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Lead Power Factor, True | Y | 13534 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Lag Power Factor, True | Y | 13535 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Lead Power Factor, Displacement | Y | 13536 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Lag Power Factor, Displacement | Y | 13537 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Active Power, Present | Y | 13538 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Active Power, Last | Y | 13539 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Active Power, Predicted | Y | 13540 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Reactive Power, Present | Y | 13541 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Reactive Power, Last | Y | 13542 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Reactive Power, Predicted | Y | 13543 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Apparent Power, Present | Y | 13544 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Apparent Power, Last | Y | 13545 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Demand, Apparent Power, Predicted | Y | 13546 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Frequency | Y | 13547 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Under Frequency | Y | 13548 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Voltage Unbalance | Y | 13549 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Over Voltage Total Harmonic Distortion | Y | 13550 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Phase Loss | Y | 13551 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  | Unary Alarms |  | Y | 13623 | --- |  | --- | --- | --- | --- | ---
|  |  | Meter Powerup (Control Power Loss) | Y | 13623 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Meter Reset | Y | 13624 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Meter Diagnostic | Y | 13625 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Phase Reversal | Y | 13626 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  | Digital Alarms |  | Y | 13633 | --- |  | --- | --- | --- | --- | ---
|  |  | Digital Alarm DI1 | Y | 13633 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Digital Alarm DI2 | Y | 13634 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Digital Alarm DI3 | Y | 13635 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
|  |  | Digital Alarm DI4 | Y | 13636 | --- | 1 | INT16U | R | 0 – 9999 | 0 | Y
| 1-Second Alarms - Standard |  |  | Y | 14000 | --- |  | --- | --- | --- | --- | ---
|  | Over Current, Phase |  | Y | 14000 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14000 | --- | 2 | INT32U | RWC |  | 0x10848B80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14002 | --- | 1 | INT16U | R |  | R_IA_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14003 | --- | 1 | INT16U | R |  | R_IB_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14004 | --- | 1 | INT16U | R |  | R_IC_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14005 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | 14007 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14009 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14011 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Base | Y | 14013 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Under Current, Phase |  | Y | 14020 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14020 | --- | 2 | INT32U | RWC |  | 0x11048B80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14022 | --- | 1 | INT16U | R |  | R_IA_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14023 | --- | 1 | INT16U | R |  | R_IB_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14024 | --- | 1 | INT16U | R |  | R_IC_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14025 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | 14027 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14029 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Dropout Time Delay | Y | 14031 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14033 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Current, Neutral |  | Y | 14040 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14040 | --- | 2 | INT32U | RWC |  | 0x10849400 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14042 | --- | 1 | INT16U | R |  | R_IN_50_60_CYC_RMS | N
|  |  | Reserved | Y | 14043 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Reserved | Y | 14044 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14045 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | 14047 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14049 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14051 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14053 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Current, Ground |  | Y | 14060 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14060 | --- | 2 | INT32U | RWC |  | 0x10849C80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14062 | --- | 1 | INT16U | R |  | R_IG_50_60_CYC_RMS | N
|  |  | Reserved | Y | 14063 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Reserved | Y | 14064 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14065 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | 14067 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14069 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14071 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14073 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Voltage, L-L |  | Y | 14080 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14080 | --- | 2 | INT32U | RWC |  | 0x1082AB80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14082 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14083 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14084 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14085 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Pickup Time Delay | Y | 14087 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14089 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14091 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14093 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Under Voltage, L-L |  | Y | 14100 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14100 | --- | 2 | INT32U | RWC |  | 0x1102AB80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14102 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14103 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14104 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14105 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | 14107 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14109 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Dropout Time Delay | Y | 14111 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14113 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Voltage, L-N |  | Y | 14120 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14120 | --- | 2 | INT32U | RWC |  | 0x1082A380 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14122 | --- | 1 | INT16U | R |  | R_VAN_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14123 | --- | 1 | INT16U | R |  | R_VBN_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14124 | --- | 1 | INT16U | R |  | R_VCN_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14125 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Pickup Time Delay | Y | 14127 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14129 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14131 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14133 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Under Voltage, L-N |  | Y | 14140 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14140 | --- | 2 | INT32U | RWC |  | 0x1102A380 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14142 | --- | 1 | INT16U | R |  | R_VAN_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14143 | --- | 1 | INT16U | R |  | R_VBN_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14144 | --- | 1 | INT16U | R |  | R_VCN_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14145 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | 14147 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14149 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Dropout Time Delay | Y | 14151 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14153 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Power, Active |  | Y | 14160 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14160 | --- | 2 | INT32U | RWC |  | 0x10875580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14162 | --- | 1 | INT16U | R |  | R_PTOT_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14163 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14164 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14165 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14167 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14169 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14171 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14173 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Power, Reactive |  | Y | 14180 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14180 | --- | 2 | INT32U | RWC |  | 0x10895580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14182 | --- | 1 | INT16U | R |  | R_QTOT_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14183 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14184 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14185 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14187 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14189 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14191 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14193 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Power, Apparent |  | Y | 14200 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14200 | --- | 2 | INT32U | RWC |  | 0x108B5580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14202 | --- | 1 | INT16U | R |  | R_STOT_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14203 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14204 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14205 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14207 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14209 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14211 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14213 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Leading Power Factor, True |  | Y | 14220 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14220 | --- | 2 | INT32U | RWC |  | 0x118EC380 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14222 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_TRUE | N
|  |  | Reserved | Y | 14223 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_TRUE | N
|  |  | Reserved | Y | 14224 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_TRUE | N
|  |  | Pickup Setpoint | Y | 14225 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14227 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14229 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14231 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14233 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Lagging Power Factor, True |  | Y | 14240 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14240 | --- | 2 | INT32U | RWC |  | 0x120EC380 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14242 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_TRUE | N
|  |  | Reserved | Y | 14243 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_TRUE | N
|  |  | Reserved | Y | 14244 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_TRUE | N
|  |  | Pickup Setpoint | Y | 14245 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14247 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14249 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14251 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14253 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Leading Power Factor, Displacement |  | Y | 14260 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14260 | --- | 2 | INT32U | RWC |  | 0x118ECB80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14262 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_DISP | N
|  |  | Reserved | Y | 14263 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_DISP | N
|  |  | Reserved | Y | 14264 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_DISP | N
|  |  | Pickup Setpoint | Y | 14265 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14267 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14269 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14271 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14273 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Lagging Power Factor, Displacement |  | Y | 14280 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14280 | --- | 2 | INT32U | RWC |  | 0x120ECB80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14282 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_DISP | N
|  |  | Reserved | Y | 14283 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_DISP | N
|  |  | Reserved | Y | 14284 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_DISP | N
|  |  | Pickup Setpoint | Y | 14285 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14287 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14289 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14291 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14293 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Active Power, Present |  | Y | 14300 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14300 | --- | 2 | INT32U | RWC |  | 0x1086E580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14302 | --- | 1 | INT16U | R |  | R_DMD_CH_01_PRES | N
|  |  | Source Register B | Y | 14303 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14304 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14305 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14307 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14309 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14311 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14313 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Active Power, Last |  | Y | 14320 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14320 | --- | 2 | INT32U | RWC |  | 0x1086D580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14322 | --- | 1 | INT16U | R |  | R_DMD_CH_01_LAST | N
|  |  | Source Register B | Y | 14323 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14324 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14325 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14327 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14329 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14331 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14333 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Active Power, Predicted |  | Y | 14340 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14340 | --- | 2 | INT32U | RWC |  | 0x1086DD80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14342 | --- | 1 | INT16U | R |  | R_DMD_CH_01_PREDICTED | N
|  |  | Source Register B | Y | 14343 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14344 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14345 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14347 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14349 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14351 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14353 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Reactive Power, Present |  | Y | 14360 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14360 | --- | 2 | INT32U | RWC |  | 0x1088E580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14362 | --- | 1 | INT16U | R |  | R_DMD_CH_02_PRES | N
|  |  | Source Register B | Y | 14363 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14364 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14365 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14367 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14369 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14371 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14373 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Reactive Power, Last |  | Y | 14380 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14380 | --- | 2 | INT32U | RWC |  | 0x1088D580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14382 | --- | 1 | INT16U | R |  | R_DMD_CH_02_LAST | N
|  |  | Source Register B | Y | 14383 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14384 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14385 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14387 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14389 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14391 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14393 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Reactive Power, Predicted |  | Y | 14400 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14400 | --- | 2 | INT32U | RWC |  | 0x1088DD80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14402 | --- | 1 | INT16U | R |  | R_DMD_CH_02_PREDICTED | N
|  |  | Source Register B | Y | 14403 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14404 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14405 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14407 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14409 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14411 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14413 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Apparent Power, Present |  | Y | 14420 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14420 | --- | 2 | INT32U | RWC |  | 0x108AE580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14422 | --- | 1 | INT16U | R |  | R_DMD_CH_03_PRES | N
|  |  | Source Register B | Y | 14423 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14424 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14425 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14427 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14429 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14431 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14433 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Apparent Power, Last |  | Y | 14440 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14440 | --- | 2 | INT32U | RWC |  | 0x108AD580 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14442 | --- | 1 | INT16U | R |  | R_DMD_CH_03_LAST | N
|  |  | Source Register B | Y | 14443 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14444 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14445 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14447 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14449 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14451 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14453 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Demand, Apparent Power, Predicted |  | Y | 14460 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14460 | --- | 2 | INT32U | RWC |  | 0x108ADD80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14462 | --- | 1 | INT16U | R |  | R_DMD_CH_03_PREDICTED | N
|  |  | Source Register B | Y | 14463 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Source Register C | Y | 14464 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14465 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | 14467 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14469 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14471 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14473 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Frequency |  | Y | 14480 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14480 | --- | 2 | INT32U | RWC |  | 0x108C0000 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14482 | --- | 1 | INT16U | R |  | R_FREQ_50_60_CYC_AVG | N
|  |  | Reserved | Y | 14483 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Reserved | Y | 14484 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14485 | Hz | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14487 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14489 | Hz | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14491 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14493 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Under Frequency |  | Y | 14500 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14500 | --- | 2 | INT32U | RWC |  | 0x110C0000 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14502 | --- | 1 | INT16U | R |  | R_FREQ_50_60_CYC_AVG | N
|  |  | Reserved | Y | 14503 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Reserved | Y | 14504 | --- | 1 | INT16U | R |  | N/A | N
|  |  | Pickup Setpoint | Y | 14505 | Hz | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | 14507 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14509 | Hz | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14511 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14513 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Voltage Unbalance |  | Y | 14520 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14520 | --- | 2 | INT32U | RWC |  | 0x1082BB80 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14522 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_UNB | N
|  |  | Source Register B | Y | 14523 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_UNB | N
|  |  | Source Register C | Y | 14524 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_UNB | N
|  |  | Pickup Setpoint | Y | 14525 | % | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14527 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14529 | % | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14531 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14533 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Over Voltage Total Harmonic Distortion |  | Y | 14540 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14540 | --- | 2 | INT32U | RWC |  | 0x1082B000 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14542 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_THD | N
|  |  | Source Register B | Y | 14543 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_THD | N
|  |  | Source Register C | Y | 14544 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_THD | N
|  |  | Pickup Setpoint | Y | 14545 | % | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14547 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14549 | % | 2 | FLOAT32 | RWC | See User Notes | 0 | Y | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | 14551 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14553 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Phase Loss |  | Y | 14560 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 14560 | --- | 2 | INT32U | RWC |  | 0x12820380 | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14562 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS | N
|  |  | Source Register B | Y | 14563 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS | N
|  |  | Source Register C | Y | 14564 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS | N
|  |  | Pickup Setpoint | Y | 14565 | V | 2 | FLOAT32 | RWC |  | 0 | Y | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | 14567 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14569 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Y
|  |  | Dropout Time Delay | Y | 14571 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14573 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
| 1-Second Alarms - Custom |  |  | Y | 14800 | --- |  | --- | --- | --- | --- | ---
|  | Custom Alarm 1 |  | Y | 14800 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 14800 | --- | 20 | UTF8 | RWC |  |  | Y
|  |  | Attributes | Y | 14820 | --- | 2 | INT32U | RWC |  |  | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14822 | --- | 1 | INT16U | RWC |  |  | Y
|  |  | Pickup Setpoint | Y | 14825 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14827 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14829 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14831 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14833 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Custom Alarm 2 |  | Y | 14840 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 14840 | --- | 20 | UTF8 | RWC |  |  | Y
|  |  | Attributes | Y | 14860 | --- | 2 | INT32U | RWC |  |  | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14862 | --- | 1 | INT16U | RWC |  |  | Y
|  |  | Pickup Setpoint | Y | 14865 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14867 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14869 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14871 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14873 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Custom Alarm 3 |  | Y | 14880 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 14880 | --- | 20 | UTF8 | RWC |  |  | Y
|  |  | Attributes | Y | 14900 | --- | 2 | INT32U | RWC |  |  | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14902 | --- | 1 | INT16U | RWC |  |  | Y
|  |  | Pickup Setpoint | Y | 14905 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14907 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14909 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14911 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14913 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Custom Alarm 4 |  | Y | 14920 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 14920 | --- | 20 | UTF8 | RWC |  |  | Y
|  |  | Attributes | Y | 14940 | --- | 2 | INT32U | RWC |  |  | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14942 | --- | 1 | INT16U | RWC |  |  | Y
|  |  | Pickup Setpoint | Y | 14945 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14947 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14949 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14951 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14953 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Custom Alarm 5 |  | Y | 14960 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 14960 | --- | 20 | UTF8 | RWC |  |  | Y
|  |  | Attributes | Y | 14980 | --- | 2 | INT32U | RWC |  |  | Y | See Alarm Attributes for details.
|  |  | Source Register A | Y | 14982 | --- | 1 | INT16U | RWC |  |  | Y
|  |  | Pickup Setpoint | Y | 14985 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Pickup Time Delay | Y | 14987 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Dropout Setpoint | Y | 14989 | --- | 2 | FLOAT32 | RWC |  | 0 | Y
|  |  | Dropout Time Delay | Y | 14991 | seconds | 2 | INT32U | RWC | --- | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 14993 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Meter Power Up (Control Power Loss) |  | Y | 16200 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16200 | --- | 2 | INT32U | RWC | --- | 0x84000019 | Y | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | 16202 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Meter Reset |  | Y | 16210 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16210 | --- | 2 | INT32U | RWC | --- | 0x84800019 | Y | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | 16212 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Meter Diagnostic |  | Y | 16220 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16220 | --- | 2 | INT32U | RWC | --- | 0x851A0000 | Y | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | 16222 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Phase Reversal |  | Y | 16230 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16230 | --- | 2 | INT32U | RWC | --- | 0x83000000 | Y | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | 16232 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
| Digital Alarms |  |  | Y | 16300 | --- |  | --- | --- | --- | --- | ---
|  | Digital Alarm DI1 |  | Y | 16300 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16300 | --- | 2 | INT32U | RWC | --- | 0x95900800 | Y | See Alarm Attributes for details.
|  |  | Pickup Time Delay | Y | 16302 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Dropout Time Delay | Y | 16304 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Digital Outputs to Associate – Standard | Y | 16306 | --- | 1 | BITMAP | RWC | --- | --- | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Digital Alarm DI2 |  | Y | 16314 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16314 | --- | 2 | INT32U | RWC | --- | 0x95901000 | Y | See Alarm Attributes for details.
|  |  | Pickup Time Delay | Y | 16316 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Dropout Time Delay | Y | 16318 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Digital Outputs to Associate – Standard | Y | 16320 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Digital Alarm DI3 |  | Y | 16328 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16328 | --- | 2 | INT32U | RWC | --- | 0x95901800 | Y | See Alarm Attributes for details.
|  |  | Pickup Time Delay | Y | 16330 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Dropout Time Delay | Y | 16332 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Digital Outputs to Associate – Standard | Y | 16334 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Digital Alarm DI4 |  | Y | 16342 | --- |  | --- | --- | --- | --- | ---
|  |  | Attributes | Y | 16342 | --- | 2 | INT32U | RWC | --- | 0x95902000 | Y | See Alarm Attributes for details.
|  |  | Pickup Time Delay | Y | 16344 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Dropout Time Delay | Y | 16346 | seconds | 2 | INT32U | RWC | --- | --- | Y
|  |  | Digital Outputs to Associate – Standard | Y | 16348 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
| Logic Alarms |  |  | Y | 18052 | --- |  | --- | --- | --- | --- | ---
|  | Logic Alarm 1 |  | Y | 18052 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18052 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 1" | Y
|  |  | Attributes | Y | 18072 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18074 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18075 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18076 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18077 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18078 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 2 |  | Y | 18085 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18085 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 2" | Y
|  |  | Attributes | Y | 18105 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18107 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18108 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18109 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18110 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18111 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 3 |  | Y | 18118 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18118 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 3" | Y
|  |  | Attributes | Y | 18138 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18140 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18141 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18142 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18143 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18144 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 4 |  | Y | 18151 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18151 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 4" | Y
|  |  | Attributes | Y | 18171 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18173 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18174 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18175 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18176 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18177 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 5 |  | Y | 18184 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18184 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 5" | Y
|  |  | Attributes | Y | 18204 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18206 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18207 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18208 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18209 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18210 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 6 |  | Y | 18217 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18217 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 6" | Y
|  |  | Attributes | Y | 18237 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18239 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18240 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18241 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18242 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18243 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 7 |  | Y | 18250 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18250 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 7" | Y
|  |  | Attributes | Y | 18270 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18272 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18273 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18274 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18275 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18276 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 8 |  | Y | 18283 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18283 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 8" | Y
|  |  | Attributes | Y | 18303 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18305 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18306 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18307 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18308 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18309 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 9 |  | Y | 18316 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18316 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 9" | Y
|  |  | Attributes | Y | 18336 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18338 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18339 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18340 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18341 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18342 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  | Logic Alarm 10 |  | Y | 18349 | --- |  | --- | --- | --- | --- | ---
|  |  | Label | Y | 18349 | --- | 20 | UTF8 | RWC | --- | "Logic Alarm 10" | Y
|  |  | Attributes | Y | 18369 | --- | 2 | INT32U | RWC | --- | 0 | Y | See Alarm Attributes for details.
|  |  | Source Alarm A | Y | 18371 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm B | Y | 18372 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm C | Y | 18373 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Source Alarm D | Y | 18374 | --- | 1 | INT16U | RWC | 0 – 190 | 0 | Y
|  |  | Digital Outputs to Associate – Standard | Y | 18375 | --- | 1 | BITMAP | RWC |  | 0 | Y | Bitmap of digital outputs to associate with this alarm.
|  |  | Data Type Custom Alarm 1 | Y | 18436 | --- | 1 | INT16U | RWC | 1 – 7 | 1 | Y | These are part of the custom alarms setup
|  |  | Data Type Custom Alarm 2 | Y | 18437 | --- | 1 | INT16U | RWC | 1 – 7 | 1 | Y
|  |  | Data Type Custom Alarm 3 | Y | 18438 | --- | 1 | INT16U | RWC | 1 – 7 | 1 | Y
|  |  | Data Type Custom Alarm 4 | Y | 18439 | --- | 1 | INT16U | RWC | 1 – 7 | 1 | Y
|  |  | Data Type Custom Alarm 5 | Y | 18440 | --- | 1 | INT16U | RWC | 1 – 7 | 1 | Y
Files |  |  |  | Y | 19000 | --- | 0 | --- | --- | --- | --- | ---
| Datalogs |  |  | Y | 19000 | --- |  | --- | --- | --- | --- | ---
|  | Energy Log |  | Y | 19000 | --- |  | --- | --- | --- | --- | ---
|  |  | Logging Status | Y | 19000 | --- | 1 | INT16U | RWC | 0-1 | 0 | Y | 0 = Disabled, 1 = Enabled
|  |  | Allocated File Size | Y | 19001 | --- | 1 | INT16U | R | --- | 0 | N | Max number of records in file
|  |  | Allocated Record Size | Y | 19002 | --- | 1 | INT16U | R | --- | 0 | N | Record length in registers
|  |  | Record Management Method | Y | 19003 | --- | 1 | INT16U | RWC | 0-1 | 0 | Y | 0 = Circular, 1 = Fill and hold
|  |  | File Status | Y | 19004 | --- | 1 | INT16U | R | --- | 0 | N | 0 = OK, 200 = Internal failure, 210 = Disabled due to config 220 = Disabled due to Null config.
|  |  | Number of records in file | Y | 19005 | --- | 1 | INT16U | R | --- | 0 | Y | Number of records wriiten, resets to 0 on file clear
|  |  | First Record Sequence Number | Y | 19006 | --- | 1 | INT16U | R | --- | 0 | Y | First record in log
|  |  | Last Record Sequence Number | Y | 19007 | --- | 1 | INT16U | R | --- | 0 | Y | Last record in the log
|  |  | Topic Mode | Y | 19008 | --- | 1 | INT16U | RWC | --- | 1 | Y | 0 = Power data model, 1 = Modbus register format
|  |  | Start Time | Y | 19009 | Minuites | 1 | INT16U | RWC | --- | 0 | Y | Not used in PM5500
|  |  | Stop Time | Y | 19010 | seconds | 1 | INT16U | RWC | --- | 1440 | Y | Not used in PM5500
|  |  | Interval Control Minutes | Y | 19011 | Minuites | 1 | INT16U | RWC | 1,5,10,15,30,60.1440 | 15 | Y
|  |  | Interval Control Seconds | Y | 19012 | seconds | 1 | INT16U | RWC | 0-59 | 0 | Y
|  |  | Date/Time Last clear | Y | 19013 | --- | 4 | DATETIME | RWC | --- | N/A | Y
|  |  | Record Item 1 | Y | 19017 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 2 | Y | 19018 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 3 | Y | 19019 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 4 | Y | 19020 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 5 | Y | 19021 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 6 | Y | 19022 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 7 | Y | 19023 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 8 | Y | 19024 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 9 | Y | 19025 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 10 | Y | 19026 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 11 | Y | 19027 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 12 | Y | 19028 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 13 | Y | 19029 | --- | 1 | INT16U | RWC | --- | 0 | Y
|  |  | Record Item 14 | Y | 19030 | --- | 1 | INT16U | RWC | --- | 0 | Y
Diagnostics |  |  |  | Y | 20000 | --- |  | --- | --- | --- | --- | ---
| Self-Test Results |  |  | Y | 20000 | --- |  | --- | --- | --- | --- | ---
|  |  | Processor Loading | Y | 20000 | % | 1 | INT16U | R | 0 – 100 | 0 | N
|  | Miscellaneous Self-Test |  | Y | 20003 | --- |  | --- | --- | --- | --- | ---
|  |  | Meter Self-Test | Y | 20003 | --- | 5 | BITMAP | R |  | 0x0000 0000 0000 0000 0000 | N | 0 = OK, 1 = Error Detected Bit 01 = Summary ( on if any other bit is on - Maintenance Icon shown on HMI ) Bit 02 = RAM Failure Bit 03 = NVRAM Failure Bit 04 = RTC Failure Bit 05 = Calibration Failure Bit 06 = Clipping Detected Bit 07 = Over-Running Energy Pulse Output Bit 08 = Inp Mtr Diag Rate Exceeded/Backup RAM failure Bit 09 = Lang File Mis Match Bit 10 = Lang String Mis Match Bit 11-16 Not Used
| Energy Preset Values |  |  | Y | 20270 | --- |  | --- | --- | --- | --- | ---
|  | Accumulated Energy - 32 bit floating point values |  | Y | 20270 | --- |  | --- | --- | --- | --- | ---
|  |  | Active Energy Delivered (Into Load) | Y | 20270 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Active Energy Received (Out of Load) | Y | 20272 | kWh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Delivered | Y | 20274 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Reactive Energy Received | Y | 20276 | kVARh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Delivered | Y | 20278 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  |  | Apparent Energy Received | Y | 20280 | kVAh | 2 | FLOAT32 | R | --- | 0 | N
|  | Accumulated Energy |  | Y | 20282 | --- |  | --- | --- | --- | --- | ---
|  |  | Accumulated Energy Preset Date/Time | Y | 20282 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | Active Energy Delivered (Into Load) | Y | 20286 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Active Energy Received (Out of Load) | Y | 20290 | Wh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Delivered | Y | 20302 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Reactive Energy Received | Y | 20306 | VARh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Delivered | Y | 20318 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Apparent Energy Received | Y | 20322 | VAh | 4 | INT64 | R | --- | 0 | Y
|  |  | Size of Maint Log | Y | 20534 | --- | 1 | INT16U | R |  | 500 | N
|  |  | Number of Entries in Maint Log | Y | 20535 | --- | 1 | INT16U | R | 0 – 500 | 0 | Y
|  |  | Entry Number of Most Recent Event | Y | 20536 | --- | 2 | INT32U | R |  | 0 | Y
Meter Data (Advanced) |  |  |  | Y | 21000 | --- |  | --- | --- | --- | --- | ---
| High Speed Metering (<=100ms) |  |  | Y | 21000 | --- |  | --- | --- | --- | --- | ---
|  | Frequency | HS Frequency | Y | 21016 | Hz | 2 | FLOAT32 | R | 42 – 70 |  | N
| Power Quality (1 to 3 Seconds) |  |  | Y | 21300 | --- |  | --- | --- | --- | --- | ---
|  | Total Harmonic Distortion, Current |  | Y | 21300 | --- |  | --- | --- | --- | --- | ---
|  |  | THD Current A | Y | 21300 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | THD Current B | Y | 21302 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Current C | Y | 21304 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Current N | Y | 21306 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Current G | Y | 21308 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Current A | Y | 21310 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N | thd = (RMS of harmonics / total RMS) * 100
|  |  | thd Current B | Y | 21312 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Current C | Y | 21314 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Current N | Y | 21316 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Current G | Y | 21318 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  | Total Demand Distortion | Total Demand Distortion | Y | 21320 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  | Total Harmonic Distortion, Voltage |  | Y | 21322 | --- |  | --- | --- | --- | --- | ---
|  |  | THD Voltage A-B | Y | 21322 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage B-C | Y | 21324 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage C-A | Y | 21326 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage L-L | Y | 21328 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage A-N | Y | 21330 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage B-N | Y | 21332 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage C-N | Y | 21334 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | THD Voltage L-N | Y | 21338 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage A-B | Y | 21340 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage B-C | Y | 21342 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage C-A | Y | 21344 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage L-L | Y | 21346 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage A-N | Y | 21348 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage B-N | Y | 21350 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage C-N | Y | 21352 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  |  | thd Voltage L-N | Y | 21356 | % | 2 | FLOAT32 | R | 0 – 100 | --- | N
|  | K-Factor |  | Y | 21358 | --- |  | --- | --- | --- | --- | ---
|  |  | K-Factor A | Y | 21358 |  | 2 | FLOAT32 | R |  |  | N
|  |  | K-Factor B | Y | 21360 |  | 2 | FLOAT32 | R |  |  | N
|  |  | K-Factor C | Y | 21362 |  | 2 | FLOAT32 | R |  |  | N
|  | Crest Factor |  | Y | 21364 | --- |  | --- | --- | --- | --- | ---
|  |  | Crest Factor A | Y | 21364 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor B | Y | 21366 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor C | Y | 21368 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor N | Y | 21370 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage A-B | Y | 21372 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage B-C | Y | 21374 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage C-A | Y | 21376 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage A-N | Y | 21378 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage B-N | Y | 21380 | --- | 2 | FLOAT32 | R |  |  | N
|  |  | Crest Factor Voltage C-N | Y | 21382 | --- | 2 | FLOAT32 | R |  |  | N
|  | Fundamental Magnitudes & Angles – Current |  | Y | 21384 | --- |  | --- | --- | --- | --- | ---
|  | Fundamental Magnitudes & Angles – Voltage |  | Y | 21404 | --- |  | --- | --- | --- | --- | ---
|  |  | Voltage A-B, H1 Magnitude, % | Y | 21712 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H1 Magnitude, V | Y | 21714 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H1 Angle | Y | 21716 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H2 Magnitude, % | Y | 21718 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H2 Magnitude, V | Y | 21720 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H2 Angle | Y | 21722 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H3 Magnitude, % | Y | 21724 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H3 Magnitude, V | Y | 21726 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H3 Angle | Y | 21728 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H4 Magnitude, % | Y | 21730 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H4 Magnitude, V | Y | 21732 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H4 Angle | Y | 21734 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H5 Magnitude, % | Y | 21736 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H5 Magnitude, V | Y | 21738 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H5 Angle | Y | 21740 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H6 Magnitude, % | Y | 21742 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H6 Magnitude, V | Y | 21744 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H6 Angle | Y | 21746 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H7 Magnitude, % | Y | 21748 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H7 Magnitude, V | Y | 21750 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H7 Angle | Y | 21752 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H8 Magnitude, % | Y | 21754 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H8 Magnitude, V | Y | 21756 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H8 Angle | Y | 21758 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H9 Magnitude, % | Y | 21760 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H9 Magnitude, V | Y | 21762 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H9 Angle | Y | 21764 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H10 Magnitude, % | Y | 21766 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H10 Magnitude, V | Y | 21768 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H10 Angle | Y | 21770 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H11 Magnitude, % | Y | 21772 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H11 Magnitude, V | Y | 21774 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H11 Angle | Y | 21776 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H12 Magnitude, % | Y | 21778 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H12 Magnitude, V | Y | 21780 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H12 Angle | Y | 21782 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H13 Magnitude, % | Y | 21784 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H13 Magnitude, V | Y | 21786 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H13 Angle | Y | 21788 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H14 Magnitude, % | Y | 21790 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H14 Magnitude, V | Y | 21792 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H14 Angle | Y | 21794 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H15 Magnitude, % | Y | 21796 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H15 Magnitude, V | Y | 21798 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H15 Angle | Y | 21800 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H16 Magnitude, % | Y | 21802 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H16 Magnitude, V | Y | 21804 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H16 Angle | Y | 21806 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H17 Magnitude, % | Y | 21808 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H17 Magnitude, V | Y | 21810 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H17 Angle | Y | 21812 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H18 Magnitude, % | Y | 21814 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H18 Magnitude, V | Y | 21816 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H18 Angle | Y | 21818 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H19 Magnitude, % | Y | 21820 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H19 Magnitude, V | Y | 21822 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H19 Angle | Y | 21824 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H20 Magnitude, % | Y | 21826 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H20 Magnitude, V | Y | 21828 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H20 Angle | Y | 21830 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H21 Magnitude, % | Y | 21832 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H21 Magnitude, V | Y | 21834 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H21 Angle | Y | 21836 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H22 Magnitude, % | Y | 21838 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H22 Magnitude, V | Y | 21840 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H22 Angle | Y | 21842 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H23 Magnitude, % | Y | 21844 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H23 Magnitude, V | Y | 21846 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H23 Angle | Y | 21848 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H24 Magnitude, % | Y | 21850 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H24 Magnitude, V | Y | 21852 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H24 Angle | Y | 21854 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H25 Magnitude, % | Y | 21856 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H25 Magnitude, V | Y | 21858 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H25 Angle | Y | 21860 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H26 Magnitude, % | Y | 21862 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H26 Magnitude, V | Y | 21864 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H26 Angle | Y | 21866 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H27 Magnitude, % | Y | 21868 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H27 Magnitude, V | Y | 21870 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H27 Angle | Y | 21872 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H28 Magnitude, % | Y | 21874 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H28 Magnitude, V | Y | 21876 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H28 Angle | Y | 21878 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H29 Magnitude, % | Y | 21880 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H29 Magnitude, V | Y | 21882 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H29 Angle | Y | 21884 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H30 Magnitude, % | Y | 21886 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H30 Magnitude, V | Y | 21888 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H30 Angle | Y | 21890 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H31 Magnitude, % | Y | 21892 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H31 Magnitude, V | Y | 21894 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H31 Angle | Y | 21896 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H32 Magnitude, % | Y | 21898 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H32 Magnitude, V | Y | 21900 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H32 Angle | Y | 21902 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H33 Magnitude, % | Y | 21904 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H33 Magnitude, V | Y | 21906 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H33 Angle | Y | 21908 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H34 Magnitude, % | Y | 21910 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H34 Magnitude, V | Y | 21912 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H34 Angle | Y | 21914 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H35 Magnitude, % | Y | 21916 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H35 Magnitude, V | Y | 21918 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H35 Angle | Y | 21920 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H36 Magnitude, % | Y | 21922 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H36 Magnitude, V | Y | 21924 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H36 Angle | Y | 21926 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H37 Magnitude, % | Y | 21928 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H37 Magnitude, V | Y | 21930 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H37 Angle | Y | 21932 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H38 Magnitude, % | Y | 21934 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H38 Magnitude, V | Y | 21936 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H38 Angle | Y | 21938 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H39 Magnitude, % | Y | 21940 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H39 Magnitude, V | Y | 21942 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H39 Angle | Y | 21944 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H40 Magnitude, % | Y | 21946 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H40 Magnitude, V | Y | 21948 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H40 Angle | Y | 21950 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H41 Magnitude, % | Y | 21952 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H41 Magnitude, V | Y | 21954 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H41 Angle | Y | 21956 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H42 Magnitude, % | Y | 21958 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H42 Magnitude, V | Y | 21960 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H42 Angle | Y | 21962 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H43 Magnitude, % | Y | 21964 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H43 Magnitude, V | Y | 21966 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H43 Angle | Y | 21968 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H44 Magnitude, % | Y | 21970 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H44 Magnitude, V | Y | 21972 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H44 Angle | Y | 21974 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H45 Magnitude, % | Y | 21976 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H45 Magnitude, V | Y | 21978 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H45 Angle | Y | 21980 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H46 Magnitude, % | Y | 21982 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H46 Magnitude, V | Y | 21984 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H46 Angle | Y | 21986 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H47 Magnitude, % | Y | 21988 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H47 Magnitude, V | Y | 21990 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H47 Angle | Y | 21992 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H48 Magnitude, % | Y | 21994 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H48 Magnitude, V | Y | 21996 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H48 Angle | Y | 21998 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H49 Magnitude, % | Y | 22000 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H49 Magnitude, V | Y | 22002 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H49 Angle | Y | 22004 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H50 Magnitude, % | Y | 22006 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H50 Magnitude, V | Y | 22008 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H50 Angle | Y | 22010 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H51 Magnitude, % | Y | 22012 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H51 Magnitude, V | Y | 22014 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H51 Angle | Y | 22016 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H52 Magnitude, % | Y | 22018 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H52 Magnitude, V | Y | 22020 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H52 Angle | Y | 22022 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H53 Magnitude, % | Y | 22024 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H53 Magnitude, V | Y | 22026 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H53 Angle | Y | 22028 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H54 Magnitude, % | Y | 22030 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H54 Magnitude, V | Y | 22032 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H54 Angle | Y | 22034 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H55 Magnitude, % | Y | 22036 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H55 Magnitude, V | Y | 22038 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H55 Angle | Y | 22040 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H56 Magnitude, % | Y | 22042 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H56 Magnitude, V | Y | 22044 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H56 Angle | Y | 22046 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H57 Magnitude, % | Y | 22048 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H57 Magnitude, V | Y | 22050 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H57 Angle | Y | 22052 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H58 Magnitude, % | Y | 22054 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H58 Magnitude, V | Y | 22056 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H58 Angle | Y | 22058 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H59 Magnitude, % | Y | 22060 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H59 Magnitude, V | Y | 22062 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H59 Angle | Y | 22064 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H60 Magnitude, % | Y | 22066 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H60 Magnitude, V | Y | 22068 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H60 Angle | Y | 22070 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H61 Magnitude, % | Y | 22072 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H61 Magnitude, V | Y | 22074 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H61 Angle | Y | 22076 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H62 Magnitude, % | Y | 22078 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H62 Magnitude, V | Y | 22080 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H62 Angle | Y | 22082 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H63 Magnitude, % | Y | 22084 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H63 Magnitude, V | Y | 22086 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-B, H63 Angle | Y | 22088 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H1 Magnitude, % | Y | 22100 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H1 Magnitude, V | Y | 22102 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H1 Angle | Y | 22104 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H2 Magnitude, % | Y | 22106 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H2 Magnitude, V | Y | 22108 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H2 Angle | Y | 22110 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H3 Magnitude, % | Y | 22112 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H3 Magnitude, V | Y | 22114 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H3 Angle | Y | 22116 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H4 Magnitude, % | Y | 22118 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H4 Magnitude, V | Y | 22120 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H4 Angle | Y | 22122 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H5 Magnitude, % | Y | 22124 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H5 Magnitude, V | Y | 22126 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H5 Angle | Y | 22128 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H6 Magnitude, % | Y | 22130 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H6 Magnitude, V | Y | 22132 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H6 Angle | Y | 22134 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H7 Magnitude, % | Y | 22136 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H7 Magnitude, V | Y | 22138 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H7 Angle | Y | 22140 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H8 Magnitude, % | Y | 22142 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H8 Magnitude, V | Y | 22144 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H8 Angle | Y | 22146 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H9 Magnitude, % | Y | 22148 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H9 Magnitude, V | Y | 22150 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H9 Angle | Y | 22152 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H10 Magnitude, % | Y | 22154 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H10 Magnitude, V | Y | 22156 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H10 Angle | Y | 22158 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H11 Magnitude, % | Y | 22160 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H11 Magnitude, V | Y | 22162 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H11 Angle | Y | 22164 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H12 Magnitude, % | Y | 22166 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H12 Magnitude, V | Y | 22168 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H12 Angle | Y | 22170 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H13 Magnitude, % | Y | 22172 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H13 Magnitude, V | Y | 22174 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H13 Angle | Y | 22176 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H14 Magnitude, % | Y | 22178 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H14 Magnitude, V | Y | 22180 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H14 Angle | Y | 22182 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H15 Magnitude, % | Y | 22184 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H15 Magnitude, V | Y | 22186 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H15 Angle | Y | 22188 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H16 Magnitude, % | Y | 22190 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H16 Magnitude, V | Y | 22192 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H16 Angle | Y | 22194 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H17 Magnitude, % | Y | 22196 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H17 Magnitude, V | Y | 22198 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H17 Angle | Y | 22200 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H18 Magnitude, % | Y | 22202 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H18 Magnitude, V | Y | 22204 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H18 Angle | Y | 22206 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H19 Magnitude, % | Y | 22208 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H19 Magnitude, V | Y | 22210 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H19 Angle | Y | 22212 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H20 Magnitude, % | Y | 22214 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H20 Magnitude, V | Y | 22216 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H20 Angle | Y | 22218 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H21 Magnitude, % | Y | 22220 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H21 Magnitude, V | Y | 22222 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H21 Angle | Y | 22224 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H22 Magnitude, % | Y | 22226 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H22 Magnitude, V | Y | 22228 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H22 Angle | Y | 22230 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H23 Magnitude, % | Y | 22232 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H23 Magnitude, V | Y | 22234 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H23 Angle | Y | 22236 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H24 Magnitude, % | Y | 22238 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H24 Magnitude, V | Y | 22240 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H24 Angle | Y | 22242 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H25 Magnitude, % | Y | 22244 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H25 Magnitude, V | Y | 22246 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H25 Angle | Y | 22248 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H26 Magnitude, % | Y | 22250 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H26 Magnitude, V | Y | 22252 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H26 Angle | Y | 22254 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H27 Magnitude, % | Y | 22256 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H27 Magnitude, V | Y | 22258 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H27 Angle | Y | 22260 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H28 Magnitude, % | Y | 22262 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H28 Magnitude, V | Y | 22264 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H28 Angle | Y | 22266 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H29 Magnitude, % | Y | 22268 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H29 Magnitude, V | Y | 22270 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H29 Angle | Y | 22272 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H30 Magnitude, % | Y | 22274 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H30 Magnitude, V | Y | 22276 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H30 Angle | Y | 22278 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H31 Magnitude, % | Y | 22280 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H31 Magnitude, V | Y | 22282 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H31 Angle | Y | 22284 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H32 Magnitude, % | Y | 22286 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H32 Magnitude, V | Y | 22288 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H32 Angle | Y | 22290 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H33 Magnitude, % | Y | 22292 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H33 Magnitude, V | Y | 22294 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H33 Angle | Y | 22296 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H34 Magnitude, % | Y | 22298 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H34 Magnitude, V | Y | 22300 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H34 Angle | Y | 22302 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H35 Magnitude, % | Y | 22304 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H35 Magnitude, V | Y | 22306 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H35 Angle | Y | 22308 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H36 Magnitude, % | Y | 22310 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H36 Magnitude, V | Y | 22312 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H36 Angle | Y | 22314 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H37 Magnitude, % | Y | 22316 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H37 Magnitude, V | Y | 22318 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H37 Angle | Y | 22320 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H38 Magnitude, % | Y | 22322 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H38 Magnitude, V | Y | 22324 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H38 Angle | Y | 22326 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H39 Magnitude, % | Y | 22328 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H39 Magnitude, V | Y | 22330 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H39 Angle | Y | 22332 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H40 Magnitude, % | Y | 22334 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H40 Magnitude, V | Y | 22336 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H40 Angle | Y | 22338 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H41 Magnitude, % | Y | 22340 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H41 Magnitude, V | Y | 22342 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H41 Angle | Y | 22344 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H42 Magnitude, % | Y | 22346 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H42 Magnitude, V | Y | 22348 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H42 Angle | Y | 22350 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H43 Magnitude, % | Y | 22352 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H43 Magnitude, V | Y | 22354 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H43 Angle | Y | 22356 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H44 Magnitude, % | Y | 22358 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H44 Magnitude, V | Y | 22360 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H44 Angle | Y | 22362 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H45 Magnitude, % | Y | 22364 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H45 Magnitude, V | Y | 22366 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H45 Angle | Y | 22368 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H46 Magnitude, % | Y | 22370 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H46 Magnitude, V | Y | 22372 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H46 Angle | Y | 22374 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H47 Magnitude, % | Y | 22376 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H47 Magnitude, V | Y | 22378 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H47 Angle | Y | 22380 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H48 Magnitude, % | Y | 22382 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H48 Magnitude, V | Y | 22384 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H48 Angle | Y | 22386 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H49 Magnitude, % | Y | 22388 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H49 Magnitude, V | Y | 22390 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H49 Angle | Y | 22392 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H50 Magnitude, % | Y | 22394 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H50 Magnitude, V | Y | 22396 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H50 Angle | Y | 22398 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H51 Magnitude, % | Y | 22400 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H51 Magnitude, V | Y | 22402 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H51 Angle | Y | 22404 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H52 Magnitude, % | Y | 22406 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H52 Magnitude, V | Y | 22408 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H52 Angle | Y | 22410 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H53 Magnitude, % | Y | 22412 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H53 Magnitude, V | Y | 22414 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H53 Angle | Y | 22416 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H54 Magnitude, % | Y | 22418 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H54 Magnitude, V | Y | 22420 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H54 Angle | Y | 22422 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H55 Magnitude, % | Y | 22424 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H55 Magnitude, V | Y | 22426 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H55 Angle | Y | 22428 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H56 Magnitude, % | Y | 22430 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H56 Magnitude, V | Y | 22432 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H56 Angle | Y | 22434 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H57 Magnitude, % | Y | 22436 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H57 Magnitude, V | Y | 22438 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H57 Angle | Y | 22440 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H58 Magnitude, % | Y | 22442 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H58 Magnitude, V | Y | 22444 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H58 Angle | Y | 22446 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H59 Magnitude, % | Y | 22448 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H59 Magnitude, V | Y | 22450 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H59 Angle | Y | 22452 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H60 Magnitude, % | Y | 22454 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H60 Magnitude, V | Y | 22456 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H60 Angle | Y | 22458 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H61 Magnitude, % | Y | 22460 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H61 Magnitude, V | Y | 22462 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H61 Angle | Y | 22464 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H62 Magnitude, % | Y | 22466 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H62 Magnitude, V | Y | 22468 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H62 Angle | Y | 22470 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H63 Magnitude, % | Y | 22472 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H63 Magnitude, V | Y | 22474 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-C, H63 Angle | Y | 22476 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H1 Magnitude, % | Y | 22488 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H1 Magnitude, V | Y | 22490 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H1 Angle | Y | 22492 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H2 Magnitude, % | Y | 22494 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H2 Magnitude, V | Y | 22496 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H2 Angle | Y | 22498 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H3 Magnitude, % | Y | 22500 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H3 Magnitude, V | Y | 22502 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H3 Angle | Y | 22504 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H4 Magnitude, % | Y | 22506 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H4 Magnitude, V | Y | 22508 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H4 Angle | Y | 22510 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H5 Magnitude, % | Y | 22512 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H5 Magnitude, V | Y | 22514 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H5 Angle | Y | 22516 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H6 Magnitude, % | Y | 22518 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H6 Magnitude, V | Y | 22520 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H6 Angle | Y | 22522 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H7 Magnitude, % | Y | 22524 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H7 Magnitude, V | Y | 22526 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H7 Angle | Y | 22528 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H8 Magnitude, % | Y | 22530 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H8 Magnitude, V | Y | 22532 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H8 Angle | Y | 22534 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H9 Magnitude, % | Y | 22536 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H9 Magnitude, V | Y | 22538 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H9 Angle | Y | 22540 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H10 Magnitude, % | Y | 22542 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H10 Magnitude, V | Y | 22544 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H10 Angle | Y | 22546 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H11 Magnitude, % | Y | 22548 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H11 Magnitude, V | Y | 22550 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H11 Angle | Y | 22552 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H12 Magnitude, % | Y | 22554 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H12 Magnitude, V | Y | 22556 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H12 Angle | Y | 22558 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H13 Magnitude, % | Y | 22560 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H13 Magnitude, V | Y | 22562 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H13 Angle | Y | 22564 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H14 Magnitude, % | Y | 22566 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H14 Magnitude, V | Y | 22568 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H14 Angle | Y | 22570 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H15 Magnitude, % | Y | 22572 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H15 Magnitude, V | Y | 22574 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H15 Angle | Y | 22576 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H16 Magnitude, % | Y | 22578 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H16 Magnitude, V | Y | 22580 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H16 Angle | Y | 22582 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H17 Magnitude, % | Y | 22584 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H17 Magnitude, V | Y | 22586 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H17 Angle | Y | 22588 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H18 Magnitude, % | Y | 22590 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H18 Magnitude, V | Y | 22592 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H18 Angle | Y | 22594 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H19 Magnitude, % | Y | 22596 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H19 Magnitude, V | Y | 22598 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H19 Angle | Y | 22600 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H20 Magnitude, % | Y | 22602 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H20 Magnitude, V | Y | 22604 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H20 Angle | Y | 22606 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H21 Magnitude, % | Y | 22608 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H21 Magnitude, V | Y | 22610 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H21 Angle | Y | 22612 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H22 Magnitude, % | Y | 22614 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H22 Magnitude, V | Y | 22616 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H22 Angle | Y | 22618 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H23 Magnitude, % | Y | 22620 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H23 Magnitude, V | Y | 22622 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H23 Angle | Y | 22624 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H24 Magnitude, % | Y | 22626 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H24 Magnitude, V | Y | 22628 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H24 Angle | Y | 22630 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H25 Magnitude, % | Y | 22632 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H25 Magnitude, V | Y | 22634 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H25 Angle | Y | 22636 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H26 Magnitude, % | Y | 22638 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H26 Magnitude, V | Y | 22640 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H26 Angle | Y | 22642 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H27 Magnitude, % | Y | 22644 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H27 Magnitude, V | Y | 22646 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H27 Angle | Y | 22648 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H28 Magnitude, % | Y | 22650 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H28 Magnitude, V | Y | 22652 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H28 Angle | Y | 22654 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H29 Magnitude, % | Y | 22656 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H29 Magnitude, V | Y | 22658 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H29 Angle | Y | 22660 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H30 Magnitude, % | Y | 22662 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H30 Magnitude, V | Y | 22664 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H30 Angle | Y | 22666 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H31 Magnitude, % | Y | 22668 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H31 Magnitude, V | Y | 22670 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H31 Angle | Y | 22672 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H32 Magnitude, % | Y | 22674 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H32 Magnitude, V | Y | 22676 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H32 Angle | Y | 22678 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H33 Magnitude, % | Y | 22680 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H33 Magnitude, V | Y | 22682 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H33 Angle | Y | 22684 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H34 Magnitude, % | Y | 22686 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H34 Magnitude, V | Y | 22688 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H34 Angle | Y | 22690 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H35 Magnitude, % | Y | 22692 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H35 Magnitude, V | Y | 22694 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H35 Angle | Y | 22696 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H36 Magnitude, % | Y | 22698 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H36 Magnitude, V | Y | 22700 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H36 Angle | Y | 22702 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H37 Magnitude, % | Y | 22704 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H37 Magnitude, V | Y | 22706 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H37 Angle | Y | 22708 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H38 Magnitude, % | Y | 22710 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H38 Magnitude, V | Y | 22712 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H38 Angle | Y | 22714 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H39 Magnitude, % | Y | 22716 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H39 Magnitude, V | Y | 22718 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H39 Angle | Y | 22720 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H40 Magnitude, % | Y | 22722 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H40 Magnitude, V | Y | 22724 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H40 Angle | Y | 22726 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H41 Magnitude, % | Y | 22728 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H41 Magnitude, V | Y | 22730 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H41 Angle | Y | 22732 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H42 Magnitude, % | Y | 22734 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H42 Magnitude, V | Y | 22736 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H42 Angle | Y | 22738 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H43 Magnitude, % | Y | 22740 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H43 Magnitude, V | Y | 22742 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H43 Angle | Y | 22744 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H44 Magnitude, % | Y | 22746 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H44 Magnitude, V | Y | 22748 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H44 Angle | Y | 22750 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H45 Magnitude, % | Y | 22752 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H45 Magnitude, V | Y | 22754 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H45 Angle | Y | 22756 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H46 Magnitude, % | Y | 22758 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H46 Magnitude, V | Y | 22760 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H46 Angle | Y | 22762 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H47 Magnitude, % | Y | 22764 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H47 Magnitude, V | Y | 22766 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H47 Angle | Y | 22768 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H48 Magnitude, % | Y | 22770 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H48 Magnitude, V | Y | 22772 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H48 Angle | Y | 22774 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H49 Magnitude, % | Y | 22776 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H49 Magnitude, V | Y | 22778 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H49 Angle | Y | 22780 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H50 Magnitude, % | Y | 22782 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H50 Magnitude, V | Y | 22784 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H50 Angle | Y | 22786 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H51 Magnitude, % | Y | 22788 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H51 Magnitude, V | Y | 22790 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H51 Angle | Y | 22792 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H52 Magnitude, % | Y | 22794 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H52 Magnitude, V | Y | 22796 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H52 Angle | Y | 22798 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H53 Magnitude, % | Y | 22800 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H53 Magnitude, V | Y | 22802 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H53 Angle | Y | 22804 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H54 Magnitude, % | Y | 22806 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H54 Magnitude, V | Y | 22808 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H54 Angle | Y | 22810 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H55 Magnitude, % | Y | 22812 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H55 Magnitude, V | Y | 22814 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H55 Angle | Y | 22816 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H56 Magnitude, % | Y | 22818 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H56 Magnitude, V | Y | 22820 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H56 Angle | Y | 22822 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H57 Magnitude, % | Y | 22824 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H57 Magnitude, V | Y | 22826 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H57 Angle | Y | 22828 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H58 Magnitude, % | Y | 22830 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H58 Magnitude, V | Y | 22832 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H58 Angle | Y | 22834 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H59 Magnitude, % | Y | 22836 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H59 Magnitude, V | Y | 22838 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H59 Angle | Y | 22840 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H60 Magnitude, % | Y | 22842 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H60 Magnitude, V | Y | 22844 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H60 Angle | Y | 22846 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H61 Magnitude, % | Y | 22848 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H61 Magnitude, V | Y | 22850 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H61 Angle | Y | 22852 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H62 Magnitude, % | Y | 22854 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H62 Magnitude, V | Y | 22856 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H62 Angle | Y | 22858 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H63 Magnitude, % | Y | 22860 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H63 Magnitude, V | Y | 22862 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-A, H63 Angle | Y | 22864 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H1 Magnitude, % | Y | 22876 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H1 Magnitude, V | Y | 22878 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H1 Angle | Y | 22880 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H2 Magnitude, % | Y | 22882 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H2 Magnitude, V | Y | 22884 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H2 Angle | Y | 22886 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H3 Magnitude, % | Y | 22888 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H3 Magnitude, V | Y | 22890 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H3 Angle | Y | 22892 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H4 Magnitude, % | Y | 22894 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H4 Magnitude, V | Y | 22896 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H4 Angle | Y | 22898 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H5 Magnitude, % | Y | 22900 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H5 Magnitude, V | Y | 22902 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H5 Angle | Y | 22904 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H6 Magnitude, % | Y | 22906 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H6 Magnitude, V | Y | 22908 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H6 Angle | Y | 22910 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H7 Magnitude, % | Y | 22912 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H7 Magnitude, V | Y | 22914 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H7 Angle | Y | 22916 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H8 Magnitude, % | Y | 22918 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H8 Magnitude, V | Y | 22920 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H8 Angle | Y | 22922 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H9 Magnitude, % | Y | 22924 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H9 Magnitude, V | Y | 22926 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H9 Angle | Y | 22928 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H10 Magnitude, % | Y | 22930 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H10 Magnitude, V | Y | 22932 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H10 Angle | Y | 22934 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H11 Magnitude, % | Y | 22936 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H11 Magnitude, V | Y | 22938 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H11 Angle | Y | 22940 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H12 Magnitude, % | Y | 22942 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H12 Magnitude, V | Y | 22944 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H12 Angle | Y | 22946 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H13 Magnitude, % | Y | 22948 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H13 Magnitude, V | Y | 22950 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H13 Angle | Y | 22952 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H14 Magnitude, % | Y | 22954 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H14 Magnitude, V | Y | 22956 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H14 Angle | Y | 22958 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H15 Magnitude, % | Y | 22960 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H15 Magnitude, V | Y | 22962 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H15 Angle | Y | 22964 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H16 Magnitude, % | Y | 22966 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H16 Magnitude, V | Y | 22968 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H16 Angle | Y | 22970 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H17 Magnitude, % | Y | 22972 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H17 Magnitude, V | Y | 22974 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H17 Angle | Y | 22976 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H18 Magnitude, % | Y | 22978 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H18 Magnitude, V | Y | 22980 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H18 Angle | Y | 22982 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H19 Magnitude, % | Y | 22984 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H19 Magnitude, V | Y | 22986 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H19 Angle | Y | 22988 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H20 Magnitude, % | Y | 22990 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H20 Magnitude, V | Y | 22992 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H20 Angle | Y | 22994 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H21 Magnitude, % | Y | 22996 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H21 Magnitude, V | Y | 22998 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H21 Angle | Y | 23000 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H22 Magnitude, % | Y | 23002 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H22 Magnitude, V | Y | 23004 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H22 Angle | Y | 23006 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H23 Magnitude, % | Y | 23008 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H23 Magnitude, V | Y | 23010 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H23 Angle | Y | 23012 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H24 Magnitude, % | Y | 23014 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H24 Magnitude, V | Y | 23016 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H24 Angle | Y | 23018 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H25 Magnitude, % | Y | 23020 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H25 Magnitude, V | Y | 23022 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H25 Angle | Y | 23024 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H26 Magnitude, % | Y | 23026 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H26 Magnitude, V | Y | 23028 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H26 Angle | Y | 23030 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H27 Magnitude, % | Y | 23032 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H27 Magnitude, V | Y | 23034 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H27 Angle | Y | 23036 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H28 Magnitude, % | Y | 23038 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H28 Magnitude, V | Y | 23040 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H28 Angle | Y | 23042 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H29 Magnitude, % | Y | 23044 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H29 Magnitude, V | Y | 23046 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H29 Angle | Y | 23048 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H30 Magnitude, % | Y | 23050 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H30 Magnitude, V | Y | 23052 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H30 Angle | Y | 23054 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H31 Magnitude, % | Y | 23056 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H31 Magnitude, V | Y | 23058 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H31 Angle | Y | 23060 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H32 Magnitude, % | Y | 23062 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H32 Magnitude, V | Y | 23064 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H32 Angle | Y | 23066 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H33 Magnitude, % | Y | 23068 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H33 Magnitude, V | Y | 23070 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H33 Angle | Y | 23072 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H34 Magnitude, % | Y | 23074 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H34 Magnitude, V | Y | 23076 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H34 Angle | Y | 23078 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H35 Magnitude, % | Y | 23080 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H35 Magnitude, V | Y | 23082 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H35 Angle | Y | 23084 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H36 Magnitude, % | Y | 23086 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H36 Magnitude, V | Y | 23088 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H36 Angle | Y | 23090 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H37 Magnitude, % | Y | 23092 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H37 Magnitude, V | Y | 23094 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H37 Angle | Y | 23096 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H38 Magnitude, % | Y | 23098 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H38 Magnitude, V | Y | 23100 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H38 Angle | Y | 23102 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H39 Magnitude, % | Y | 23104 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H39 Magnitude, V | Y | 23106 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H39 Angle | Y | 23108 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H40 Magnitude, % | Y | 23110 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H40 Magnitude, V | Y | 23112 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H40 Angle | Y | 23114 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H41 Magnitude, % | Y | 23116 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H41 Magnitude, V | Y | 23118 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H41 Angle | Y | 23120 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H42 Magnitude, % | Y | 23122 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H42 Magnitude, V | Y | 23124 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H42 Angle | Y | 23126 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H43 Magnitude, % | Y | 23128 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H43 Magnitude, V | Y | 23130 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H43 Angle | Y | 23132 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H44 Magnitude, % | Y | 23134 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H44 Magnitude, V | Y | 23136 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H44 Angle | Y | 23138 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H45 Magnitude, % | Y | 23140 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H45 Magnitude, V | Y | 23142 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H45 Angle | Y | 23144 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H46 Magnitude, % | Y | 23146 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H46 Magnitude, V | Y | 23148 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H46 Angle | Y | 23150 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H47 Magnitude, % | Y | 23152 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H47 Magnitude, V | Y | 23154 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H47 Angle | Y | 23156 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H48 Magnitude, % | Y | 23158 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H48 Magnitude, V | Y | 23160 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H48 Angle | Y | 23162 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H49 Magnitude, % | Y | 23164 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H49 Magnitude, V | Y | 23166 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H49 Angle | Y | 23168 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H50 Magnitude, % | Y | 23170 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H50 Magnitude, V | Y | 23172 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H50 Angle | Y | 23174 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H51 Magnitude, % | Y | 23176 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H51 Magnitude, V | Y | 23178 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H51 Angle | Y | 23180 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H52 Magnitude, % | Y | 23182 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H52 Magnitude, V | Y | 23184 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H52 Angle | Y | 23186 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H53 Magnitude, % | Y | 23188 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H53 Magnitude, V | Y | 23190 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H53 Angle | Y | 23192 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H54 Magnitude, % | Y | 23194 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H54 Magnitude, V | Y | 23196 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H54 Angle | Y | 23198 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H55 Magnitude, % | Y | 23200 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H55 Magnitude, V | Y | 23202 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H55 Angle | Y | 23204 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H56 Magnitude, % | Y | 23206 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H56 Magnitude, V | Y | 23208 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H56 Angle | Y | 23210 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H57 Magnitude, % | Y | 23212 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H57 Magnitude, V | Y | 23214 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H57 Angle | Y | 23216 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H58 Magnitude, % | Y | 23218 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H58 Magnitude, V | Y | 23220 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H58 Angle | Y | 23222 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H59 Magnitude, % | Y | 23224 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H59 Magnitude, V | Y | 23226 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H59 Angle | Y | 23228 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H60 Magnitude, % | Y | 23230 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H60 Magnitude, V | Y | 23232 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H60 Angle | Y | 23234 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H61 Magnitude, % | Y | 23236 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H61 Magnitude, V | Y | 23238 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H61 Angle | Y | 23240 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H62 Magnitude, % | Y | 23242 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H62 Magnitude, V | Y | 23244 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H62 Angle | Y | 23246 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H63 Magnitude, % | Y | 23248 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H63 Magnitude, V | Y | 23250 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage A-N, H63 Angle | Y | 23252 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H1 Magnitude, % | Y | 23264 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H1 Magnitude, V | Y | 23266 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H1 Angle | Y | 23268 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H2 Magnitude, % | Y | 23270 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H2 Magnitude, V | Y | 23272 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H2 Angle | Y | 23274 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H3 Magnitude, % | Y | 23276 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H3 Magnitude, V | Y | 23278 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H3 Angle | Y | 23280 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H4 Magnitude, % | Y | 23282 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H4 Magnitude, V | Y | 23284 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H4 Angle | Y | 23286 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H5 Magnitude, % | Y | 23288 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H5 Magnitude, V | Y | 23290 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H5 Angle | Y | 23292 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H6 Magnitude, % | Y | 23294 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H6 Magnitude, V | Y | 23296 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H6 Angle | Y | 23298 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H7 Magnitude, % | Y | 23300 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H7 Magnitude, V | Y | 23302 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H7 Angle | Y | 23304 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H8 Magnitude, % | Y | 23306 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H8 Magnitude, V | Y | 23308 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H8 Angle | Y | 23310 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H9 Magnitude, % | Y | 23312 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H9 Magnitude, V | Y | 23314 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H9 Angle | Y | 23316 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H10 Magnitude, % | Y | 23318 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H10 Magnitude, V | Y | 23320 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H10 Angle | Y | 23322 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H11 Magnitude, % | Y | 23324 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H11 Magnitude, V | Y | 23326 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H11 Angle | Y | 23328 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H12 Magnitude, % | Y | 23330 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H12 Magnitude, V | Y | 23332 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H12 Angle | Y | 23334 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H13 Magnitude, % | Y | 23336 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H13 Magnitude, V | Y | 23338 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H13 Angle | Y | 23340 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H14 Magnitude, % | Y | 23342 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H14 Magnitude, V | Y | 23344 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H14 Angle | Y | 23346 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H15 Magnitude, % | Y | 23348 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H15 Magnitude, V | Y | 23350 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H15 Angle | Y | 23352 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H16 Magnitude, % | Y | 23354 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H16 Magnitude, V | Y | 23356 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H16 Angle | Y | 23358 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H17 Magnitude, % | Y | 23360 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H17 Magnitude, V | Y | 23362 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H17 Angle | Y | 23364 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H18 Magnitude, % | Y | 23366 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H18 Magnitude, V | Y | 23368 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H18 Angle | Y | 23370 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H19 Magnitude, % | Y | 23372 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H19 Magnitude, V | Y | 23374 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H19 Angle | Y | 23376 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H20 Magnitude, % | Y | 23378 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H20 Magnitude, V | Y | 23380 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H20 Angle | Y | 23382 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H21 Magnitude, % | Y | 23384 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H21 Magnitude, V | Y | 23386 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H21 Angle | Y | 23388 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H22 Magnitude, % | Y | 23390 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H22 Magnitude, V | Y | 23392 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H22 Angle | Y | 23394 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H23 Magnitude, % | Y | 23396 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H23 Magnitude, V | Y | 23398 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H23 Angle | Y | 23400 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H24 Magnitude, % | Y | 23402 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H24 Magnitude, V | Y | 23404 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H24 Angle | Y | 23406 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H25 Magnitude, % | Y | 23408 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H25 Magnitude, V | Y | 23410 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H25 Angle | Y | 23412 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H26 Magnitude, % | Y | 23414 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H26 Magnitude, V | Y | 23416 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H26 Angle | Y | 23418 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H27 Magnitude, % | Y | 23420 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H27 Magnitude, V | Y | 23422 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H27 Angle | Y | 23424 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H28 Magnitude, % | Y | 23426 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H28 Magnitude, V | Y | 23428 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H28 Angle | Y | 23430 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H29 Magnitude, % | Y | 23432 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H29 Magnitude, V | Y | 23434 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H29 Angle | Y | 23436 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H30 Magnitude, % | Y | 23438 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H30 Magnitude, V | Y | 23440 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H30 Angle | Y | 23442 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H31 Magnitude, % | Y | 23444 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H31 Magnitude, V | Y | 23446 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H31 Angle | Y | 23448 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H32 Magnitude, % | Y | 23450 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H32 Magnitude, V | Y | 23452 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H32 Angle | Y | 23454 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H33 Magnitude, % | Y | 23456 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H33 Magnitude, V | Y | 23458 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H33 Angle | Y | 23460 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H34 Magnitude, % | Y | 23462 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H34 Magnitude, V | Y | 23464 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H34 Angle | Y | 23466 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H35 Magnitude, % | Y | 23468 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H35 Magnitude, V | Y | 23470 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H35 Angle | Y | 23472 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H36 Magnitude, % | Y | 23474 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H36 Magnitude, V | Y | 23476 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H36 Angle | Y | 23478 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H37 Magnitude, % | Y | 23480 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H37 Magnitude, V | Y | 23482 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H37 Angle | Y | 23484 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H38 Magnitude, % | Y | 23486 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H38 Magnitude, V | Y | 23488 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H38 Angle | Y | 23490 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H39 Magnitude, % | Y | 23492 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H39 Magnitude, V | Y | 23494 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H39 Angle | Y | 23496 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H40 Magnitude, % | Y | 23498 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H40 Magnitude, V | Y | 23500 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H40 Angle | Y | 23502 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H41 Magnitude, % | Y | 23504 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H41 Magnitude, V | Y | 23506 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H41 Angle | Y | 23508 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H42 Magnitude, % | Y | 23510 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H42 Magnitude, V | Y | 23512 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H42 Angle | Y | 23514 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H43 Magnitude, % | Y | 23516 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H43 Magnitude, V | Y | 23518 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H43 Angle | Y | 23520 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H44 Magnitude, % | Y | 23522 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H44 Magnitude, V | Y | 23524 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H44 Angle | Y | 23526 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H45 Magnitude, % | Y | 23528 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H45 Magnitude, V | Y | 23530 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H45 Angle | Y | 23532 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H46 Magnitude, % | Y | 23534 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H46 Magnitude, V | Y | 23536 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H46 Angle | Y | 23538 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H47 Magnitude, % | Y | 23540 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H47 Magnitude, V | Y | 23542 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H47 Angle | Y | 23544 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H48 Magnitude, % | Y | 23546 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H48 Magnitude, V | Y | 23548 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H48 Angle | Y | 23550 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H49 Magnitude, % | Y | 23552 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H49 Magnitude, V | Y | 23554 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H49 Angle | Y | 23556 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H50 Magnitude, % | Y | 23558 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H50 Magnitude, V | Y | 23560 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H50 Angle | Y | 23562 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H51 Magnitude, % | Y | 23564 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H51 Magnitude, V | Y | 23566 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H51 Angle | Y | 23568 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H52 Magnitude, % | Y | 23570 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H52 Magnitude, V | Y | 23572 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H52 Angle | Y | 23574 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H53 Magnitude, % | Y | 23576 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H53 Magnitude, V | Y | 23578 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H53 Angle | Y | 23580 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H54 Magnitude, % | Y | 23582 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H54 Magnitude, V | Y | 23584 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H54 Angle | Y | 23586 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H55 Magnitude, % | Y | 23588 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H55 Magnitude, V | Y | 23590 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H55 Angle | Y | 23592 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H56 Magnitude, % | Y | 23594 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H56 Magnitude, V | Y | 23596 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H56 Angle | Y | 23598 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H57 Magnitude, % | Y | 23600 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H57 Magnitude, V | Y | 23602 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H57 Angle | Y | 23604 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H58 Magnitude, % | Y | 23606 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H58 Magnitude, V | Y | 23608 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H58 Angle | Y | 23610 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H59 Magnitude, % | Y | 23612 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H59 Magnitude, V | Y | 23614 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H59 Angle | Y | 23616 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H60 Magnitude, % | Y | 23618 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H60 Magnitude, V | Y | 23620 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H60 Angle | Y | 23622 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H61 Magnitude, % | Y | 23624 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H61 Magnitude, V | Y | 23626 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H61 Angle | Y | 23628 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H62 Magnitude, % | Y | 23630 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H62 Magnitude, V | Y | 23632 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H62 Angle | Y | 23634 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H63 Magnitude, % | Y | 23636 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H63 Magnitude, V | Y | 23638 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage B-N, H63 Angle | Y | 23640 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H1 Magnitude, % | Y | 23652 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H1 Magnitude, V | Y | 23654 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H1 Angle | Y | 23656 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H2 Magnitude, % | Y | 23658 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H2 Magnitude, V | Y | 23660 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H2 Angle | Y | 23662 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H3 Magnitude, % | Y | 23664 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H3 Magnitude, V | Y | 23666 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H3 Angle | Y | 23668 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H4 Magnitude, % | Y | 23670 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H4 Magnitude, V | Y | 23672 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H4 Angle | Y | 23674 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H5 Magnitude, % | Y | 23676 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H5 Magnitude, V | Y | 23678 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H5 Angle | Y | 23680 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H6 Magnitude, % | Y | 23682 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H6 Magnitude, V | Y | 23684 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H6 Angle | Y | 23686 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H7 Magnitude, % | Y | 23688 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H7 Magnitude, V | Y | 23690 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H7 Angle | Y | 23692 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H8 Magnitude, % | Y | 23694 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H8 Magnitude, V | Y | 23696 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H8 Angle | Y | 23698 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H9 Magnitude, % | Y | 23700 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H9 Magnitude, V | Y | 23702 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H9 Angle | Y | 23704 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H10 Magnitude, % | Y | 23706 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H10 Magnitude, V | Y | 23708 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H10 Angle | Y | 23710 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H11 Magnitude, % | Y | 23712 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H11 Magnitude, V | Y | 23714 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H11 Angle | Y | 23716 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H12 Magnitude, % | Y | 23718 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H12 Magnitude, V | Y | 23720 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H12 Angle | Y | 23722 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H13 Magnitude, % | Y | 23724 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H13 Magnitude, V | Y | 23726 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H13 Angle | Y | 23728 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H14 Magnitude, % | Y | 23730 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H14 Magnitude, V | Y | 23732 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H14 Angle | Y | 23734 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H15 Magnitude, % | Y | 23736 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H15 Magnitude, V | Y | 23738 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H15 Angle | Y | 23740 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H16 Magnitude, % | Y | 23742 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H16 Magnitude, V | Y | 23744 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H16 Angle | Y | 23746 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H17 Magnitude, % | Y | 23748 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H17 Magnitude, V | Y | 23750 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H17 Angle | Y | 23752 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H18 Magnitude, % | Y | 23754 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H18 Magnitude, V | Y | 23756 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H18 Angle | Y | 23758 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H19 Magnitude, % | Y | 23760 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H19 Magnitude, V | Y | 23762 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H19 Angle | Y | 23764 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H20 Magnitude, % | Y | 23766 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H20 Magnitude, V | Y | 23768 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H20 Angle | Y | 23770 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H21 Magnitude, % | Y | 23772 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H21 Magnitude, V | Y | 23774 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H21 Angle | Y | 23776 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H22 Magnitude, % | Y | 23778 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H22 Magnitude, V | Y | 23780 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H22 Angle | Y | 23782 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H23 Magnitude, % | Y | 23784 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H23 Magnitude, V | Y | 23786 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H23 Angle | Y | 23788 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H24 Magnitude, % | Y | 23790 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H24 Magnitude, V | Y | 23792 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H24 Angle | Y | 23794 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H25 Magnitude, % | Y | 23796 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H25 Magnitude, V | Y | 23798 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H25 Angle | Y | 23800 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H26 Magnitude, % | Y | 23802 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H26 Magnitude, V | Y | 23804 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H26 Angle | Y | 23806 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H27 Magnitude, % | Y | 23808 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H27 Magnitude, V | Y | 23810 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H27 Angle | Y | 23812 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H28 Magnitude, % | Y | 23814 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H28 Magnitude, V | Y | 23816 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H28 Angle | Y | 23818 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H29 Magnitude, % | Y | 23820 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H29 Magnitude, V | Y | 23822 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H29 Angle | Y | 23824 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H30 Magnitude, % | Y | 23826 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H30 Magnitude, V | Y | 23828 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H30 Angle | Y | 23830 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H31 Magnitude, % | Y | 23832 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H31 Magnitude, V | Y | 23834 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H31 Angle | Y | 23836 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H32 Magnitude, % | Y | 23838 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H32 Magnitude, V | Y | 23840 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H32 Angle | Y | 23842 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H33 Magnitude, % | Y | 23844 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H33 Magnitude, V | Y | 23846 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H33 Angle | Y | 23848 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H34 Magnitude, % | Y | 23850 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H34 Magnitude, V | Y | 23852 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H34 Angle | Y | 23854 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H35 Magnitude, % | Y | 23856 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H35 Magnitude, V | Y | 23858 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H35 Angle | Y | 23860 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H36 Magnitude, % | Y | 23862 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H36 Magnitude, V | Y | 23864 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H36 Angle | Y | 23866 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H37 Magnitude, % | Y | 23868 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H37 Magnitude, V | Y | 23870 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H37 Angle | Y | 23872 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H38 Magnitude, % | Y | 23874 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H38 Magnitude, V | Y | 23876 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H38 Angle | Y | 23878 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H39 Magnitude, % | Y | 23880 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H39 Magnitude, V | Y | 23882 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H39 Angle | Y | 23884 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H40 Magnitude, % | Y | 23886 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H40 Magnitude, V | Y | 23888 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H40 Angle | Y | 23890 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H41 Magnitude, % | Y | 23892 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H41 Magnitude, V | Y | 23894 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H41 Angle | Y | 23896 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H42 Magnitude, % | Y | 23898 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H42 Magnitude, V | Y | 23900 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H42 Angle | Y | 23902 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H43 Magnitude, % | Y | 23904 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H43 Magnitude, V | Y | 23906 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H43 Angle | Y | 23908 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H44 Magnitude, % | Y | 23910 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H44 Magnitude, V | Y | 23912 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H44 Angle | Y | 23914 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H45 Magnitude, % | Y | 23916 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H45 Magnitude, V | Y | 23918 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H45 Angle | Y | 23920 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H46 Magnitude, % | Y | 23922 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H46 Magnitude, V | Y | 23924 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H46 Angle | Y | 23926 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H47 Magnitude, % | Y | 23928 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H47 Magnitude, V | Y | 23930 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H47 Angle | Y | 23932 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H48 Magnitude, % | Y | 23934 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H48 Magnitude, V | Y | 23936 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H48 Angle | Y | 23938 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H49 Magnitude, % | Y | 23940 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H49 Magnitude, V | Y | 23942 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H49 Angle | Y | 23944 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H50 Magnitude, % | Y | 23946 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H50 Magnitude, V | Y | 23948 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H50 Angle | Y | 23950 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H51 Magnitude, % | Y | 23952 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H51 Magnitude, V | Y | 23954 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H51 Angle | Y | 23956 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H52 Magnitude, % | Y | 23958 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H52 Magnitude, V | Y | 23960 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H52 Angle | Y | 23962 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H53 Magnitude, % | Y | 23964 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H53 Magnitude, V | Y | 23966 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H53 Angle | Y | 23968 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H54 Magnitude, % | Y | 23970 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H54 Magnitude, V | Y | 23972 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H54 Angle | Y | 23974 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H55 Magnitude, % | Y | 23976 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H55 Magnitude, V | Y | 23978 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H55 Angle | Y | 23980 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H56 Magnitude, % | Y | 23982 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H56 Magnitude, V | Y | 23984 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H56 Angle | Y | 23986 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H57 Magnitude, % | Y | 23988 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H57 Magnitude, V | Y | 23990 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H57 Angle | Y | 23992 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H58 Magnitude, % | Y | 23994 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H58 Magnitude, V | Y | 23996 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H58 Angle | Y | 23998 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H59 Magnitude, % | Y | 24000 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H59 Magnitude, V | Y | 24002 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H59 Angle | Y | 24004 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H60 Magnitude, % | Y | 24006 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H60 Magnitude, V | Y | 24008 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H60 Angle | Y | 24010 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H61 Magnitude, % | Y | 24012 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H61 Magnitude, V | Y | 24014 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H61 Angle | Y | 24016 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H62 Magnitude, % | Y | 24018 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H62 Magnitude, V | Y | 24020 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H62 Angle | Y | 24022 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H63 Magnitude, % | Y | 24024 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H63 Magnitude, V | Y | 24026 | V | 2 | FLOAT32 | R |  |  | N
|  |  | Voltage C-N, H63 Angle | Y | 24028 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H1 Magnitude, % | Y | 24428 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H1 Magnitude, A | Y | 24430 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H1 Angle | Y | 24432 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H2 Magnitude, % | Y | 24434 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H2 Magnitude, A | Y | 24436 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H2 Angle | Y | 24438 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H3 Magnitude, % | Y | 24440 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H3 Magnitude, A | Y | 24442 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H3 Angle | Y | 24444 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H4 Magnitude, % | Y | 24446 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H4 Magnitude, A | Y | 24448 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H4 Angle | Y | 24450 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H5 Magnitude, % | Y | 24452 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H5 Magnitude, A | Y | 24454 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H5 Angle | Y | 24456 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H6 Magnitude, % | Y | 24458 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H6 Magnitude, A | Y | 24460 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H6 Angle | Y | 24462 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H7 Magnitude, % | Y | 24464 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H7 Magnitude, A | Y | 24466 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H7 Angle | Y | 24468 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H8 Magnitude, % | Y | 24470 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H8 Magnitude, A | Y | 24472 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H8 Angle | Y | 24474 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H9 Magnitude, % | Y | 24476 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H9 Magnitude, A | Y | 24478 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H9 Angle | Y | 24480 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H10 Magnitude, % | Y | 24482 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H10 Magnitude, A | Y | 24484 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H10 Angle | Y | 24486 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H11 Magnitude, % | Y | 24488 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H11 Magnitude, A | Y | 24490 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H11 Angle | Y | 24492 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H12 Magnitude, % | Y | 24494 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H12 Magnitude, A | Y | 24496 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H12 Angle | Y | 24498 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H13 Magnitude, % | Y | 24500 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H13 Magnitude, A | Y | 24502 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H13 Angle | Y | 24504 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H14 Magnitude, % | Y | 24506 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H14 Magnitude, A | Y | 24508 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H14 Angle | Y | 24510 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H15 Magnitude, % | Y | 24512 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H15 Magnitude, A | Y | 24514 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H15 Angle | Y | 24516 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H16 Magnitude, % | Y | 24518 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H16 Magnitude, A | Y | 24520 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H16 Angle | Y | 24522 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H17 Magnitude, % | Y | 24524 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H17 Magnitude, A | Y | 24526 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H17 Angle | Y | 24528 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H18 Magnitude, % | Y | 24530 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H18 Magnitude, A | Y | 24532 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H18 Angle | Y | 24534 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H19 Magnitude, % | Y | 24536 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H19 Magnitude, A | Y | 24538 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H19 Angle | Y | 24540 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H20 Magnitude, % | Y | 24542 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H20 Magnitude, A | Y | 24544 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H20 Angle | Y | 24546 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H21 Magnitude, % | Y | 24548 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H21 Magnitude, A | Y | 24550 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H21 Angle | Y | 24552 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H22 Magnitude, % | Y | 24554 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H22 Magnitude, A | Y | 24556 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H22 Angle | Y | 24558 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H23 Magnitude, % | Y | 24560 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H23 Magnitude, A | Y | 24562 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H23 Angle | Y | 24564 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H24 Magnitude, % | Y | 24566 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H24 Magnitude, A | Y | 24568 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H24 Angle | Y | 24570 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H25 Magnitude, % | Y | 24572 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H25 Magnitude, A | Y | 24574 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H25 Angle | Y | 24576 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H26 Magnitude, % | Y | 24578 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H26 Magnitude, A | Y | 24580 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H26 Angle | Y | 24582 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H27 Magnitude, % | Y | 24584 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H27 Magnitude, A | Y | 24586 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H27 Angle | Y | 24588 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H28 Magnitude, % | Y | 24590 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H28 Magnitude, A | Y | 24592 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H28 Angle | Y | 24594 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H29 Magnitude, % | Y | 24596 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H29 Magnitude, A | Y | 24598 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H29 Angle | Y | 24600 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H30 Magnitude, % | Y | 24602 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H30 Magnitude, A | Y | 24604 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H30 Angle | Y | 24606 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H31 Magnitude, % | Y | 24608 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H31 Magnitude, A | Y | 24610 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H31 Angle | Y | 24612 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H32 Magnitude, % | Y | 24614 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H32 Magnitude, A | Y | 24616 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H32 Angle | Y | 24618 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H33 Magnitude, % | Y | 24620 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H33 Magnitude, A | Y | 24622 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H33 Angle | Y | 24624 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H34 Magnitude, % | Y | 24626 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H34 Magnitude, A | Y | 24628 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H34 Angle | Y | 24630 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H35 Magnitude, % | Y | 24632 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H35 Magnitude, A | Y | 24634 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H35 Angle | Y | 24636 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H36 Magnitude, % | Y | 24638 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H36 Magnitude, A | Y | 24640 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H36 Angle | Y | 24642 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H37 Magnitude, % | Y | 24644 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H37 Magnitude, A | Y | 24646 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H37 Angle | Y | 24648 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H38 Magnitude, % | Y | 24650 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H38 Magnitude, A | Y | 24652 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H38 Angle | Y | 24654 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H39 Magnitude, % | Y | 24656 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H39 Magnitude, A | Y | 24658 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H39 Angle | Y | 24660 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H40 Magnitude, % | Y | 24662 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H40 Magnitude, A | Y | 24664 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H40 Angle | Y | 24666 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H41 Magnitude, % | Y | 24668 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H41 Magnitude, A | Y | 24670 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H41 Angle | Y | 24672 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H42 Magnitude, % | Y | 24674 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H42 Magnitude, A | Y | 24676 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H42 Angle | Y | 24678 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H43 Magnitude, % | Y | 24680 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H43 Magnitude, A | Y | 24682 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H43 Angle | Y | 24684 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H44 Magnitude, % | Y | 24686 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H44 Magnitude, A | Y | 24688 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H44 Angle | Y | 24690 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H45 Magnitude, % | Y | 24692 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H45 Magnitude, A | Y | 24694 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H45 Angle | Y | 24696 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H46 Magnitude, % | Y | 24698 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H46 Magnitude, A | Y | 24700 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H46 Angle | Y | 24702 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H47 Magnitude, % | Y | 24704 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H47 Magnitude, A | Y | 24706 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H47 Angle | Y | 24708 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H48 Magnitude, % | Y | 24710 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H48 Magnitude, A | Y | 24712 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H48 Angle | Y | 24714 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H49 Magnitude, % | Y | 24716 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H49 Magnitude, A | Y | 24718 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H49 Angle | Y | 24720 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H50 Magnitude, % | Y | 24722 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H50 Magnitude, A | Y | 24724 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H50 Angle | Y | 24726 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H51 Magnitude, % | Y | 24728 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H51 Magnitude, A | Y | 24730 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H51 Angle | Y | 24732 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H52 Magnitude, % | Y | 24734 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H52 Magnitude, A | Y | 24736 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H52 Angle | Y | 24738 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H53 Magnitude, % | Y | 24740 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H53 Magnitude, A | Y | 24742 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H53 Angle | Y | 24744 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H54 Magnitude, % | Y | 24746 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H54 Magnitude, A | Y | 24748 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H54 Angle | Y | 24750 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H55 Magnitude, % | Y | 24752 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H55 Magnitude, A | Y | 24754 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H55 Angle | Y | 24756 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H56 Magnitude, % | Y | 24758 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H56 Magnitude, A | Y | 24760 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H56 Angle | Y | 24762 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H57 Magnitude, % | Y | 24764 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H57 Magnitude, A | Y | 24766 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H57 Angle | Y | 24768 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H58 Magnitude, % | Y | 24770 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H58 Magnitude, A | Y | 24772 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H58 Angle | Y | 24774 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H59 Magnitude, % | Y | 24776 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H59 Magnitude, A | Y | 24778 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H59 Angle | Y | 24780 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H60 Magnitude, % | Y | 24782 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H60 Magnitude, A | Y | 24784 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H60 Angle | Y | 24786 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H61 Magnitude, % | Y | 24788 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H61 Magnitude, A | Y | 24790 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H61 Angle | Y | 24792 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H62 Magnitude, % | Y | 24794 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H62 Magnitude, A | Y | 24796 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H62 Angle | Y | 24798 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H63 Magnitude, % | Y | 24800 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H63 Magnitude, A | Y | 24802 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current A, H63 Angle | Y | 24804 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H1 Magnitude, % | Y | 24816 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H1 Magnitude, A | Y | 24818 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H1 Angle | Y | 24820 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H2 Magnitude, % | Y | 24822 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H2 Magnitude, A | Y | 24824 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H2 Angle | Y | 24826 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H3 Magnitude, % | Y | 24828 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H3 Magnitude, A | Y | 24830 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H3 Angle | Y | 24832 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H4 Magnitude, % | Y | 24834 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H4 Magnitude, A | Y | 24836 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H4 Angle | Y | 24838 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H5 Magnitude, % | Y | 24840 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H5 Magnitude, A | Y | 24842 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H5 Angle | Y | 24844 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H6 Magnitude, % | Y | 24846 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H6 Magnitude, A | Y | 24848 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H6 Angle | Y | 24850 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H7 Magnitude, % | Y | 24852 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H7 Magnitude, A | Y | 24854 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H7 Angle | Y | 24856 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H8 Magnitude, % | Y | 24858 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H8 Magnitude, A | Y | 24860 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H8 Angle | Y | 24862 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H9 Magnitude, % | Y | 24864 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H9 Magnitude, A | Y | 24866 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H9 Angle | Y | 24868 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H10 Magnitude, % | Y | 24870 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H10 Magnitude, A | Y | 24872 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H10 Angle | Y | 24874 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H11 Magnitude, % | Y | 24876 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H11 Magnitude, A | Y | 24878 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H11 Angle | Y | 24880 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H12 Magnitude, % | Y | 24882 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H12 Magnitude, A | Y | 24884 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H12 Angle | Y | 24886 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H13 Magnitude, % | Y | 24888 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H13 Magnitude, A | Y | 24890 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H13 Angle | Y | 24892 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H14 Magnitude, % | Y | 24894 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H14 Magnitude, A | Y | 24896 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H14 Angle | Y | 24898 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H15 Magnitude, % | Y | 24900 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H15 Magnitude, A | Y | 24902 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H15 Angle | Y | 24904 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H16 Magnitude, % | Y | 24906 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H16 Magnitude, A | Y | 24908 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H16 Angle | Y | 24910 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H17 Magnitude, % | Y | 24912 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H17 Magnitude, A | Y | 24914 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H17 Angle | Y | 24916 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H18 Magnitude, % | Y | 24918 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H18 Magnitude, A | Y | 24920 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H18 Angle | Y | 24922 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H19 Magnitude, % | Y | 24924 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H19 Magnitude, A | Y | 24926 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H19 Angle | Y | 24928 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H20 Magnitude, % | Y | 24930 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H20 Magnitude, A | Y | 24932 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H20 Angle | Y | 24934 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H21 Magnitude, % | Y | 24936 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H21 Magnitude, A | Y | 24938 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H21 Angle | Y | 24940 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H22 Magnitude, % | Y | 24942 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H22 Magnitude, A | Y | 24944 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H22 Angle | Y | 24946 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H23 Magnitude, % | Y | 24948 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H23 Magnitude, A | Y | 24950 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H23 Angle | Y | 24952 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H24 Magnitude, % | Y | 24954 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H24 Magnitude, A | Y | 24956 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H24 Angle | Y | 24958 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H25 Magnitude, % | Y | 24960 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H25 Magnitude, A | Y | 24962 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H25 Angle | Y | 24964 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H26 Magnitude, % | Y | 24966 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H26 Magnitude, A | Y | 24968 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H26 Angle | Y | 24970 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H27 Magnitude, % | Y | 24972 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H27 Magnitude, A | Y | 24974 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H27 Angle | Y | 24976 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H28 Magnitude, % | Y | 24978 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H28 Magnitude, A | Y | 24980 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H28 Angle | Y | 24982 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H29 Magnitude, % | Y | 24984 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H29 Magnitude, A | Y | 24986 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H29 Angle | Y | 24988 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H30 Magnitude, % | Y | 24990 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H30 Magnitude, A | Y | 24992 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H30 Angle | Y | 24994 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H31 Magnitude, % | Y | 24996 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H31 Magnitude, A | Y | 24998 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H31 Angle | Y | 25000 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H32 Magnitude, % | Y | 25002 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H32 Magnitude, A | Y | 25004 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H32 Angle | Y | 25006 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H33 Magnitude, % | Y | 25008 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H33 Magnitude, A | Y | 25010 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H33 Angle | Y | 25012 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H34 Magnitude, % | Y | 25014 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H34 Magnitude, A | Y | 25016 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H34 Angle | Y | 25018 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H35 Magnitude, % | Y | 25020 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H35 Magnitude, A | Y | 25022 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H35 Angle | Y | 25024 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H36 Magnitude, % | Y | 25026 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H36 Magnitude, A | Y | 25028 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H36 Angle | Y | 25030 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H37 Magnitude, % | Y | 25032 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H37 Magnitude, A | Y | 25034 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H37 Angle | Y | 25036 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H38 Magnitude, % | Y | 25038 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H38 Magnitude, A | Y | 25040 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H38 Angle | Y | 25042 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H39 Magnitude, % | Y | 25044 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H39 Magnitude, A | Y | 25046 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H39 Angle | Y | 25048 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H40 Magnitude, % | Y | 25050 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H40 Magnitude, A | Y | 25052 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H40 Angle | Y | 25054 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H41 Magnitude, % | Y | 25056 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H41 Magnitude, A | Y | 25058 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H41 Angle | Y | 25060 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H42 Magnitude, % | Y | 25062 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H42 Magnitude, A | Y | 25064 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H42 Angle | Y | 25066 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H43 Magnitude, % | Y | 25068 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H43 Magnitude, A | Y | 25070 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H43 Angle | Y | 25072 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H44 Magnitude, % | Y | 25074 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H44 Magnitude, A | Y | 25076 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H44 Angle | Y | 25078 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H45 Magnitude, % | Y | 25080 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H45 Magnitude, A | Y | 25082 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H45 Angle | Y | 25084 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H46 Magnitude, % | Y | 25086 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H46 Magnitude, A | Y | 25088 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H46 Angle | Y | 25090 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H47 Magnitude, % | Y | 25092 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H47 Magnitude, A | Y | 25094 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H47 Angle | Y | 25096 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H48 Magnitude, % | Y | 25098 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H48 Magnitude, A | Y | 25100 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H48 Angle | Y | 25102 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H49 Magnitude, % | Y | 25104 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H49 Magnitude, A | Y | 25106 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H49 Angle | Y | 25108 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H50 Magnitude, % | Y | 25110 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H50 Magnitude, A | Y | 25112 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H50 Angle | Y | 25114 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H51 Magnitude, % | Y | 25116 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H51 Magnitude, A | Y | 25118 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H51 Angle | Y | 25120 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H52 Magnitude, % | Y | 25122 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H52 Magnitude, A | Y | 25124 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H52 Angle | Y | 25126 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H53 Magnitude, % | Y | 25128 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H53 Magnitude, A | Y | 25130 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H53 Angle | Y | 25132 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H54 Magnitude, % | Y | 25134 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H54 Magnitude, A | Y | 25136 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H54 Angle | Y | 25138 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H55 Magnitude, % | Y | 25140 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H55 Magnitude, A | Y | 25142 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H55 Angle | Y | 25144 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H56 Magnitude, % | Y | 25146 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H56 Magnitude, A | Y | 25148 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H56 Angle | Y | 25150 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H57 Magnitude, % | Y | 25152 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H57 Magnitude, A | Y | 25154 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H57 Angle | Y | 25156 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H58 Magnitude, % | Y | 25158 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H58 Magnitude, A | Y | 25160 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H58 Angle | Y | 25162 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H59 Magnitude, % | Y | 25164 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H59 Magnitude, A | Y | 25166 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H59 Angle | Y | 25168 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H60 Magnitude, % | Y | 25170 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H60 Magnitude, A | Y | 25172 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H60 Angle | Y | 25174 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H61 Magnitude, % | Y | 25176 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H61 Magnitude, A | Y | 25178 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H61 Angle | Y | 25180 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H62 Magnitude, % | Y | 25182 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H62 Magnitude, A | Y | 25184 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H62 Angle | Y | 25186 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H63 Magnitude, % | Y | 25188 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H63 Magnitude, A | Y | 25190 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current B, H63 Angle | Y | 25192 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H1 Magnitude, % | Y | 25204 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H1 Magnitude, A | Y | 25206 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H1 Angle | Y | 25208 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H2 Magnitude, % | Y | 25210 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H2 Magnitude, A | Y | 25212 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H2 Angle | Y | 25214 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H3 Magnitude, % | Y | 25216 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H3 Magnitude, A | Y | 25218 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H3 Angle | Y | 25220 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H4 Magnitude, % | Y | 25222 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H4 Magnitude, A | Y | 25224 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H4 Angle | Y | 25226 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H5 Magnitude, % | Y | 25228 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H5 Magnitude, A | Y | 25230 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H5 Angle | Y | 25232 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H6 Magnitude, % | Y | 25234 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H6 Magnitude, A | Y | 25236 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H6 Angle | Y | 25238 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H7 Magnitude, % | Y | 25240 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H7 Magnitude, A | Y | 25242 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H7 Angle | Y | 25244 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H8 Magnitude, % | Y | 25246 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H8 Magnitude, A | Y | 25248 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H8 Angle | Y | 25250 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H9 Magnitude, % | Y | 25252 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H9 Magnitude, A | Y | 25254 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H9 Angle | Y | 25256 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H10 Magnitude, % | Y | 25258 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H10 Magnitude, A | Y | 25260 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H10 Angle | Y | 25262 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H11 Magnitude, % | Y | 25264 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H11 Magnitude, A | Y | 25266 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H11 Angle | Y | 25268 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H12 Magnitude, % | Y | 25270 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H12 Magnitude, A | Y | 25272 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H12 Angle | Y | 25274 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H13 Magnitude, % | Y | 25276 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H13 Magnitude, A | Y | 25278 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H13 Angle | Y | 25280 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H14 Magnitude, % | Y | 25282 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H14 Magnitude, A | Y | 25284 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H14 Angle | Y | 25286 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H15 Magnitude, % | Y | 25288 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H15 Magnitude, A | Y | 25290 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H15 Angle | Y | 25292 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H16 Magnitude, % | Y | 25294 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H16 Magnitude, A | Y | 25296 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H16 Angle | Y | 25298 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H17 Magnitude, % | Y | 25300 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H17 Magnitude, A | Y | 25302 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H17 Angle | Y | 25304 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H18 Magnitude, % | Y | 25306 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H18 Magnitude, A | Y | 25308 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H18 Angle | Y | 25310 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H19 Magnitude, % | Y | 25312 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H19 Magnitude, A | Y | 25314 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H19 Angle | Y | 25316 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H20 Magnitude, % | Y | 25318 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H20 Magnitude, A | Y | 25320 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H20 Angle | Y | 25322 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H21 Magnitude, % | Y | 25324 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H21 Magnitude, A | Y | 25326 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H21 Angle | Y | 25328 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H22 Magnitude, % | Y | 25330 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H22 Magnitude, A | Y | 25332 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H22 Angle | Y | 25334 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H23 Magnitude, % | Y | 25336 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H23 Magnitude, A | Y | 25338 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H23 Angle | Y | 25340 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H24 Magnitude, % | Y | 25342 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H24 Magnitude, A | Y | 25344 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H24 Angle | Y | 25346 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H25 Magnitude, % | Y | 25348 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H25 Magnitude, A | Y | 25350 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H25 Angle | Y | 25352 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H26 Magnitude, % | Y | 25354 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H26 Magnitude, A | Y | 25356 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H26 Angle | Y | 25358 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H27 Magnitude, % | Y | 25360 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H27 Magnitude, A | Y | 25362 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H27 Angle | Y | 25364 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H28 Magnitude, % | Y | 25366 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H28 Magnitude, A | Y | 25368 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H28 Angle | Y | 25370 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H29 Magnitude, % | Y | 25372 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H29 Magnitude, A | Y | 25374 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H29 Angle | Y | 25376 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H30 Magnitude, % | Y | 25378 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H30 Magnitude, A | Y | 25380 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H30 Angle | Y | 25382 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H31 Magnitude, % | Y | 25384 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H31 Magnitude, A | Y | 25386 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H31 Angle | Y | 25388 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H32 Magnitude, % | Y | 25390 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H32 Magnitude, A | Y | 25392 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H32 Angle | Y | 25394 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H33 Magnitude, % | Y | 25396 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H33 Magnitude, A | Y | 25398 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H33 Angle | Y | 25400 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H34 Magnitude, % | Y | 25402 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H34 Magnitude, A | Y | 25404 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H34 Angle | Y | 25406 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H35 Magnitude, % | Y | 25408 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H35 Magnitude, A | Y | 25410 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H35 Angle | Y | 25412 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H36 Magnitude, % | Y | 25414 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H36 Magnitude, A | Y | 25416 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H36 Angle | Y | 25418 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H37 Magnitude, % | Y | 25420 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H37 Magnitude, A | Y | 25422 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H37 Angle | Y | 25424 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H38 Magnitude, % | Y | 25426 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H38 Magnitude, A | Y | 25428 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H38 Angle | Y | 25430 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H39 Magnitude, % | Y | 25432 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H39 Magnitude, A | Y | 25434 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H39 Angle | Y | 25436 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H40 Magnitude, % | Y | 25438 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H40 Magnitude, A | Y | 25440 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H40 Angle | Y | 25442 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H41 Magnitude, % | Y | 25444 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H41 Magnitude, A | Y | 25446 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H41 Angle | Y | 25448 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H42 Magnitude, % | Y | 25450 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H42 Magnitude, A | Y | 25452 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H42 Angle | Y | 25454 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H43 Magnitude, % | Y | 25456 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H43 Magnitude, A | Y | 25458 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H43 Angle | Y | 25460 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H44 Magnitude, % | Y | 25462 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H44 Magnitude, A | Y | 25464 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H44 Angle | Y | 25466 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H45 Magnitude, % | Y | 25468 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H45 Magnitude, A | Y | 25470 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H45 Angle | Y | 25472 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H46 Magnitude, % | Y | 25474 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H46 Magnitude, A | Y | 25476 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H46 Angle | Y | 25478 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H47 Magnitude, % | Y | 25480 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H47 Magnitude, A | Y | 25482 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H47 Angle | Y | 25484 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H48 Magnitude, % | Y | 25486 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H48 Magnitude, A | Y | 25488 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H48 Angle | Y | 25490 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H49 Magnitude, % | Y | 25492 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H49 Magnitude, A | Y | 25494 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H49 Angle | Y | 25496 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H50 Magnitude, % | Y | 25498 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H50 Magnitude, A | Y | 25500 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H50 Angle | Y | 25502 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H51 Magnitude, % | Y | 25504 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H51 Magnitude, A | Y | 25506 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H51 Angle | Y | 25508 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H52 Magnitude, % | Y | 25510 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H52 Magnitude, A | Y | 25512 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H52 Angle | Y | 25514 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H53 Magnitude, % | Y | 25516 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H53 Magnitude, A | Y | 25518 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H53 Angle | Y | 25520 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H54 Magnitude, % | Y | 25522 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H54 Magnitude, A | Y | 25524 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H54 Angle | Y | 25526 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H55 Magnitude, % | Y | 25528 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H55 Magnitude, A | Y | 25530 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H55 Angle | Y | 25532 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H56 Magnitude, % | Y | 25534 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H56 Magnitude, A | Y | 25536 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H56 Angle | Y | 25538 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H57 Magnitude, % | Y | 25540 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H57 Magnitude, A | Y | 25542 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H57 Angle | Y | 25544 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H58 Magnitude, % | Y | 25546 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H58 Magnitude, A | Y | 25548 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H58 Angle | Y | 25550 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H59 Magnitude, % | Y | 25552 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H59 Magnitude, A | Y | 25554 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H59 Angle | Y | 25556 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H60 Magnitude, % | Y | 25558 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H60 Magnitude, A | Y | 25560 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H60 Angle | Y | 25562 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H61 Magnitude, % | Y | 25564 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H61 Magnitude, A | Y | 25566 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H61 Angle | Y | 25568 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H62 Magnitude, % | Y | 25570 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H62 Magnitude, A | Y | 25572 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H62 Angle | Y | 25574 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H63 Magnitude, % | Y | 25576 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H63 Magnitude, A | Y | 25578 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current C, H63 Angle | Y | 25580 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H1 Magnitude, % | Y | 25592 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H1 Magnitude, A | Y | 25594 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H1 Angle | Y | 25596 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H2 Magnitude, % | Y | 25598 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H2 Magnitude, A | Y | 25600 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H2 Angle | Y | 25602 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H3 Magnitude, % | Y | 25604 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H3 Magnitude, A | Y | 25606 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H3 Angle | Y | 25608 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H4 Magnitude, % | Y | 25610 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H4 Magnitude, A | Y | 25612 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H4 Angle | Y | 25614 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H5 Magnitude, % | Y | 25616 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H5 Magnitude, A | Y | 25618 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H5 Angle | Y | 25620 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H6 Magnitude, % | Y | 25622 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H6 Magnitude, A | Y | 25624 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H6 Angle | Y | 25626 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H7 Magnitude, % | Y | 25628 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H7 Magnitude, A | Y | 25630 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H7 Angle | Y | 25632 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H8 Magnitude, % | Y | 25634 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H8 Magnitude, A | Y | 25636 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H8 Angle | Y | 25638 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H9 Magnitude, % | Y | 25640 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H9 Magnitude, A | Y | 25642 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H9 Angle | Y | 25644 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H10 Magnitude, % | Y | 25646 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H10 Magnitude, A | Y | 25648 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H10 Angle | Y | 25650 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H11 Magnitude, % | Y | 25652 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H11 Magnitude, A | Y | 25654 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H11 Angle | Y | 25656 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H12 Magnitude, % | Y | 25658 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H12 Magnitude, A | Y | 25660 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H12 Angle | Y | 25662 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H13 Magnitude, % | Y | 25664 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H13 Magnitude, A | Y | 25666 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H13 Angle | Y | 25668 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H14 Magnitude, % | Y | 25670 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H14 Magnitude, A | Y | 25672 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H14 Angle | Y | 25674 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H15 Magnitude, % | Y | 25676 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H15 Magnitude, A | Y | 25678 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H15 Angle | Y | 25680 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H16 Magnitude, % | Y | 25682 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H16 Magnitude, A | Y | 25684 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H16 Angle | Y | 25686 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H17 Magnitude, % | Y | 25688 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H17 Magnitude, A | Y | 25690 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H17 Angle | Y | 25692 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H18 Magnitude, % | Y | 25694 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H18 Magnitude, A | Y | 25696 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H18 Angle | Y | 25698 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H19 Magnitude, % | Y | 25700 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H19 Magnitude, A | Y | 25702 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H19 Angle | Y | 25704 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H20 Magnitude, % | Y | 25706 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H20 Magnitude, A | Y | 25708 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H20 Angle | Y | 25710 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H21 Magnitude, % | Y | 25712 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H21 Magnitude, A | Y | 25714 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H21 Angle | Y | 25716 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H22 Magnitude, % | Y | 25718 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H22 Magnitude, A | Y | 25720 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H22 Angle | Y | 25722 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H23 Magnitude, % | Y | 25724 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H23 Magnitude, A | Y | 25726 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H23 Angle | Y | 25728 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H24 Magnitude, % | Y | 25730 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H24 Magnitude, A | Y | 25732 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H24 Angle | Y | 25734 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H25 Magnitude, % | Y | 25736 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H25 Magnitude, A | Y | 25738 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H25 Angle | Y | 25740 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H26 Magnitude, % | Y | 25742 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H26 Magnitude, A | Y | 25744 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H26 Angle | Y | 25746 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H27 Magnitude, % | Y | 25748 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H27 Magnitude, A | Y | 25750 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H27 Angle | Y | 25752 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H28 Magnitude, % | Y | 25754 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H28 Magnitude, A | Y | 25756 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H28 Angle | Y | 25758 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H29 Magnitude, % | Y | 25760 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H29 Magnitude, A | Y | 25762 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H29 Angle | Y | 25764 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H30 Magnitude, % | Y | 25766 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H30 Magnitude, A | Y | 25768 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H30 Angle | Y | 25770 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H31 Magnitude, % | Y | 25772 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H31 Magnitude, A | Y | 25774 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H31 Angle | Y | 25776 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H32 Magnitude, % | Y | 25778 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H32 Magnitude, A | Y | 25780 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H32 Angle | Y | 25782 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H33 Magnitude, % | Y | 25784 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H33 Magnitude, A | Y | 25786 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H33 Angle | Y | 25788 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H34 Magnitude, % | Y | 25790 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H34 Magnitude, A | Y | 25792 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H34 Angle | Y | 25794 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H35 Magnitude, % | Y | 25796 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H35 Magnitude, A | Y | 25798 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H35 Angle | Y | 25800 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H36 Magnitude, % | Y | 25802 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H36 Magnitude, A | Y | 25804 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H36 Angle | Y | 25806 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H37 Magnitude, % | Y | 25808 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H37 Magnitude, A | Y | 25810 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H37 Angle | Y | 25812 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H38 Magnitude, % | Y | 25814 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H38 Magnitude, A | Y | 25816 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H38 Angle | Y | 25818 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H39 Magnitude, % | Y | 25820 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H39 Magnitude, A | Y | 25822 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H39 Angle | Y | 25824 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H40 Magnitude, % | Y | 25826 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H40 Magnitude, A | Y | 25828 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H40 Angle | Y | 25830 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H41 Magnitude, % | Y | 25832 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H41 Magnitude, A | Y | 25834 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H41 Angle | Y | 25836 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H42 Magnitude, % | Y | 25838 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H42 Magnitude, A | Y | 25840 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H42 Angle | Y | 25842 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H43 Magnitude, % | Y | 25844 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H43 Magnitude, A | Y | 25846 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H43 Angle | Y | 25848 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H44 Magnitude, % | Y | 25850 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H44 Magnitude, A | Y | 25852 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H44 Angle | Y | 25854 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H45 Magnitude, % | Y | 25856 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H45 Magnitude, A | Y | 25858 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H45 Angle | Y | 25860 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H46 Magnitude, % | Y | 25862 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H46 Magnitude, A | Y | 25864 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H46 Angle | Y | 25866 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H47 Magnitude, % | Y | 25868 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H47 Magnitude, A | Y | 25870 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H47 Angle | Y | 25872 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H48 Magnitude, % | Y | 25874 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H48 Magnitude, A | Y | 25876 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H48 Angle | Y | 25878 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H49 Magnitude, % | Y | 25880 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H49 Magnitude, A | Y | 25882 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H49 Angle | Y | 25884 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H50 Magnitude, % | Y | 25886 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H50 Magnitude, A | Y | 25888 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H50 Angle | Y | 25890 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H51 Magnitude, % | Y | 25892 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H51 Magnitude, A | Y | 25894 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H51 Angle | Y | 25896 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H52 Magnitude, % | Y | 25898 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H52 Magnitude, A | Y | 25900 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H52 Angle | Y | 25902 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H53 Magnitude, % | Y | 25904 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H53 Magnitude, A | Y | 25906 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H53 Angle | Y | 25908 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H54 Magnitude, % | Y | 25910 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H54 Magnitude, A | Y | 25912 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H54 Angle | Y | 25914 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H55 Magnitude, % | Y | 25916 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H55 Magnitude, A | Y | 25918 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H55 Angle | Y | 25920 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H56 Magnitude, % | Y | 25922 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H56 Magnitude, A | Y | 25924 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H56 Angle | Y | 25926 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H57 Magnitude, % | Y | 25928 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H57 Magnitude, A | Y | 25930 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H57 Angle | Y | 25932 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H58 Magnitude, % | Y | 25934 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H58 Magnitude, A | Y | 25936 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H58 Angle | Y | 25938 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H59 Magnitude, % | Y | 25940 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H59 Magnitude, A | Y | 25942 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H59 Angle | Y | 25944 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H60 Magnitude, % | Y | 25946 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H60 Magnitude, A | Y | 25948 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H60 Angle | Y | 25950 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H61 Magnitude, % | Y | 25952 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H61 Magnitude, A | Y | 25954 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H61 Angle | Y | 25956 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H62 Magnitude, % | Y | 25958 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H62 Magnitude, A | Y | 25960 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H62 Angle | Y | 25962 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H63 Magnitude, % | Y | 25964 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H63 Magnitude, A | Y | 25966 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current N, H63 Angle | Y | 25968 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H1 Magnitude, % | Y | 25980 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H1 Magnitude, A | Y | 25982 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H1 Angle | Y | 25984 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H2 Magnitude, % | Y | 25986 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H2 Magnitude, A | Y | 25988 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H2 Angle | Y | 25990 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H3 Magnitude, % | Y | 25992 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H3 Magnitude, A | Y | 25994 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H3 Angle | Y | 25996 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H4 Magnitude, % | Y | 25998 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H4 Magnitude, A | Y | 26000 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H4 Angle | Y | 26002 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H5 Magnitude, % | Y | 26004 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H5 Magnitude, A | Y | 26006 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H5 Angle | Y | 26008 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H6 Magnitude, % | Y | 26010 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H6 Magnitude, A | Y | 26012 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H6 Angle | Y | 26014 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H7 Magnitude, % | Y | 26016 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H7 Magnitude, A | Y | 26018 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H7 Angle | Y | 26020 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H8 Magnitude, % | Y | 26022 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H8 Magnitude, A | Y | 26024 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H8 Angle | Y | 26026 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H9 Magnitude, % | Y | 26028 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H9 Magnitude, A | Y | 26030 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H9 Angle | Y | 26032 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H10 Magnitude, % | Y | 26034 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H10 Magnitude, A | Y | 26036 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H10 Angle | Y | 26038 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H11 Magnitude, % | Y | 26040 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H11 Magnitude, A | Y | 26042 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H11 Angle | Y | 26044 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H12 Magnitude, % | Y | 26046 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H12 Magnitude, A | Y | 26048 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H12 Angle | Y | 26050 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H13 Magnitude, % | Y | 26052 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H13 Magnitude, A | Y | 26054 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H13 Angle | Y | 26056 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H14 Magnitude, % | Y | 26058 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H14 Magnitude, A | Y | 26060 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H14 Angle | Y | 26062 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H15 Magnitude, % | Y | 26064 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H15 Magnitude, A | Y | 26066 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H15 Angle | Y | 26068 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H16 Magnitude, % | Y | 26070 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H16 Magnitude, A | Y | 26072 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H16 Angle | Y | 26074 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H17 Magnitude, % | Y | 26076 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H17 Magnitude, A | Y | 26078 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H17 Angle | Y | 26080 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H18 Magnitude, % | Y | 26082 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H18 Magnitude, A | Y | 26084 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H18 Angle | Y | 26086 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H19 Magnitude, % | Y | 26088 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H19 Magnitude, A | Y | 26090 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H19 Angle | Y | 26092 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H20 Magnitude, % | Y | 26094 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H20 Magnitude, A | Y | 26096 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H20 Angle | Y | 26098 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H21 Magnitude, % | Y | 26100 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H21 Magnitude, A | Y | 26102 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H21 Angle | Y | 26104 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H22 Magnitude, % | Y | 26106 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H22 Magnitude, A | Y | 26108 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H22 Angle | Y | 26110 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H23 Magnitude, % | Y | 26112 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H23 Magnitude, A | Y | 26114 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H23 Angle | Y | 26116 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H24 Magnitude, % | Y | 26118 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H24 Magnitude, A | Y | 26120 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H24 Angle | Y | 26122 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H25 Magnitude, % | Y | 26124 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H25 Magnitude, A | Y | 26126 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H25 Angle | Y | 26128 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H26 Magnitude, % | Y | 26130 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H26 Magnitude, A | Y | 26132 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H26 Angle | Y | 26134 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H27 Magnitude, % | Y | 26136 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H27 Magnitude, A | Y | 26138 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H27 Angle | Y | 26140 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H28 Magnitude, % | Y | 26142 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H28 Magnitude, A | Y | 26144 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H28 Angle | Y | 26146 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H29 Magnitude, % | Y | 26148 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H29 Magnitude, A | Y | 26150 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H29 Angle | Y | 26152 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H30 Magnitude, % | Y | 26154 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H30 Magnitude, A | Y | 26156 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H30 Angle | Y | 26158 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H31 Magnitude, % | Y | 26160 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H31 Magnitude, A | Y | 26162 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H31 Angle | Y | 26164 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H32 Magnitude, % | Y | 26166 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H32 Magnitude, A | Y | 26168 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H32 Angle | Y | 26170 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H33 Magnitude, % | Y | 26172 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H33 Magnitude, A | Y | 26174 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H33 Angle | Y | 26176 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H34 Magnitude, % | Y | 26178 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H34 Magnitude, A | Y | 26180 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H34 Angle | Y | 26182 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H35 Magnitude, % | Y | 26184 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H35 Magnitude, A | Y | 26186 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H35 Angle | Y | 26188 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H36 Magnitude, % | Y | 26190 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H36 Magnitude, A | Y | 26192 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H36 Angle | Y | 26194 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H37 Magnitude, % | Y | 26196 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H37 Magnitude, A | Y | 26198 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H37 Angle | Y | 26200 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H38 Magnitude, % | Y | 26202 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H38 Magnitude, A | Y | 26204 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H38 Angle | Y | 26206 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H39 Magnitude, % | Y | 26208 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H39 Magnitude, A | Y | 26210 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H39 Angle | Y | 26212 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H40 Magnitude, % | Y | 26214 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H40 Magnitude, A | Y | 26216 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H40 Angle | Y | 26218 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H41 Magnitude, % | Y | 26220 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H41 Magnitude, A | Y | 26222 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H41 Angle | Y | 26224 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H42 Magnitude, % | Y | 26226 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H42 Magnitude, A | Y | 26228 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H42 Angle | Y | 26230 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H43 Magnitude, % | Y | 26232 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H43 Magnitude, A | Y | 26234 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H43 Angle | Y | 26236 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H44 Magnitude, % | Y | 26238 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H44 Magnitude, A | Y | 26240 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H44 Angle | Y | 26242 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H45 Magnitude, % | Y | 26244 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H45 Magnitude, A | Y | 26246 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H45 Angle | Y | 26248 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H46 Magnitude, % | Y | 26250 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H46 Magnitude, A | Y | 26252 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H46 Angle | Y | 26254 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H47 Magnitude, % | Y | 26256 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H47 Magnitude, A | Y | 26258 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H47 Angle | Y | 26260 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H48 Magnitude, % | Y | 26262 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H48 Magnitude, A | Y | 26264 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H48 Angle | Y | 26266 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H49 Magnitude, % | Y | 26268 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H49 Magnitude, A | Y | 26270 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H49 Angle | Y | 26272 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H50 Magnitude, % | Y | 26274 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H50 Magnitude, A | Y | 26276 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H50 Angle | Y | 26278 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H51 Magnitude, % | Y | 26280 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H51 Magnitude, A | Y | 26282 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H51 Angle | Y | 26284 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H52 Magnitude, % | Y | 26286 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H52 Magnitude, A | Y | 26288 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H52 Angle | Y | 26290 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H53 Magnitude, % | Y | 26292 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H53 Magnitude, A | Y | 26294 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H53 Angle | Y | 26296 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H54 Magnitude, % | Y | 26298 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H54 Magnitude, A | Y | 26300 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H54 Angle | Y | 26302 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H55 Magnitude, % | Y | 26304 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H55 Magnitude, A | Y | 26306 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H55 Angle | Y | 26308 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H56 Magnitude, % | Y | 26310 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H56 Magnitude, A | Y | 26312 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H56 Angle | Y | 26314 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H57 Magnitude, % | Y | 26316 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H57 Magnitude, A | Y | 26318 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H57 Angle | Y | 26320 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H58 Magnitude, % | Y | 26322 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H58 Magnitude, A | Y | 26324 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H58 Angle | Y | 26326 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H59 Magnitude, % | Y | 26328 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H59 Magnitude, A | Y | 26330 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H59 Angle | Y | 26332 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H60 Magnitude, % | Y | 26334 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H60 Magnitude, A | Y | 26336 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H60 Angle | Y | 26338 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H61 Magnitude, % | Y | 26340 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H61 Magnitude, A | Y | 26342 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H61 Angle | Y | 26344 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H62 Magnitude, % | Y | 26346 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H62 Magnitude, A | Y | 26348 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H62 Angle | Y | 26350 | degrees | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H63 Magnitude, % | Y | 26352 | % | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H63 Magnitude, A | Y | 26354 | A | 2 | FLOAT32 | R |  |  | N
|  |  | Current G, H63 Angle | Y | 26356 | degrees | 2 | FLOAT32 | R |  |  | N
| Minimum Values |  |  | Y | 27214 | --- |  | --- | --- | --- | --- | ---
|  |  | Min/Max Reset Datetime | Y | 27214 | --- | 4 | DATETIME | R | --- | N/A | Y
|  | Current |  | Y | 27218 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Current A | Y | 27218 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current B | Y | 27220 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current C | Y | 27222 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current N | Y | 27224 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current G | Y | 27226 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current Avg | Y | 27228 | A | 2 | FLOAT32 | R |  |  | Y
|  | Current Unbalance |  | Y | 27230 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Current Unbalance A | Y | 27230 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current Unbalance B | Y | 27232 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current Unbalance C | Y | 27234 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Current Unbalance Worst | Y | 27236 | % | 2 | FLOAT32 | R |  |  | Y
|  | Voltage |  | Y | 27238 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Voltage A-B | Y | 27238 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage B-C | Y | 27240 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage C-A | Y | 27242 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage L-L Avg | Y | 27244 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage A-N | Y | 27246 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage B-N | Y | 27248 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage C-N | Y | 27250 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage L-N Avg | Y | 27254 | V | 2 | FLOAT32 | R |  |  | Y
|  | Voltage Unbalance |  | Y | 27256 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Voltage Unbalance A-B | Y | 27256 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance B-C | Y | 27258 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance C-A | Y | 27260 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance L-L Worst | Y | 27262 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance A-N | Y | 27264 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance B-N | Y | 27266 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance C-N | Y | 27268 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Voltage Unbalance L-N Worst | Y | 27270 | % | 2 | FLOAT32 | R |  |  | Y
|  | Power |  | Y | 27272 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Active Power A | Y | 27272 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Active Power B | Y | 27274 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Active Power C | Y | 27276 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Active Power Total | Y | 27278 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Reactive Power A | Y | 27280 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Reactive Power B | Y | 27282 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Reactive Power C | Y | 27284 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Reactive Power Total | Y | 27286 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Apparent Power A | Y | 27288 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Apparent Power B | Y | 27290 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Apparent Power C | Y | 27292 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Apparent Power Total | Y | 27294 | kVA | 2 | FLOAT32 | R |  |  | Y
|  | Power Factor |  | Y | 27306 | --- |  | --- | --- | --- | --- | ---
|  |  | Min Power Factor A | Y | 27306 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Power Factor B | Y | 27308 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Power Factor C | Y | 27310 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Power Factor Total | Y | 27312 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Displacement Power Factor A | Y | 27314 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Displacement Power Factor B | Y | 27316 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Displacement Power Factor C | Y | 27318 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Min Displacement PF Total | Y | 27320 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  | Total Harmonic Distortion, Current |  | Y | 27338 | --- |  | --- | --- | --- | --- | ---
|  |  | Min THD Current A | Y | 27338 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | Min THD Current B | Y | 27340 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Current C | Y | 27342 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Current N | Y | 27344 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Current G | Y | 27346 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Current A | Y | 27348 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y | thd = (RMS of harmonics / total RMS) * 100
|  |  | Min thd Current B | Y | 27350 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Current C | Y | 27352 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Current N | Y | 27354 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Current G | Y | 27356 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  | Total Demand Distortion | Min Total Demand Distortion | Y | 27358 | % | 2 | FLOAT32 | R | 0 – 100 | --- | Y
|  | Total Harmonic Distortion, Voltage |  | Y | 27360 | --- |  | --- | --- | --- | --- | ---
|  |  | Min THD Voltage A-B | Y | 27360 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage B-C | Y | 27362 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage C-A | Y | 27364 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage L-L Avg | Y | 27366 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage A-N | Y | 27368 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage B-N | Y | 27370 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage C-N | Y | 27372 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min THD Voltage L-N Avg | Y | 27376 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage A-B | Y | 27378 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage B-C | Y | 27380 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage C-A | Y | 27382 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage L-L Avg | Y | 27384 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage A-N | Y | 27386 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage B-N | Y | 27388 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage C-N | Y | 27390 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  |  | Min thd Voltage L-N Avg | Y | 27394 | % | 2 | FLOAT32 | R | 0 – 100 |  | Y
|  | Frequency | Min Frequency | Y | 27616 | Hz | 2 | FLOAT32 | R | 42 – 70 |  | Y
|  |  | Min Input Metering Rate 01 | Y | 27618 |  | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Input Metering Rate 02 | Y | 27620 |  | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Input Metering Rate 03 | Y | 27622 |  | 2 | FLOAT32 | R |  |  | Y
|  |  | Min Input Metering Rate 04 | Y | 27624 |  | 2 | FLOAT32 | R |  |  | Y
|  | Temperature | Min Temperature | Y | 27638 | degrees C | 2 | FLOAT32 | R | -40 -- 125 |  | Y | Internal unit temperature
|  |  | Min Temp Date/Time Also in diagnostics | Y | 27640 | --- | 4 | DATETIME | R | --- | N/A | Y
| Maximum Values |  |  | Y | 27694 | --- |  | --- | --- | --- | --- | ---
|  | Current |  | Y | 27694 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Current A | Y | 27694 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current B | Y | 27696 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current C | Y | 27698 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current N | Y | 27700 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current G | Y | 27702 | A | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current Avg | Y | 27704 | A | 2 | FLOAT32 | R |  |  | Y
|  | Current Unbalance |  | Y | 27706 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Current Unbalance A | Y | 27706 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current Unbalance B | Y | 27708 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current Unbalance C | Y | 27710 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Current Unbalance Worst | Y | 27712 | % | 2 | FLOAT32 | R |  |  | Y
|  | Voltage |  | Y | 27714 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Voltage A-B | Y | 27714 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage B-C | Y | 27716 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage C-A | Y | 27718 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage L-L Avg | Y | 27720 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage A-N | Y | 27722 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage B-N | Y | 27724 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage C-N | Y | 27726 | V | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage L-N Avg | Y | 27730 | V | 2 | FLOAT32 | R |  |  | Y
|  | Voltage Unbalance |  | Y | 27732 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Voltage Unbalance A-B | Y | 27732 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance B-C | Y | 27734 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance C-A | Y | 27736 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance L-L Worst | Y | 27738 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance A-N | Y | 27740 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance B-N | Y | 27742 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance C-N | Y | 27744 | % | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Voltage Unbalance L-N Worst | Y | 27746 | % | 2 | FLOAT32 | R |  |  | Y
|  | Power |  | Y | 27748 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Active Power A | Y | 27748 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Active Power B | Y | 27750 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Active Power C | Y | 27752 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Active Power Total | Y | 27754 | kW | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Reactive Power A | Y | 27756 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Reactive Power B | Y | 27758 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Reactive Power C | Y | 27760 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Reactive Power Total | Y | 27762 | kVAR | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Apparent Power A | Y | 27764 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Apparent Power B | Y | 27766 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Apparent Power C | Y | 27768 | kVA | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Apparent Power Total | Y | 27770 | kVA | 2 | FLOAT32 | R |  |  | Y
|  | Power Factor |  | Y | 27782 | --- |  | --- | --- | --- | --- | ---
|  |  | Max Power Factor A | Y | 27782 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Power Factor B | Y | 27784 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Power Factor C | Y | 27786 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Power Factor Total | Y | 27788 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Displacement Power Factor A | Y | 27790 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Displacement Power Factor B | Y | 27792 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Displacement Power Factor C | Y | 27794 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  |  | Max Displacement PF Total | Y | 27796 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0 |  | Y
|  | Total Harmonic Distortion, Current |  | Y | 27814 | --- |  | --- | --- | --- | --- | ---
|  |  | Max THD Current A | Y | 27814 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | Max THD Current B | Y | 27816 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Current C | Y | 27818 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Current N | Y | 27820 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Current G | Y | 27822 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Current A | Y | 27824 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y | thd = (RMS of harmonics / total RMS) * 100
|  |  | Max thd Current B | Y | 27826 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Current C | Y | 27828 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Current N | Y | 27830 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Current G | Y | 27832 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  | Total Demand Distortion | Max Total Demand Distortion | Y | 27834 | % | 2 | FLOAT32 | R | 0 – 100 | --- | Y
|  | Total Harmonic Distortion, Voltage |  | Y | 27836 | --- |  | --- | --- | --- | --- | ---
|  |  | Max THD Voltage A-B | Y | 27836 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage B-C | Y | 27838 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage C-A | Y | 27840 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage L-L | Y | 27842 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage A-N | Y | 27844 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage B-N | Y | 27846 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage C-N | Y | 27848 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max THD Voltage L-N | Y | 27852 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage A-B | Y | 27854 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage B-C | Y | 27856 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage C-A | Y | 27858 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage L-L | Y | 27860 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage A-N | Y | 27862 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage B-N | Y | 27864 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage C-N | Y | 27866 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  |  | Max thd Voltage L-N | Y | 27870 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | Y
|  | Frequency | Max Frequency | Y | 28092 | Hz | 2 | FLOAT32 | R | 42 – 70 |  | Y
|  |  | Max Input Metering Rate 01 | Y | 28094 | --- | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Input Metering Rate 02 | Y | 28096 | --- | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Input Metering Rate 03 | Y | 28098 | --- | 2 | FLOAT32 | R |  |  | Y
|  |  | Max Input Metering Rate 04 | Y | 28100 | --- | 2 | FLOAT32 | R |  |  | Y
|  | Temperature | Max Temperature | Y | 28114 | degrees C | 2 | FLOAT32 | R | -40 -- 125 |  | Y | Internal unit temperature
|  |  | Max Temp Date/Time also in diagnostics | Y | 28116 | --- | 4 | DATETIME | R | --- | N/A | Y
| Firmware Versions (advanced multi-CPU and programmable logc ) |  |  | Y | 32285 | --- |  | --- | --- | --- | --- | ---
|  | FPGA 1 |  | Y | 32285 | --- |  | --- | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | 32285 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | 32286 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Y – Minor | Y | 32287 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Z – Quality | Y | 32288 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | 32290 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Y | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | 32291 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Y – Minor | Y | 32292 | --- | 1 | INT16U | R | 00 – 99 | 0 | Y
|  |  | Z – Quality | Y | 32293 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Y
|  |  | Date/Time of Last Firmware Download | Y | 32295 | --- | 4 | DATETIME | R | --- | N/A | Y
|  |  | BACnet Device ID | Y | 64483 | --- | 2 | INT32U | RW | --- | --- | Y | Last 6 digits of Serial Number
|  |  | BACnet UDP Port | Y | 64485 | --- | 1 | INT16U | RW | --- | 0xBAC0 | Y | BACnet UDP Port
|  |  | BACnet BBMD Status | Y | 64486 | --- | 1 | INT16U | RW | 0 - 1 | 0 | Y | BACnet BBMD Status
|  |  | BACnet BBMD IP Address | Y | 64487 | --- | 2 | INT16U | RW | --- | 0 | Y | BACnet BBMD IP Address
|  |  | BACnet BBMD Port | Y | 64489 | --- | 1 | INT16U | RW | --- | 0xBAC0 | Y | BACnet BBMD Port
|  |  | BACnet BBMD Time to Live | Y | 64490 | --- | 1 | INT16U | RW | --- | 600 | Y | BACnet BBMD Time to Live
|  |  | BACnet APDU Timeout | Y | 64491 | --- | 1 | INT16U | RW | --- | 0 | Y | BACnet APDU Timeout
|  |  | BACnet APDU Number of Retries | Y | 64492 | --- | 1 | INT16U | RW | --- | 0 | Y | BACnet APDU Number of Retries

## Coils
Category | Sub Cat 1 | Sub Cat 2 | Description Access Via Function Code 0x01 and 0x02 | PM5500 | Reference Register | Bit | Coil | Publish
Digital IO Status |  |  |  | Y |  |  |  | Y
| Digital Inputs |  |  | Y |  |  |  | Y
|  | Digital Input Status Validity - Base Unit |  | Y |  |  |  | Y
|  |  | Base Unit Digital Input 1 Validity | Y | 2400 | 0 | 38400 | Y
|  |  | Base Unit Digital Input 2 Validity | Y | 2400 | 1 | 38401 | Y
|  |  | Base Unit Digital Input 3 Validity | Y | 2400 | 2 | 38402 | Y
|  |  | Base Unit Digital Input 4 Validity | Y | 2400 | 3 | 38403 | Y
|  | Digital Input Status - Base Unit |  | Y |  |  |  | Y
|  |  | Base Unit Digital Input 1 | Y | 2401 | 0 | 38416 | Y
|  |  | Base Unit Digital Input 2 | Y | 2401 | 1 | 38417 | Y
|  |  | Base Unit Digital Input 3 | Y | 2401 | 2 | 38418 | Y
|  |  | Base Unit Digital Input 4 | Y | 2401 | 3 | 38419 | Y
| Digital Outputs |  |  | Y |  |  |  | Y
|  | Digital Output Status Validity - Base Unit |  | Y |  |  |  | Y
|  |  | Base Unit Digital Output 1 Validity | Y | 2402 | 0 | 38432 | Y
|  |  | Base Unit Digital Output 2 Validity | Y | 2402 | 1 | 38433 | Y
|  | Digital Output Status - Base Unit |  | Y |  |  |  | Y
|  |  | Base Unit Digital Output 1 | Y | 2403 | 0 | 38448 | Y
|  |  | Base Unit Digital Output 2 | Y | 2403 | 1 | 38449 | Y
Detected Alarm Status |  |  |  | Y |  |  |  | Y
| Detected Status |  |  | Y |  |  |  | Y
|  | Standard - 1 second Group 1 Validity |  | Y |  |  |  | Y
|  |  | Over Current, Phase Validity | Y | 2420 | 0 | 38720 | Y
|  |  | Under Current, Phase Validity | Y | 2420 | 1 | 38721 | Y
|  |  | Over Current, Neutral Validity | Y | 2420 | 2 | 38722 | Y
|  |  | Over Current, Ground Validity | Y | 2420 | 3 | 38723 | Y
|  |  | Over Voltage, L-L Validity | Y | 2420 | 4 | 38724 | Y
|  |  | Under Voltage, L-L Validity | Y | 2420 | 5 | 38725 | Y
|  |  | Over Voltage, L-N Validity | Y | 2420 | 6 | 38726 | Y
|  |  | Under Voltage, L-N Validity | Y | 2420 | 7 | 38727 | Y
|  |  | Over Power, Active Validity | Y | 2420 | 8 | 38728 | Y
|  |  | Over Power, Reactive Validity | Y | 2420 | 9 | 38729 | Y
|  |  | Over Power, Apparent Validity | Y | 2420 | 10 | 38730 | Y
|  |  | Leading Power Factor, True Validity | Y | 2420 | 11 | 38731 | Y
|  |  | Lagging Power Factor, True Validity | Y | 2420 | 12 | 38732 | Y
|  |  | Leading Power Factor, Displacement Validity | Y | 2420 | 13 | 38733 | Y
|  |  | Lagging Power Factor, Displacement Validity | Y | 2420 | 14 | 38734 | Y
|  |  | Over Demand, Active Power, Present Validity | Y | 2420 | 15 | 38735 | Y
|  | Standard - 1 second Group 1 |  | Y |  |  |  | Y
|  |  | Over Current, Phase | Y | 2421 | 0 | 38736 | Y
|  |  | Under Current, Phase | Y | 2421 | 1 | 38737 | Y
|  |  | Over Current, Neutral | Y | 2421 | 2 | 38738 | Y
|  |  | Over Current, Ground | Y | 2421 | 3 | 38739 | Y
|  |  | Over Voltage, L-L | Y | 2421 | 4 | 38740 | Y
|  |  | Under Voltage, L-L | Y | 2421 | 5 | 38741 | Y
|  |  | Over Voltage, L-N | Y | 2421 | 6 | 38742 | Y
|  |  | Under Voltage, L-N | Y | 2421 | 7 | 38743 | Y
|  |  | Over Power, Active | Y | 2421 | 8 | 38744 | Y
|  |  | Over Power, Reactive | Y | 2421 | 9 | 38745 | Y
|  |  | Over Power, Apparent | Y | 2421 | 10 | 38746 | Y
|  |  | Leading Power Factor, True | Y | 2421 | 11 | 38747 | Y
|  |  | Lagging Power Factor, True | Y | 2421 | 12 | 38748 | Y
|  |  | Leading Power Factor, Displacement | Y | 2421 | 13 | 38749 | Y
|  |  | Lagging Power Factor, Displacement | Y | 2421 | 14 | 38750 | Y
|  |  | Over Demand, Active Power, Present | Y | 2421 | 15 | 38751 | Y
|  | Standard - 1 second Group 2 Validity |  | Y |  |  |  | Y
|  |  | Over Demand, Active Power, Last Validity | Y | 2422 | 0 | 38752 | Y
|  |  | Over Demand, Active Power, Predicted Validity | Y | 2422 | 1 | 38753 | Y
|  |  | Over Demand, Reactive Power, Present Validity | Y | 2422 | 2 | 38754 | Y
|  |  | Over Demand, Reactive Power, Last Validity | Y | 2422 | 3 | 38755 | Y
|  |  | Over Demand, Reactive Power, Predicted Validity | Y | 2422 | 4 | 38756 | Y
|  |  | Over Demand, Apparent Power, Present Validity | Y | 2422 | 5 | 38757 | Y
|  |  | Over Demand, Apparent Power, Last Validity | Y | 2422 | 6 | 38758 | Y
|  |  | Over Demand, Apparent Power, Predicted Validity | Y | 2422 | 7 | 38759 | Y
|  |  | Over Frequency Validity | Y | 2422 | 8 | 38760 | Y
|  |  | Under Frequency Validity | Y | 2422 | 9 | 38761 | Y
|  |  | Over Voltage Unbalance Validity | Y | 2422 | 10 | 38762 | Y
|  |  | Over Voltage Total Harmonic Distortion Validity | Y | 2422 | 11 | 38763 | Y
|  |  | Phase Loss Validity | Y | 2422 | 12 | 38764 | Y
|  | Standard - 1 second Group 2 |  | Y |  |  |  | Y
|  |  | Over Demand, Active Power, Last | Y | 2423 | 0 | 38768 | Y
|  |  | Over Demand, Active Power, Predicted | Y | 2423 | 1 | 38769 | Y
|  |  | Over Demand, Reactive Power, Present | Y | 2423 | 2 | 38770 | Y
|  |  | Over Demand, Reactive Power, Last | Y | 2423 | 3 | 38771 | Y
|  |  | Over Demand, Reactive Power, Predicted | Y | 2423 | 4 | 38772 | Y
|  |  | Over Demand, Apparent Power, Present | Y | 2423 | 5 | 38773 | Y
|  |  | Over Demand, Apparent Power, Last | Y | 2423 | 6 | 38774 | Y
|  |  | Over Demand, Apparent Power, Predicted | Y | 2423 | 7 | 38775 | Y
|  |  | Over Frequency | Y | 2423 | 8 | 38776 | Y
|  |  | Under Frequency | Y | 2423 | 9 | 38777 | Y
|  |  | Over Voltage Unbalance | Y | 2423 | 10 | 38778 | Y
|  |  | Over Voltage Total Harmonic Distortion | Y | 2423 | 11 | 38779 | Y
|  |  | Phase Loss | Y | 2423 | 12 | 38780 | Y
|  | Standard - 1 second Group 3 Validity |  | Y |  |  |  | Y
|  | Standard - 1 second Group 3 |  | Y |  |  |  | Y
|  | Custom - 1 second Validity |  | Y |  |  |  | Y
|  |  | Custom Alarm 1 Validity | Y | 2426 | 0 | 38816 | Y
|  |  | Custom Alarm 2 Validity | Y | 2426 | 1 | 38817 | Y
|  |  | Custom Alarm 3 Validity | Y | 2426 | 2 | 38818 | Y
|  |  | Custom Alarm 4 Validity | Y | 2426 | 3 | 38819 | Y
|  |  | Custom Alarm 5 Validity | Y | 2426 | 4 | 38820 | Y
|  | Custom - 1 second |  | Y |  |  |  | Y
|  |  | Custom Alarm 1 | Y | 2427 | 0 | 38832 | Y
|  |  | Custom Alarm 2 | Y | 2427 | 1 | 38833 | Y
|  |  | Custom Alarm 3 | Y | 2427 | 2 | 38834 | Y
|  |  | Custom Alarm 4 | Y | 2427 | 3 | 38835 | Y
|  |  | Custom Alarm 5 | Y | 2427 | 4 | 38836 | Y
|  | Standard - High Speed Group 1 Validity |  | Y |  |  |  | Y
|  | Standard - High Speed Group 1 |  | Y |  |  |  | Y
|  | Standard - High Speed Group 2 Validity |  | Y |  |  |  | Y
|  | Standard - High Speed Group 2 |  | Y |  |  |  | Y
|  | Custom - High Speed Validity |  | Y |  |  |  | Y
|  | Custom - High Speed |  | Y |  |  |  | Y
|  | Disturbance Validity |  | Y |  |  |  | Y
|  | Disturbance |  | Y |  |  |  | Y
|  | Transient Validity |  | Y |  |  |  | Y
|  | Transient |  | Y |  |  |  | Y
|  | Waveshape Validity |  | Y |  |  |  | Y
|  | Waveshape |  | Y |  |  |  | Y
|  | Unary Validity |  | Y |  |  |  | Y
|  |  | Meter Power Up (Control Power Loss) Valdity | Y | 2440 | 0 | 39040 | Y
|  |  | Meter Reset Valdity | Y | 2440 | 1 | 39041 | Y
|  |  | Meter Diagnostic Valdity | Y | 2440 | 2 | 39042 | Y
|  |  | Phase Reversal Valdity | Y | 2440 | 3 | 39043 | Y
|  | Unary |  | Y |  |  |  | Y
|  |  | Meter Power Up (Control Power Loss) | Y | 2441 | 0 | 39056 | Y
|  |  | Meter Reset | Y | 2441 | 1 | 39057 | Y
|  |  | Meter Diagnostic | Y | 2441 | 2 | 39058 | Y
|  |  | Phase Reversal | Y | 2441 | 3 | 39059 | Y
|  | Digital Group 1 Validity |  | Y |  |  |  | Y
|  |  | Digital Alarm DI1 Validity | Y | 2442 | 0 | 39072 | Y
|  |  | Digital Alarm DI2 Validity | Y | 2442 | 1 | 39073 | Y
|  |  | Digital Alarm DI2 Validity | Y | 2442 | 2 | 39074 | Y
|  |  | Digital Alarm DI2 Validity | Y | 2442 | 3 | 39075 | Y
|  | Digital Group 1 |  | Y |  |  |  | Y
|  |  | Digital Alarm DI1 | Y | 2443 | 0 | 39088 | Y
|  |  | Digital Alarm DI2 | Y | 2443 | 1 | 39089 | Y
|  |  | Digital Alarm DI2 | Y | 2443 | 2 | 39090 | Y
|  |  | Digital Alarm DI2 | Y | 2443 | 3 | 39091 | Y
|  | Logic Validity |  | Y |  |  |  | Y
|  |  | Logic Alarm 1 Validity | Y | 2456 | 0 | 39296 | Y
|  |  | Logic Alarm 2 Validity | Y | 2456 | 1 | 39297 | Y
|  |  | Logic Alarm 3 Validity | Y | 2456 | 2 | 39298 | Y
|  |  | Logic Alarm 4 Validity | Y | 2456 | 3 | 39299 | Y
|  |  | Logic Alarm 5 Validity | Y | 2456 | 4 | 39300 | Y
|  |  | Logic Alarm 6 Validity | Y | 2456 | 5 | 39301 | Y
|  |  | Logic Alarm 7 Validity | Y | 2456 | 6 | 39302 | Y
|  |  | Logic Alarm 8 Validity | Y | 2456 | 7 | 39303 | Y
|  |  | Logic Alarm 9 Validity | Y | 2456 | 8 | 39304 | Y
|  |  | Logic Alarm 10 Validity | Y | 2456 | 9 | 39305 | Y
|  | Logic |  | Y |  |  |  | Y
|  |  | Logic Alarm 1 | Y | 2457 | 0 | 39312 | Y
|  |  | Logic Alarm 2 | Y | 2457 | 1 | 39313 | Y
|  |  | Logic Alarm 3 | Y | 2457 | 2 | 39314 | Y
|  |  | Logic Alarm 4 | Y | 2457 | 3 | 39315 | Y
|  |  | Logic Alarm 5 | Y | 2457 | 4 | 39316 | Y
|  |  | Logic Alarm 6 | Y | 2457 | 5 | 39317 | Y
|  |  | Logic Alarm 7 | Y | 2457 | 6 | 39318 | Y
|  |  | Logic Alarm 8 | Y | 2457 | 7 | 39319 | Y
|  |  | Logic Alarm 9 | Y | 2457 | 8 | 39320 | Y
|  |  | Logic Alarm 10 | Y | 2457 | 9 | 39321 | Y

## Commands
Subsystem | Command Name | Command Number | Command Tag | PM5500 |  | Parameters | User Notes | Allowed for Unprotected Command Interface
REGISTER_ACCESS (0-999) |  |  |  | Y | Y
| Reset Subsystem(s) to Default | 1 | C_RESET_SUBSYS_TO_DEFAULT | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Subsystems) (3) Subsystem ID or -1 (For All Subsystems) | Subsystem IDs 0 = Register Access 1 = System 2 = Metering 3 = Commands 4 = HMI 5 = Communications 6 = IO 7 = Alarms 8 = Files 9 = Diagnostics 10 = Security
SYSTEM (1000-1999) |  |  |  | Y | Y
| Warm Start Reset | 1000 | C_WARM_START_RESET | Y |  | (1) Command Semaphore | This command does not provide a command status or result.
| Reset Power Fail Counter | 1002 | C_RESET_POWER_FAIL_COUNT | Y |  | (1) Command Semaphore |  | Y
| Set Date/Time | 1003 | C_SET_DT | Y |  | (1) Command Semaphore (2) Year (2000-2127) (3) Month (4) Day of Month (5) Hour (6) Minute (7) Second (8) Millisecond |  | Y
| Meter Name Setup | 1008 | C_METER_NAME_SETUP | Y |  | (1) Command Semaphore (2-21 ) Meter Name
METERING (2000-2999) |  |  |  | Y | Y
| Basic Meter Setup | 2000 | C_BASIC_METER_SETUP | Y |  | (1) Command Semaphore (2) Number of Phases (3) Number of Wires (4) Power System Configuration (5) Nominal Frequency (6-7) Nominal Voltage (8-9) Nominal Current (10-11) Nominal Power Factor (12) Normal Phase Rotation
| Demand System Setup | 2002 | C_DMD_SETUP | Y |  | (1) Command Semaphore (2) Demand System ID (3) Demand Method (4) Demand Interval Duration (5) Demand Subinterval Duration | Demand System ID 1 = Power 2 = Current 3 = Input Metering
| Energy Pulse Output Setup | 2003 | C_ENERGY_PULSE_OUTPUT_SETUP | Y |  | (1) Command Semaphore (2) Energy Channel (3) Digital Output ID (4-5) Pulse Weight (6) Energy Channel (7) Digital Output ID (8-9) Pulse Weight (10) Energy Channel (11) Digital Output ID (12-13) Pulse Weight | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 99 = Energy LED
| Preset Accumuated Energy | 2006 | C_PRESET_ACCUMULATED_ENG | Y |  | (1) Command Semaphore (2-5) Active Energy Delivered (Into Load) (6-9) Active Energy Received (Out of Load) (10-13) Reactive Energy Delivered (14-17) Reactive Energy Received (18-21) Apparent Energy Delivered (22-25) Apparent Energy Received |  | Y
| Reset Cycle Count | 2007 | C_RESET_CYCLE_COUNT | Y |  | (1) Command Semaphore |  | Y
| Multi-tariff Metering Control | 2008 | C_MULTITARIFF_CONTROL | Y |  | (1) Command Semaphore (2) Active Rate (0-8) |  | Y
| Reset All Min/Max | 2009 | C_RESET_ALL_MIN_MAX | Y |  | (1) Command Semaphore |  | Y
| Reset Active Load Timer | 2010 | C_RESET_ACTIVE_LOAD_TIMER | Y |  | (1) Command Semaphore |  | Y
| Reset All Demands | 2011 | C_RESET_ALL_DMDS | Y |  | (1) Command Semaphore (2-5) Demand Reset Password | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Current Demand | 2012 | C_RESET_CUR_DMD | Y |  | (1) Command Semaphore |  | Y
| Reset Power Demand | 2013 | C_RESET_POWER_DMD | Y |  | (1) Command Semaphore (2-5) Demand Reset Password | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Input Metering Demand | 2014 | C_RESET_INPUT_MET_DMD | Y |  | (1) Command Semaphore |  | Y
| Reset All Peak Demands | 2015 | C_RESET_ALL_PEAK_DMDS | Y |  | (1) Command Semaphore (2-5) Demand Reset Password | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Current Peak Demands | 2016 | C_RESET_CUR_PEAK_DMDS | Y |  | (1) Command Semaphore |  | Y
| Reset Power Peak Demands | 2017 | C_RESET_POWER_PEAK_DMDS | Y |  | (1) Command Semaphore (2-5) Demand Reset Password | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Input Metering Peak Demand | 2018 | C_RESET_INPUT_MET_PEAK_DMD | Y |  | (1) Command Semaphore |  | Y
| Start New Demand Interval | 2019 | C_START_NEW_DMD_INTERVAL | Y |  | (1) Command Semaphore (2) Bitmap of Demand Systems |  | Y
| Reset All Energies | 2020 | C_RESET_ALL_ENERGIES | Y |  | (1) Command Semaphore |  | Y
| Reset All Accumulated Energies | 2021 | C_RESET_ALL_ACC_ENG | Y |  | (1) Command Semaphore |  | Y
| Reset All Time-of-Use Multi-Tariff Energies | 2022 | C_RESET_ALL_TOU_MT_ENG | Y |  | (1) Command Semaphore |  | Y
| Reset Input Metering Accumulations | 2023 | C_RESET_INPUT_MET_ACC | Y |  | (1) Command Semaphore (2) 1 or -1 ( For all Input Metering channels) (3) Channel ID or -1 (For all channels) |  | Y
| Reset All Energy Pulse Output Channels | 2024 | C_RESET_ALL_ENG_PULSE_OUTPUT | Y |  | (1) Command Semaphore |  | Y
| Meter Initialization | 2037 | C_METER_INITIALIZATION | Y |  | (1) Command Semaphore | Resets Energy, Demand, Demand peaks, Min/Max, Alarm counters, Alarm logs, Alarm event queue, IO Counters, IO Timers, Active Load Timer, Comm diagnostics, power fail counter, cycle counter Data logs (Scout only), and Waveform capture Files (Scout only).
| Energy / Alarm LED Enable | 2039 | C_ENERGY_LED_ENABLE | Y |  | (1) Command Semaphore (2) 0 = Disable / 1 = Alarm / 2 = Energy
| TDD Setup | 2043 | C_TDD_SETUP | Y |  | (1) Command Semaphore (2-3) Peak Current Demand Over Last Year
| Active Load Timer Setup | 2044 | C_ACTIVE_LOAD_TIMER_SETUP | Y |  | (1) Command Semaphore (2-3) Active Load Timer Setpoint
| Set Multi-Tariff Mode | 2053 | C_MULTI_TARIFF_MODE | Y |  | (1) Command Semaphore (2) Mode |  | N
| Set Multi-Tariff Rate Command | 2054 | C_MULTI_TARIFF_RATE | Y |  | (1) Command Semaphore (2) Active Rate 0-8 | Only allow if mode is Command | Y
| Set Multi-Tariff Time of Day | 2055 | C_MULTI_TARIFF_TOD | Y |  | (1) Command Semaphore (2) RATE 1 Day Type (3) RATE 1 Start Time (4) RATE 1 End Time (5) RATE 2 Day Type (6) RATE 2 Start Time (7) RATE 2 End Time (8) RATE 3 Day Type (9) RATE 3 Start Time (10) RATE 3 End Time (11) RATE 4 Day Type (12) RATE 4 Start Time (13) RATE 4 End Time (14) RATE 5 Day Type (15) RATE 5 Start Time (16) RATE 5 End Time (17) RATE 6 Day Type (18) RATE 6 Start Time (19) RATE 6 End Time (20) RATE 7 Day Type (21) RATE 7 Start Time (22) RATE 7 End Time (23) RATE 8 Day Type (24) RATE 8 Start Time (25) RATE 8 End Time |  | N
| Set Time for Demand Synch | 2063 | C_DMD_SYNCH_TIME | Y |  | (1) Command Semaphore (2) Synch Time | Time is 0000 to 2359 | N
COMMANDS (3000-3999) |  |  |  | Y | Y
HMI (4000-4999) |  |  |  | Y | Y
| HMI Setup | 4000 | C_HMI_SETUP | Y |  | (1) Command Semaphore (2) HMI Contrast Setting (3) HMI Backlight On/Off (4) HMI Language (5) HMI IEC/IEEE Mode (6) HMI Date Format (7) HMI Time Format (8) HMI Backlight Timeout (9) HMI Screen Timeout (10) HMI Energy Resolution (11) HMI Current Resolution (12) HMI Voltage Resulution (13) HMI Power Resolution
| HMI QR SCREEN ENABLE | 4007 | C_HMI_QR_SCREEN_ENABLE | Y |  | (1) Command Semaphore (2) Enable/Disable QR Code Screen 0 = Disable 1 = Enable
COMMUNICATIONS (5000-5999) |  |  |  | Y | Y
| Communications Setup | 5000 | C_COMMS_SETUP | Y |  | (1) Command Semaphore (2) Communications Port ID (3) RS-485 Comm Port (M/S) Protocol (4) RS-485 Comm Port (M/S) Address (5) RS-485 Comm Port (M/S) Baud Rate (6) RS-485 Comm Port (M/S) Parity (7) RS-485 Comm Port (M/S) Modbus ASCII Default Timeout | Communications Port ID 1 = Standard RS-485 | Y
| Reset Comm Port Counters | 5001 | C_RESET_COMM_CHANNEL_COUNT | Y |  | (1) Command Semphore (2) Communications Port ID | Communications Port ID 1 = Standard RS-485 | Y
IO (6000-6999) |  |  |  | Y | Y
| Digital Output Setup | 6000 | C_DO_SETUP | Y |  | (1) Command Semaphore (2) Digital Output ID (3-22) Label (23) Behavioral Mode (24) On Time For Timed Mode | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
| Digital Input Setup | 6001 | C_DI_SETUP | Y |  | (1) Command Semaphore (2) Digital Input ID (3-22) Label (23) Debounce Time | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02 3 = Digital Input S03 4 = Digital Input S04
| De-energize Digital Output | 6002 | C_DE_ENERGIZE_DO | Y |  | (1) Command Semaphore (2) Digital Output ID | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 | Y
| Energize Digital Output | 6003 | C_ENERGIZE_DO | Y |  | (1) Command Semaphore (2) Digital Output ID | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 | Y
| Release Digital Output From Coil Hold | 6004 | C_RELEASE_DO_FROM_COIL_HOLD | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 | Y
| Release Digital Output From Override Control | 6005 | C_RELEASE_DO_FROM_OVERRIDE | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
| Place Digital Output In Override Control | 6006 | C_PLACE_DO_IN_OVERRIDE | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
| Reset Operation Counter for Digital Output | 6007 | C_RESET_COUNT_FOR_DO | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 | Y
| Reset On-Time for Digital Output | 6008 | C_RESET_ON_TIME_FOR_DO | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 | Y
| Reset Operation Counter for Digital Input | 6009 | C_RESET_COUNT_FOR_DI | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Inputs) (3) Digital Input ID or -1 (For All Digital Inputs) | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02 3 = Digital Input S03 4 = Digital Input S04 | Y
| Reset On-Time for Digital Input | 6010 | C_RESET_ON_TIME_FOR_DI | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Digital Inputs) (3) Digital Input ID or -1 (For All Digital Inputs) | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02 3 = Digital Input S03 4 = Digital Input S04 | Y
| Setup Digital Input to Demand Associations | 6011 | C_DI_SETUP_DEMAND | Y |  | (1) Command Semaphore (2) Digital Input ID for Demand System 1 (3) Digital Input ID for Demand System 2 (4) Digital Input ID for Demand System 3 (5) Digital Input ID for Demand System 4 (6) Digital Input ID for Demand System 5 (7) Digital Input ID for Demand System 6
| Setup Digital Output to Demand Associations | 6012 | C_DO_SETUP_DEMAND | Y |  | (1) Command Semaphore (2) Digital Output ID for Demand System 1 (3) Digital Output ID for Demand System 2 (4) Digital Output ID for Demand System 3 (5) Digital Output ID for Demand System 4 (6) Digital Output ID for Demand System 5 (7) Digital Output ID for Demand System 6
| Setup Digital Input to Multi-Tariff Associations | 6013 | C_DI_SETUP_MULTI_TARIFF | Y |  | (1) Command Semaphore (2) Number of Multi-tariff Rates Active (3) Number of Digital Inputs Used to Control Multi-tariff |  | N
| Input Metering Setup | 6014 | C_INPUT_METERING_SETUP | Y |  | (1) Command Semaphore (2) Input Metering Channel (3-22) Label (23) Mode (24-25) Metering Pulse Weight (26) Consumption Units Code (27) Demand Units Code (28) Digital Input Association
| De-energize Digital Output While in Override | 6015 | C_DE_ENERGIZE_DO_OVERRIDE | Y |  | (1) Command Semaphore (2) Digital Output ID | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
| Energize Digital Output While in Override | 6016 | C_ENERGIZE_DO_OVERRIDE | Y |  | (1) Command Semaphore (2) Digital Output ID | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
ALARMS (7000-7999) |  |  |  | Y | Y
| Over/Under Alarm Setup | 7000 | C_OVR_UND_ALM_SETUP | Y |  | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Setpoints (0 = Fixed, 1 = Variable) (5) Learning (0 = Not Learning, 1 = Learning) (6) Enable (0 = Disabled, 1 = Enabled) (7-8) Pickup Setpoint (9-10) Pickup Time Delay (11-12) Dropout Setpoint (13-14) Dropout Time Delay (15) Digital Outputs to Associate - Standard | Alarm ID 1 = Over Current, Phase 2 = Under Current, Phase 3 = Over Current, Neutral 4 = Over Current, Ground 5 = Over Voltage, L-L 6 = Under Voltage, L-L 7 = Over Voltage, L-N 8 = Under Voltage, L-N 9 = Over Power, Active 10 = Over Power, Reactive 11 = Over Power, Apparent 12 = Leading Power Factor, True 13 = Lagging Power Factor, True 14 = Leading Power Factor, Displacement 15 = Lagging Power Factor, Displacement 16 = Over Demand, Active Power, Present 17 = Over Demand, Active Power, Last 18 = Over Demand, Active Power, Predicted 19 = Over Demand, Reactive Power, Present 20 = Over Demand, Reactive Power, Last 21 = Over Demand, Reactive Power, Predicted 22 = Over Demand, Apparent Power, Present 23 = Over Demand, Apparent Power, Last 24 = Over Demand, Apparent Power, Predicted 25 = Over Frequency 26 = Under Frequency 27 = Over Voltage Unbalance 28 = Over Voltage Total Harmonic Distortion 29 = Phase Loss 41 = Custom Alarm 1 42 = Custom Alarm 2 43 = Custom Alarm 3 44 = Custom Alarm 4 45 = Custom Alarm 5 46 = Custom Alarm 6 47 = Custom Alarm 7 48 = Custom Alarm 8 49 = Custom Alarm 9 50 = Custom Alarm 10
| Custom Over/Under Alarm Creation | 7001 | C_CUSTOM_OVR_UND_ALM_CREATE | Y |  | (1) Command Semaphore (2) Alarm ID (3-22) Label (23) Subtype (24) Parameter (25) Modifier (26) Phases (27) Level | Alarm ID 41 = Custom Alarm 1 42 = Custom Alarm 2 43 = Custom Alarm 3 44 = Custom Alarm 4 45 = Custom Alarm 5 46 = Custom Alarm 6 47 = Custom Alarm 7 48 = Custom Alarm 8 49 = Custom Alarm 9 50 = Custom Alarm 10 PM5500 only supports 1-5
| Reset Alarm Counters | 7002 | C_RESET_ALM_COUNT | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Alarm Counters) (3) Alarm Counter ID or -1 (For All Alarm Counters) | Alarm ID 1-29 1-Second Standard 41-50 1-Second Custom 101-104 Unary 111-114 Digital
| Acknowledge Alarms | 7003 | C_ACK_ALMS | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Alarms) (3) Alarm ID or -1 (For All Alarms) |  | Y
| Disable Alarms | 7004 | C_DISABLE_ALMS | Y |  | (1) Command Semaphore (2) 1 or -1 (For All Alarms) (3) Alarm ID or -1 (For All Alarms)
| Reset Aggregated Alarm History | 7005 | C_RESET_REG_BASED_ALM_LOG | Y |  | (1) Command Semaphore |  | Y
| Reset Event Queue | 7006 | C_RESET_EVENT_QUEUE | Y |  | (1) Command Semaphore |  | Y
| Digital Alarm Setup | 7007 | C_DIGITAL_ALARM_SETUP | Y |  | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Enable (0 = Disabled, 1 = Enabled) (5) Subtype (0 = Off, 1 = On) (6-7) Pickup Time Delay (8-9) Dropout Time Delay (10) Digital Outputs to Associate - Standard | Alarm ID 111 = Digital Input S01 112 = Digital Input S02 113 = Digital Input S03 114 = Digital Input S04
| Unary Alarm Setup | 7008 | C_UNARY_ALARM_SETUP | Y |  | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Enable (0 = Disabled, 1 = Enabled) (5) Digital Outputs to Associate - Standard | Alarm ID 101 = Meter Power Up (Control Power Loss) 102 = Meter Reset 103 = Meter Diagnostics 104 = Phase Reversal
| Logic Alarm Setup | 7010 | C_LOGIC_ALARM_SETUP | Y |  | (1) Command Semaphore (2) Alarm ID (201-210) (3-22) Label (23) Priority (0=None, 1=High, 2=Medium, 3=Low) (24) Enable (0 = Disabled, 1 = Enabled) (25) Subtype (15 = AND, 16 = NAND, 17 = OR, 18 = NOR, 19 = XOR) (26) Source Alarm A (27) Source Alarm B (28) Source Alarm C (29) Source Alarm D (30) Digital Outputs to Associate - Standard (31-34) Digital Outputs to Associate - Options (Scout Only) (35) Datalogs to Trigger (Scout Only) (36) Waveform Capture to Trigger (Scout Only) | Alarm ID 201 = Logic Alarm 1... 210 = Logic alarm 10
| Enable Data Log | 8001 | C_ENABLE_DATA_LOG | Y |  | (1) Command Semaphore (2) File ID (3) Enable/Disable (0=Disable, 1=Enable)
| Setup Data Log | 8002 | C_SETUP_DATA LOG | Y |  | (1) Command Semaphore (2) File ID (3) Record Management Method (4) Topic List Reference (5) Start time (6) Stop time (7) Interval Control minutes (1,5,10,15,30,60,1440) (8) ID Item 1 (9) ID Item 2 (10) ID Item 3 (11) ID Item 4 (12) ID Item 5 (13) ID Item 6 (14) ID Item 7 (15) ID Item 8 (16) ID Item 9 (17) ID Item 10 (18) ID Item 11 (19) ID Item 12 (20) ID Item 13 (21) ID Item 14
| Clear Data Log | 8003 | C_CLEAR_DATA_LOG | Y |  | (1) Command Semaphore (2) File ID
DIAGNOSTICS (9000-9999) |  |  |  | Y | Y
| Reset Diagnostic Log | 9000 | C_RESET_DIA_ERROR_LOG | Y |  | (1) Command Semaphore |  | Y

## Data Types
Data Type | Description | Native Range | N/A Value | Notes
UTF8 | Alphanumeric | 0-3 bytes | 0x00
INT16 | Signed Integer, 16 bits | -32,768 - 32,767 | 0x8000
INT16U | Unsigned Integer, 16 bits | 0 - 65,535 | 0xFFFF
INT32 | Signed Integer, 32 bits | -2,147,483,648 – 2,147,483,647 | 0x80000000
INT32U | Unsigned Integer, 32 bits | 0 - 4,294,967,295 | 0xFFFFFFFF
INT64 | Signed Integer, 64 bits |  | 0x8000000000000000
FLOAT32 | Floating Point, 32 bits | +/- 1*10^38 | 0xFFC00000
FLOAT64 | Floating Point, 64 bits | +/-1.798*10^308 | 0xFFF8000000000000
BITMAP |  |  | 0x8000 Example for a status bitmap 1 register long. | For status bitmaps that are multiple registers long, the most significant bit will be set to indicate the entire bitmap is N/A.This does not apply to configuration bitmaps. So, in setup commands that include a bitmap as a parameter, the user must always include the desired value for these bitmaps.
DATETIME | DateTime | 1/1/2000 – 12/31/2127 | 0xFFFFFFFFFFFFFFFF | DateTime coding format using 4 words as per IEC 870-5-4 Word 1 b0-b6: Year (0 - 127) b7-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved Word 3 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 4 b0-b15: Millisecond (0 - 59999)
DATE | Date |  | 0xFFFFFFFF | Word 1 b0-b7: Year (0 - 99) b8-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved
TIME | Time |  | 0xFFFFFFFF | Word 1 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 2 b0-b15: Millisecond (0 - 59999)
PORTAL | A portal provides a means to access data of a size up to 125 registers by doing a Modbus block read of a single register. This allows large data sets to be accessed without using a large number of registers. An example might be a data type of PORTAL100 located at register 1000. In order to read the 100 registers, the user would do a block read of 100 registers beginning at register 1000. The data at PORTAL100 could be stored in an internal format and presented to the user by the meter communications firmware as 100 16 bit quantities.
4Q FP PF | Four Quadrant Floating Point Power Factor | -2 - 2 | 0xFFC00000 | Power factor values are specially encoded floating point values. Angle of complex power = power factor register value 0° = 1 90° = 0 180° = -1 270° = 2 Q1: 0 < x < 1 Q2: -2 < x < -1 Q3: -1 < x < 0 Q4: 1 < x < 2 Pseudo code to decode PF Value if (rigVal > 1) { PF_Val = 2 - regVal; PF is leading } else if (regVal < -1) { PF_Val = -2-regVal PF is leading } else if ( abs(regVal) equals 1 ) { PF_Val = regVal PF is at unity } else { PF_Val = regVal PF is lagging }

## Alarm Attributes
Alarm Attributes
| type |  | subtype |  | parameter |  | modifier |  | phases |  | level |  | priority |  | setpoints |  | learning |  | enable
| Bits 28-31 |  | Bits 23-27 |  | Bits 17-22 |  | Bits 11-16 |  | Bits 07-10 |  | Bits 05-06 |  | Bits 03-04 |  | Bit 02 |  | Bit 01 |  | Bit 00
0 | NONE | 0 | NONE | 0 | NONE | 0 | NONE | 0 | NONE | 0 | LEVEL0 | 0 | NONE | 0 | FIXED | 0 | NOT_LEARNING | 0 | DISABLED
1 | STANDARD1S | 1 | OVER SIGNED | 1 | VOLTAGE | 1 | 1 | 1 | A | 1 | LEVEL1 | 1 | HIGH | 1 | VARIABLE | 1 | LEARNING | 1 | ENABLED
2 | CUSTOM1S | 2 | UNDER SIGNED | 2 | CURRENT | 2 | 2 | 2 | B | 2 | LEVEL2 | 2 | MEDIUM
3 | STANDARDHS | 3 | LEADING | 3 | ACTIVE_POWER | 3 | 3 | 3 | C | 3 | LEVEL3 | 3 | LOW
4 | CUSTOMHS | 4 | LAGGING | 4 | REACTIVE_POWER | 4 | 4 | 4 | AB
5 | DISTURBANCE | 5 | PHASELOSS | 5 | APPARENT_POWER | 5 | 5 | 5 | BC
6 | TRANSIENT | 6 | PHASEREV | 6 | FREQUENCY | 6 | 6 | 6 | CA
7 | WAVESHAPE | 7 | REVPOWER | 7 | POWER_FACTOR | 7 | 7 | 7 | ABC
8 | UNARY | 8 | POWERUP | 8 | STANDARD | 8 | 8 | 8 | N
9 | DIGITAL | 9 | RESET | 9 | OPTION_SLOT_A | 9 | 9 | 9 | G
A | BINARY | A | DIAGNOSTIC | A | OPTION_SLOT_B | A | 10 | A | NG
B | TIME_OF_DAY | B | OFF2ON | B | OPTION_SLOT_C | B | 11 | B | 3PHASE_TOTAL
C | LOGIC | C | ON2OFF | C | OPTION_SLOT_D | C | 12 | C | NOT_USED
D |  | D | SWELL | D | SELF_TEST | D | 13 | D | NOT_USED
E |  | E | SAG | E | HARMONIC | E | 14 | E | NOT_USED
F |  | F | AND | F | INTERHARMONIC | F | 15 | F | NOT_USED
|  | 10 | NAND | 10 | K_FACTOR | 10 | 16
|  | 11 | OR | 11 | FLICKER | 11 | PHASE
|  | 12 | NOR | 12 | ENERGY | 12 | NEUTRAL
|  | 13 | XOR | 13 | DATETIME | 13 | GROUND
|  | 14 | NOT | 14 | TEMPERATURE | 14 | LN
|  | 15 | OVER ABSOLUTE | 15 | INPUT_METERING_1 | 15 | LL
|  | 16 | UNDER ABSOLUTE | 16 | INPUT_METERING_2 | 16 | THD
|  | 17 |  | 17 | INPUT_METERING_3 | 17 | UNBALANCE
|  | 18 |  | 18 | INPUT_METERING_4 | 18 | TRUE
|  | 19 |  | 19 | INPUT_METERING_5 | 19 | DISPLACEMENT
|  | 1A |  | 1A | INPUT_METERING_6 | 1A | DEMAND_LAST
|  | 1B |  | 1B | INPUT_METERING_7 | 1B | DEMAND_PREDICTED
|  | 1C |  | 1C | INPUT_METERING_8 | 1C | DEMAND_PRESENT
|  | 1D |  | 1D | INPUT_METERING_9 | 1D | RMS
|  | 1E |  | 1E | INPUT_METERING_10 | 1E | FUNDAMENTAL
|  | 1F | NOT_USED | 1F |  | 1F | ANGLE
|  |  |  | 20 |  | 20 | DEMAND_PEAK
|  |  |  | 21 |  | 21 | CREST_FACTOR
|  |  |  | 22 |  | 22 | DISTORTION
|  |  |  | 23 |  | 23 | INSTANTANEOUS
|  |  |  | 24 |  | 24 | SHORT_TERM
|  |  |  | 25 |  | 25 | LONG_TERM
|  |  |  | 26 |  | 26 | POSITIVE_SEQUENCE
|  |  |  | 27 |  | 27 | NEGATIVE_SEQUENCE
|  |  |  | 28 |  | 28 | ZERO_SEQUENCE
|  |  |  | 29 |  | 29 | TREND
|  |  |  | 2A |  | 2A | 3_PHASE
|  |  |  | 2B |  | 2B | ACCUMULATED
|  |  |  | 2C |  | 2C | CONDITIONAL
|  |  |  | 2D |  | 2D | INCREMENTAL
|  |  |  | 2E |  | 2E | TOU_RATE_1
|  |  |  | 2F |  | 2F | TOU_RATE_2
|  |  |  | 30 |  | 30 | TOU_RATE_3
|  |  |  | 31 |  | 31 | TOU_RATE_4
|  |  |  | 32 |  | 32
|  |  |  | 33 |  | 33
|  |  |  | 34 |  | 34
|  |  |  | 35 |  | 35
|  |  |  | 36 |  | 36
|  |  |  | 37 |  | 37
|  |  |  | 38 |  | 38
|  |  |  | 39 |  | 39
|  |  |  | 3A |  | 3A
|  |  |  | 3B |  | 3B
|  |  |  | 3C |  | 3C
|  |  |  | 3D | USER_DEFINED1 | 3D | USER_DEFINED1
|  |  |  | 3E | USER_DEFINED2 | 3E | USER_DEFINED2
|  |  |  | 3F | USER_DEFINED3 | 3F | USER_DEFINED3

## Units Codes
Code | Abbreviation | Description
0 |  | No Units
1 | % | Percentage
2 | °C | Degrees Celsius
3 | °F | Degrees Fahrenheit
4 | Deg | Degrees Angular
5 | Hz | Hertz
6 | A | amperes
7 | kA | Kilo Amperes
8 | V | Volts
9 | kV | Kilo Volts
10 | MV | Mega Volts
11 | W | Watts
12 | kW | Kilowatts
13 | MW | Megawatts
14 | VAR | Volt-Ampere Reactive
15 | kVAR | Kilo Volt-Ampere Reactive
16 | MVAR | Mega Volt-Ampere Reactive
17 | VA | Volt-Amperes
18 | kVA | Kilo Volt-Amperes
19 | MVA | Mega Volt-Amperes
20 | WH | Watt-Hour
21 | kWH | Kilowatt-Hour
22 | MWH | Megawatt-Hour
23 | VARH | Reactive Volt-Ampere Hour
24 | kVARH | Reactive Kilo Volt-Ampere Hour
25 | MVARH | Reactive Mega Volt-Ampere Hour
26 | VAH | Volt-Ampere Hours
27 | kVAH | Kilo Volt-Ampere Hours
28 | MVAH | Mega Volt-Ampere Hours
29 | Seconds | Seconds
30 | Minutes | Minutes
31 | Hours | Hours
32 | Bytes (RAM) | Bytes
33 | kBytes (RAM) | Kilobytes
34 | $ | Dollars
35 | gal | gallons
36 | gal/hr | gallons/hour
37 | gal/min | gallons/minute
38 | cfm | cubic feet/min
39 | PSI | PSI
40 | BTU | BTU
41 | L | liters
42 | ton-hours | ton-hours
43 | l/hr | liters/hour
44 | l/min | liters/min
45 | € | Euros
46 | ms | Milliseconds
47 | m³ | cubic-meters
48 | m³/sec | cubic-meters/sec
49 | m³/min | cubic-meters/min
50 | m³/hr | cubic-meters/hour
51 | Pa | pascals
52 | Bars | bar
53 | RPM | Revolutions/min
55 | BTU/hr | BTU/hour
56 | PSIG | Pounds/square inch gauge
57 | SCFM | Standard cubic feet/min
58 | MCF | Thousand cubic feet
59 | Therm | Therm
60 | SCFH | Standard cubic feet/hour
61 | PSIA | pounds/square inch absolute
62 | lbs | pounds
63 | kg | Kilogram
64 | klbs | Kilopounds
65 | lb/hr | pound/hour
66 | ton/hr | ton/hour
67 | kg/hr | Kilogram/hour
68 | in. Hg | inch of Mercury
69 | kPa | kiloPascals
70 | %RH | percentage of relative humidity
71 | MPH | miles per hour
72 | m/sec | meters/sec
73 | mV/cal/(cm²/min) | milliVolts/calorie/(square centimeters/min)
74 | in | inches
75 | mm | millimeter
76 | GWH | GigaWatt-Hour
77 | GVARH | Reactive Giga Volt-Ampere Hour
78 | GVAH | Giga Volt-Ampere Hours
79 | AH | Ampere-Hours
80 | kAH | Kiloamp-Hours
81 | Therm/hr | Therm/hour

## References
References
Y | Yes, data item is supported as standard feature
O | Yes, item is supported as an option
P | Data item is supported but is private
R | An R in the Access column means the register may be read.
W | A W in the Access column means the register may be written.
C | A C in the Access column means the register may only be written via a setup command.
ASCII Characters | 0 1 2 3 4 5 6 7 8 9 A B C D E F
0 NUL SOH STX ETX EOT ENQ ACK BEL BS HT LF VT FF CR SO SI
1 DLE DC1 DC2 DC3 DC4 NAK SYN ETB CAN EM SUB ESC FS GS RS US
2 SP ! " # $ % & ' ( ) * + , – . /
3 0 1 2 3 4 5 6 7 8 9 : ; < = > ?
4 @ A B C D E F G H I J K L M N O
5 P Q R S T U V W X Y Z [ \ ] ^ _
6 ` a b c d e f g h i j k l m n o
7 p q r s t u v w x y z { ¦ } ~ DEL
Abbreviations | PRODUCTION_HISTORY - PROD_HIST
APPLIED – APLY
READING – READ
SHIFT – SFT
PRESENT – PRES
PREVIOUS – PREV
DURATION – DUR
NOMINAL – NOM
PRIMARY – PRI
SECONDARY – SEC
WIRECORRECT – SWC
FIELD_CAL_CT_RATIO_PH_A - FLD_CAL_CT_A
FIELD_CAL_VT_RATIO_PH_A - FLD_CAL_VT_A
R_METER_SETUP_ENERGY_OUT_PW01 - R_METER_SETUP_ENERGY_ PW01
R_METER_SETUP_ENERGY_OUT_DIGOUT_01 - R_METER_SETUP_ENERGY_DO_01
RS485 – 485
DIAG – DIA
DIAGNOSTIC – DIA
BEHAVIORAL – BEH
REGISTER – REG
OVER – OVR
UNDER – UND
CURRENT – CUR
VOLTAGE – VOLT
LEVEL – LVL
TYPE – TYP
ENABLE_PRI – EP
VOLT_LL – VLL
VOLT_LN – VLN
DATALOG – DLG
LEADING_PF_TRUE – LEDPFT
LAGGING_PF_TRUE – LAGPGT
LEADING_PF_DISP – LEDPFD
LAGGING_PF_DISP – LAGPGD
DEMAND – DEM
1S_STD – 1ST
TYPE_LEVEL – TL
UNBALANCE – UNB
ENERGY_ACCUM – ENG_ACC
ENERGY – ENG
INTERVAL - INT
Passwords shall be 4 alphanumeric characters long.
Passwords shall always be entered and setup left-to-right.
Characters shall be selected from the following subset of US ASCII printable characters:
Character Decimal Description
# 35 NUMBER SIGN
$ 36 DOLLAR SIGN
% 37 PERCENT SIGN
& 38 AMPERSAND
* 42 ASTERISK
+ 43 PLUS SIGN
- 45 MINUS SIGN
/ 47 SLASH
0 48 DIGIT ZERO
1 49 DIGIT ONE
2 50 DIGIT TWO
3 51 DIGIT THREE
4 52 DIGIT FOUR
5 53 DIGIT FIVE
6 54 DIGIT SIX
7 55 DIGIT SEVEN
8 56 DIGIT EIGHT
9 57 DIGIT NINE
? 63 QUESTION MARK
@ 64 COMMERCIAL AT SIGN
A 65 CAPITAL LETTER A
B 66 CAPITAL LETTER B
C 67 CAPITAL LETTER C
D 68 CAPITAL LETTER D
E 69 CAPITAL LETTER E
F 70 CAPITAL LETTER F
G 71 CAPITAL LETTER G
H 72 CAPITAL LETTER H
I 73 CAPITAL LETTER I
J 74 CAPITAL LETTER J
K 75 CAPITAL LETTER K
L 76 CAPITAL LETTER L
M 77 CAPITAL LETTER M
N 78 CAPITAL LETTER N
O 79 CAPITAL LETTER O
P 80 CAPITAL LETTER P
Q 81 CAPITAL LETTER Q
R 82 CAPITAL LETTER R
S 83 CAPITAL LETTER S
T 84 CAPITAL LETTER T
U 85 CAPITAL LETTER U
V 86 CAPITAL LETTER V
W 87 CAPITAL LETTER W
X 88 CAPITAL LETTER X
Y 89 CAPITAL LETTER Y
Z 90 CAPITAL LETTER Z
a 97 SMALL LETTER a
b 98 SMALL LETTER b
c 99 SMALL LETTER c
d 100 SMALL LETTER d
e 101 SMALL LETTER e
f 102 SMALL LETTER f
g 103 SMALL LETTER g
h 104 SMALL LETTER h
i 105 SMALL LETTER i
j 106 SMALL LETTER j
k 107 SMALL LETTER k
l 108 SMALL LETTER l
m 109 SMALL LETTER m
n 110 SMALL LETTER n
o 111 SMALL LETTER o
p 112 SMALL LETTER p
q 113 SMALL LETTER q
r 114 SMALL LETTER r
s 115 SMALL LETTER s
t 116 SMALL LETTER t
u 117 SMALL LETTER u
v 118 SMALL LETTER v
w 119 SMALL LETTER w
x 120 SMALL LETTER x
y 121 SMALL LETTER y
z 122 SMALL LETTER z