| Aspect | AIS | GIS |
| --- | --- | --- |
| Design standards | IEC (e.g. IEC 62271-1, IEC 62271-200, IEC 62271-100 …etc) | IEC (e.g. IEC 62271-1, IEC 62271-200, IEC 62271-100 …etc) |
| Media used for “Busbar” insulation | Air | SF6 |
| Media used for “Switching” | Air, Oil, SF6 or Vacuum | SF6 or Vacuum |
| Dimensions/physical size/footprint | Relatively larger, as clearances are in “Air”, thus some safe clearances must be maintained to satisfy the dielectric performance. | Relatively smaller (some times combining more than one function in one gas tank thus considerably reducing overall line-up dimensions/footprint) |
| Sensitivity to environment/pollution | Moderate, pollution & humidity can have some effects on insulation that is exposed in air | Excellent, gas tank usually with high ingress protection (e.g. IP67) with very little sensitivity to environment, humidity, even altitude |
| Maintenance requirement | Moderate | Minimal, because the busbars & switching units are both completely sealed thus limiting the need for insulation cleaning & need for user intervention. |
| Need for gas pressure monitoring | Might be required only for switching devices incorporating SF6 gas | Might be required only for both busbars & switching devices incorporating SF6 gas |
| Modularity/Extension | Modular by nature of its design, future function units can be generally added via simple extension process without specific limitations. In other words, AIS offers more flexibility toward extension & upgrades | Modularity depend on the design of the range, future extension shall be taken into consideration at early stages, adding of future function units can be realized with some limitation regarding the number of extensions. |
| Type of execution with switching devices | Fixed or draw-out according to design | Fixed |
| Cable termination requirements | No specific requirements, normal cable termination types can be used | Specific cable terminations required to maintain proper insulation with reduced air clearances in cable connection compartment |