## Sheet1
Device type: VAMP 255 |  |  | Motor mode
Program version: V10.108
Note: Data lists are customizable.
Possible data items for each category of data is listed below the default mappings.
IEC-101
Single Point Information
Idx | GI | Event | Item
2 | 0 | 0 | DI1
3 | 0 | 0 | DI2
4 | 0 | 0 | DI3
5 | 0 | 0 | DI4
6 | 0 | 0 | DI5
7 | 0 | 0 | DI6
8 | 0 | 0 | ARena
9 | 0 | 0 | ARLck
10 | 0 | 0 | ARReq1
11 | 0 | 0 | ARReq2
12 | 0 | 0 | ARReq3
13 | 0 | 0 | ARReq4
14 | 0 | 0 | ARReq5
15 | 0 | 0 | ARShot1
16 | 0 | 0 | ARShot2
17 | 0 | 0 | ARShot3
18 | 0 | 0 | ARShot4
19 | 0 | 0 | ARShot5
20 | 0 | 0 | ARCr
21 | 0 | 0 | I>s
22 | 0 | 0 | I>>s
23 | 0 | 0 | I>>>s
24 | 0 | 0 | I>t
25 | 0 | 0 | I>>t
26 | 0 | 0 | I>>>t
27 | 0 | 0 | I2>s
28 | 0 | 0 | I2>t
29 | 0 | 0 | T>s
30 | 0 | 0 | T>t
31 | 0 | 0 | IoInt>s
32 | 0 | 0 | IoInt>t
33 | 0 | 0 | Io>s
34 | 0 | 0 | Io>>s
35 | 0 | 0 | Io>t
36 | 0 | 0 | Io>>t
37 | 0 | 0 | Io>>>s
38 | 0 | 0 | Io>>>>s
39 | 0 | 0 | Io>>>t
40 | 0 | 0 | Io>>>>t
41 | 0 | 0 | Uo>s
42 | 0 | 0 | Uo>>s
43 | 0 | 0 | Uo>t
44 | 0 | 0 | Uo>>t
45 | 0 | 0 | IoD>s
46 | 0 | 0 | IoD>>s
47 | 0 | 0 | IoD>t
48 | 0 | 0 | IoD>>t
49 | 0 | 0 | CBFPs
50 | 0 | 0 | CBFPt
51 | 0 | 0 | FltL1
52 | 0 | 0 | FltL2
53 | 0 | 0 | FltL3
54 | 0 | 0 | P<s
55 | 0 | 0 | P<<s
56 | 0 | 0 | P<t
57 | 0 | 0 | P<<t
58 | 0 | 0 | df/dt_s
59 | 0 | 0 | df/dt_t
60 | 0 | 0 | U1<s
61 | 0 | 0 | U1<<s
62 | 0 | 0 | U1<t
63 | 0 | 0 | U1<<t
64 | 0 | 0 | Z<s
65 | 0 | 0 | Z<<s
Possible data items:
DI1
DI2
DI3
DI4
DI5
DI6
DI7
DI8
DI9
DI10
DI11
DI12
DI13
DI14
DI15
DI16
DI17
DI18
ARena
ARLck
ARReq1
ARReq2
ARReq3
ARReq4
ARReq5
ARShot1
ARShot2
ARShot3
ARShot4
ARShot5
ARCr
I>s
I>>s
I>>>s
I>t
I>>t
I>>>t
I2>s
I2>t
T>s
T>t
If2>s
If2>t
Io>s
Io>>s
Io>t
Io>>t
Io>>>s
Io>>>>s
Io>>>t
Io>>>>t
Uo>s
Uo>>s
Uo>t
Uo>>t
Iφ>s
Iφ>>s
Iφ>>>s
Iφ>>>>s
Iφ>t
Iφ>>t
Iφ>>>t
Iφ>>>>t
IoD>s
IoD>>s
IoD>t
IoD>>t
U>s
U>>s
U>>>s
U>t
U>>t
U>>>t
U<s
U<<s
U<<<s
U<t
U<<t
U<<<t
fXs
fXXs
fXt
fXXt
f<s
f<<s
f<t
f<<t
CBFPs
CBFPt
FltL1
FltL2
FltL3
P<s
P<<s
P<t
P<<t
df/dt_s
df/dt_t
U1<s
U1<<s
U1<t
U1<<t
Z<s
Z<<s
Z<t
Z<<t
X<s
X<<s
X<t
X<<t
Uof3<s
Uof3<t
Uf>s
Uf>t
Q<s
Q<t
dI>t
dI>>t
I'>s
I'>>s
I'>t
I'>>t
I'2>s
I'2>t
Ist>s
Ist>t
I<s
I<t
I2>>s
I2>>t
DI19
DI20
DI21
DI22
DI23
DI24
DI25
DI26
DI27
DI28
DI29
DI30
DI31
DI32
Z1<s
Z1<t
Z2<s
Z2<t
Z3<s
Z3<t
Z4<s
Z4<t
Z5<s
Z5<t
Z1e<s
Z1e<t
Z2e<s
Z2e<t
Z3e<s
Z3e<t
Z4e<s
Z4e<t
Z5e<s
Z5e<t
IoInt>s
IoInt>t
ExtDI1
ExtDI2
ExtDI3
ExtDI4
ExtDI5
ExtDI6
ExtDI7
ExtDI8
ExtDI9
ExtDI10
ExtDI11
ExtDI12
ExtDI13
ExtDI14
ExtDI15
ExtDI16
ExtDI17
ExtDI18
Logic1
Logic2
Logic3
Logic4
Logic5
Logic6
Logic7
Logic8
Logic9
Logic10
Logic11
Logic12
Logic13
Logic14
Logic15
Logic16
Logic17
Logic18
Logic19
Logic20
SGrp1
SGrp2
CTSV_alarm
VTSV_alarm
R/L
VI1
VI2
VI3
VI4
Prg1s
Prg1t
Prg2s
Prg2t
Prg3s
Prg3t
Prg4s
Prg4t
Prg5s
Prg5t
Prg6s
Prg6t
Prg7s
Prg7t
Prg8s
Prg8t
87Ls
87Lt
ArcStg1
ArcStg2
ArcStg3
ArcStg4
ArcStg5
ArcStg6
ArcStg7
ArcStg8
Double Point Information
Idx | GI | Event | Item
4097 | 0 | 0 | Obj1
4098 | 0 | 0 | Obj2
4099 | 0 | 0 | Obj3
4100 | 0 | 0 | Obj4
4101 | 0 | 0 | Obj5
4102 | 0 | 0 | Obj6
4103 | 0 | 0 | Obj7
4104 | 0 | 0 | Obj8
Possible data items:
Obj1
Obj2
Obj3
Obj4
Obj5
Obj6
Obj7
Obj8
Analog Inputs
Idx | GI | Event | Item
16385 | 0 | 0 | IL1
16386 | 0 | 0 | IL2
16387 | 0 | 0 | IL3
16388 | 0 | 0 | UL1
16389 | 0 | 0 | UL2
16390 | 0 | 0 | UL3
16391 | 0 | 0 | U12
16392 | 0 | 0 | U23
16393 | 0 | 0 | U31
16394 | 0 | 0 | Io1
16395 | 0 | 0 | Io2
16396 | 0 | 0 | IoCalc
16397 | 0 | 0 | Uo
16398 | 0 | 0 | P
16399 | 0 | 0 | Q
16400 | 0 | 0 | S
16401 | 0 | 0 | P.F.
16402 | 0 | 0 | CosPhi
16403 | 0 | 0 | f
Possible data items:
IL1
IL2
IL3
UL1
UL2
UL3
U12
U23
U31
Io1
Io2
IoCalc
Uo
P
Q
S
P.F.
CosPhi
f
IL1RMS
IL2RMS
IL3RMS
Prms
Qrms
Srms
IL1da
IL2da
IL3da
Pda
Qda
Sda
PFda
CosPhida
fda
Prmsda
Qrmsda
Srmsda
THDIL
THDIL1
THDIL2
THDIL3
THDU
THDUa
THDUb
THDUc
I'L1
I'L2
I'L3
I'oCalc
dIL1
dIL2
dIL3
I'L1RMS
I'L2RMS
I'L3RMS
I'L1da
I'L2da
I'L3da
THDI'L
THDI'L1
THDI'L2
THDI'L3
AI1
AI2
AI3
AI4
AI5
AI6
AI7
AI8
AI9
AI10
AI11
AI12
AI13
AI14
AI15
AI16
Z12primary
Z23primary
Z31primary
Z12sec.
Z23sec.
Z31sec.
Z12angle
Z23angle
Z31angle
I>Value
I>>Value
I>>>Value
I_HV_Side
TRTD
Z1Gprimary
Z2Gprimary
Z3Gprimary
Z1Gsec.
Z2Gsec.
Z3Gsec.
Z1Gangle
Z2Gangle
Z3Gangle
PS1Value
PS2Value
PS3Value
PS4Value
PS5Value
PS6Value
PS7Value
PS8Value
PL1
PL2
PL3
QL1
QL2
QL3
SL1
SL2
SL3
cosL1
cosL2
cosL3
I1
I2
I2/I1
Iseq
U1
U2
U2/U1
Useq
U1SagSwell
U2SagSwell
U3SagSwell
Io1rms
Io2rms
IoRMSpeak
IoRMSfund
IoRMSrms
IoRMS/fund
Analog Events
Idx | Event | Item
18433 | 0 | I>Value
18434 | 0 | I>>Value
18435 | 0 | I>>>Value
18436 | 0 | XFlt
18437 | 0 | IFltLast
18438 | 0 | PS1Value
18439 | 0 | PS2Value
18440 | 0 | PS3Value
18441 | 0 | PS4Value
18442 | 0 | PS5Value
18443 | 0 | PS6Value
18444 | 0 | PS7Value
18445 | 0 | PS8Value
Possible data items:
I>Value
I>>Value
I>>>Value
XFlt
IFltLast
PS1Value
PS2Value
PS3Value
PS4Value
PS5Value
PS6Value
PS7Value
PS8Value
IoRMSpeak
IoRMSfund
IoRMSrms
IoRMS/fund
Integrated Totals
Idx | GI | Item
20481 | 0 | E+
20482 | 0 | E-
20483 | 0 | Eq+
20484 | 0 | Eq-
20485 | 0 | Starts
20486 | 0 | Fail
20487 | 0 | Shot1
20488 | 0 | Shot2
20489 | 0 | Shot3
20490 | 0 | Shot4
20491 | 0 | Shot5
Possible data items:
E+
E-
Eq+
Eq-
DI1
DI2
DI3
DI4
DI5
DI6
DI7
DI8
DI9
DI10
DI11
DI12
DI13
DI14
DI15
DI16
DI17
DI18
DI19
DI20
DI21
DI22
DI23
DI24
DI25
DI26
DI27
DI28
DI29
DI30
DI31
DI32
Starts
Fail
Shot1
Shot2
Shot3
Shot4
Shot5
SBO
Idx | Item
34817 | Obj1
34818 | Obj2
34819 | Obj3
34820 | Obj4
34821 | Obj5
34822 | Obj6
Possible data items:
Obj1
Obj2
Obj3
Obj4
Obj5
Obj6
DO
Idx | Item
32769 | Latch
32770 | ARena
32771 | A1
32772 | A2
32773 | A3
32774 | A4
32775 | A5
32776 | SGrp1
32777 | SGrp2
32778 | R/L
32779 | VI1
32780 | VI2
32781 | VI3
32782 | VI4
Possible data items:
Latch
ARena
A1
A2
A3
A4
A5
SGrp1
SGrp2
R/L
VI1
VI2
VI3
VI4
Obj1
Obj2
Obj3
Obj4
Obj5
Obj6