## PM5500_LE
PM5500_LE Series Translator Details
Data Recorder | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | ModbusAddr | Format | RequestType | IONHandle | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | 400090 | UINT16 | R | 4864 |  |  |  |  | 1
|  | Factory Information | Factory 1 | FAC1 Compliance |  |  |  |  | 4865
|  | Factory Information | Factory 1 | FAC1 Options |  |  |  |  | 4866
|  | Factory Information | Factory 1 | FAC1 Revision | FAC1 Revision | 401637 | UINT16 | R | 4867
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | 400130 | UINT32 | R | 4868 |  |  |  |  | 2
|  | Factory Information | Factory 1 | FAC1 ION Version |  |  |  |  | 30510
|  | Factory Information | Factory 1 | FAC1 Template |  |  |  |  | 4989
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | 400030 | ASCII | R | 22340 |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 Manuf Date Time | FAC1 Manuf Date Time | 400132 | DateTime3_IEC870_UTC | R | 30129
|  | Factory Information | Factory 1 | FAC1 Hardware Revision | FAC1 Hardware Revision | 400136 | ASCII | R | 30130 |  |  |  |  | 5
|  | Factory Information | Factory 1 | FAC1 FW Rev RS | FAC1 FW Rev RS | 401669 | UINT16 | R | 30131
|  | Alarm - Summary | Alarm Counters | High Priority Counter | High Priority Counter | 413522 | UINT16 | R | 160432388
|  | Alarm - Summary | Alarm Counters | Low Priority Counter | Low Priority Counter | 413520 | UINT16 | R | 160432386
|  | Alarm - Summary | Alarm Counters | Medium Priority Counter | Medium Priority Counter | 413521 | UINT16 | R | 160432387
|  | Alarm - Summary | Alarm Counters | Total Alarms Counter | Total Alarms Counter | 413519 | UINT16 | R | 160432385
|  | Alarm - Summary | Alarm Status | Alarm Active | Alarm Active | 411010 | MaskedBool | R | 160432129 | 0x0001
|  | Alarm - Summary | Alarm Status | High Priority Active | High Priority Active | 411010 | MaskedBool | R | 160432130 | 0x0002
|  | Alarm - Summary | Alarm Status | Low Priority Active | Low Priority Active | 411010 | MaskedBool | R | 160432132 | 0x0008
|  | Alarm - Summary | Alarm Status | Medium Priority Active | Medium Priority Active | 411010 | MaskedBool | R | 160432131 | 0x0004
|  | Alarm - Summary | Alarm Status | Priority None Active | Priority None Active | 411010 | MaskedBool | R | 160432133 | 0x0010
|  | Alarms - Over Under | Over Active Power | Over Active Power Alarm | Over Active Power Alarm | 411059 | MaskedBool | R | 209719297 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Ack Status | Over Active Power-Ack Status | 411078 | MaskedBool | R | 209719298 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Count | Over Active Power-Alarm Count | 413531 | UINT16 | R | 209719306
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Enabled | Over Active Power-Alarm Enabled | 411040 | MaskedBool | R | 209719299 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Output |  |  |  |  | 209719305
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Priority |  |  |  |  | 209719300
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Delay |  |  |  |  | 209719304
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Setpoint |  |  |  |  | 209719303
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Delay |  |  |  |  | 209719302
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Setpoint |  |  |  |  | 209719301
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power Alarm | Over Apparent Power Alarm | 411059 | MaskedBool | R | 209717249 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Ack Status | Over Apparent Power-Ack Status | 411078 | MaskedBool | R | 209717250 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Count | Over Apparent Power-Alarm Count | 413533 | UINT16 | R | 209717258
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Enabled | Over Apparent Power-Alarm Enabled | 411040 | MaskedBool | R | 209717251 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Output |  |  |  |  | 209717257
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Priority |  |  |  |  | 209717252
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Delay |  |  |  |  | 209717256
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Setpoint |  |  |  |  | 209717255
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Delay |  |  |  |  | 209717254
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Setpoint |  |  |  |  | 209717253
|  | Alarms - Over Under | Over Current Earth | Over Current Earth Alarm | Over Current Earth Alarm | 411059 | MaskedBool | R | 209716225 | 0x0008
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Ack Status | Over Current Earth-Ack Status | 411078 | MaskedBool | R | 209716226 | 0x0008
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Alarm Count | Over Current Earth-Alarm Count | 413526 | UINT16 | R | 209716234
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Alarm Enabled | Over Current Earth-Alarm Enabled | 411040 | MaskedBool | R | 209716227 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Alarm Output |  |  |  |  | 209716233
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Alarm Priority |  |  |  |  | 209716228
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Dropout Delay |  |  |  |  | 209716232
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Dropout Setpoint |  |  |  |  | 209716231
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Pickup Delay |  |  |  |  | 209716230
|  | Alarms - Over Under | Over Current Earth | Over Current Earth-Pickup Setpoint |  |  |  |  | 209716229
|  | Alarms - Over Under | Over Current N | Over Current Neutral Alarm | Over Current Neutral Alarm | 411059 | MaskedBool | R | 209716481 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Ack Status | Over Current Neutral-Ack Status | 411078 | MaskedBool | R | 209716482 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Count | Over Current Neutral-Alarm Count | 413525 | UINT16 | R | 209716490
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Enabled | Over Current Neutral-Alarm Enabled | 411040 | MaskedBool | R | 209716483 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Output |  |  |  |  | 209716489
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Priority |  |  |  |  | 209716484
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Delay |  |  |  |  | 209716488
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Setpoint |  |  |  |  | 209716487
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Delay |  |  |  |  | 209716486
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Setpoint |  |  |  |  | 209716485
|  | Alarms - Over Under | Over Current Phase | Over Current Phase Alarm | Over Current Phase Alarm | 411059 | MaskedBool | R | 209716737 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Ack Status | Over Current Phase-Ack Status | 411078 | MaskedBool | R | 209716738 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Count | Over Current Phase-Alarm Count | 413523 | UINT16 | R | 209716746
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Enabled | Over Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209716739 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Output |  |  |  |  | 209716745
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Priority |  |  |  |  | 209716740
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Delay |  |  |  |  | 209716744
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Setpoint |  |  |  |  | 209716743
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Delay |  |  |  |  | 209716742
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Setpoint |  |  |  |  | 209716741
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last Alarm | Over Demand Active Power Last Alarm | 411060 | MaskedBool | R | 209719553 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Ack Status | Over Demand Active Power Last-Ack Status | 411079 | MaskedBool | R | 209719554 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Count | Over Demand Active Power Last-Alarm Count | 413539 | UINT16 | R | 209719562
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Enabled | Over Demand Active Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209719555 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Output |  |  |  |  | 209719561
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Priority |  |  |  |  | 209719556
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Delay |  |  |  |  | 209719560
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Setpoint |  |  |  |  | 209719559
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Delay |  |  |  |  | 209719558
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Setpoint |  |  |  |  | 209719557
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted Alarm | Over Demand Active Power Predicted Alarm | 411060 | MaskedBool | R | 209719809 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Ack Status | Over Demand Active Power Predicted-Ack Status | 411079 | MaskedBool | R | 209719810 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Count | Over Demand Active Power Predicted-Alarm Count | 413540 | UINT16 | R | 209719818
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Enabled | Over Demand Active Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209719811 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Output |  |  |  |  | 209719817
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Priority |  |  |  |  | 209719812
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Delay |  |  |  |  | 209719816
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Setpoint |  |  |  |  | 209719815
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Delay |  |  |  |  | 209719814
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Setpoint |  |  |  |  | 209719813
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present Alarm | Over Demand Active Power Present Alarm | 411059 | MaskedBool | R | 209720065 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Ack Status | Over Demand Active Power Present-Ack Status | 411078 | MaskedBool | R | 209720066 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Count | Over Demand Active Power Present-Alarm Count | 413538 | UINT16 | R | 209720074
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Enabled | Over Demand Active Power Present-Alarm Enabled | 411040 | MaskedBool | R | 209720067 | 0x8000 | 32768 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Output |  |  |  |  | 209720073
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Priority |  |  |  |  | 209720068
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Delay |  |  |  |  | 209720072
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Setpoint |  |  |  |  | 209720071
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Delay |  |  |  |  | 209720070
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Setpoint |  |  |  |  | 209720069
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last Alarm | Over Demand Apparent Power Last Alarm | 411060 | MaskedBool | R | 209717505 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Ack Status | Over Demand Apparent Power Last-Ack Status | 411079 | MaskedBool | R | 209717506 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Count | Over Demand Apparent Power Last-Alarm Count | 413545 | UINT16 | R | 209717514
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Enabled | Over Demand Apparent Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209717507 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Output |  |  |  |  | 209717513
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Priority |  |  |  |  | 209717508
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Delay |  |  |  |  | 209717512
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Setpoint |  |  |  |  | 209717511
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Delay |  |  |  |  | 209717510
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Setpoint |  |  |  |  | 209717509
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted Alarm | Over Demand Apparent Power Predicted Alarm | 411060 | MaskedBool | R | 209717761 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Ack Status | Over Demand Apparent Power Predicted-Ack Status | 411079 | MaskedBool | R | 209717762 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Count | Over Demand Apparent Power Predicted-Alarm Count | 413546 | UINT16 | R | 209717770
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Enabled | Over Demand Apparent Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209717763 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Output |  |  |  |  | 209717769
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Priority |  |  |  |  | 209717764
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Delay |  |  |  |  | 209717768
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Setpoint |  |  |  |  | 209717767
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Delay |  |  |  |  | 209717766
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Setpoint |  |  |  |  | 209717765
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present Alarm | Over Demand Apparent Power Present Alarm | 411060 | MaskedBool | R | 209718017 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Ack Status | Over Demand Apparent Power Present-Ack Status | 411079 | MaskedBool | R | 209718018 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Count | Over Demand Apparent Power Present-Alarm Count | 413544 | UINT16 | R | 209718026
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Enabled | Over Demand Apparent Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209718019 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Output |  |  |  |  | 209718025
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Priority |  |  |  |  | 209718020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Delay |  |  |  |  | 209718024
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Setpoint |  |  |  |  | 209718023
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Delay |  |  |  |  | 209718022
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Setpoint |  |  |  |  | 209718021
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last Alarm | Over Demand Reactive Power Last Alarm | 411060 | MaskedBool | R | 209718529 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Ack Status | Over Demand Reactive Power Last-Ack Status | 411079 | MaskedBool | R | 209718530 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Count | Over Demand Reactive Power Last-Alarm Count | 413542 | UINT16 | R | 209718538
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Enabled | Over Demand Reactive Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209718531 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Output |  |  |  |  | 209718537
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Priority |  |  |  |  | 209718532
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Delay |  |  |  |  | 209718536
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Setpoint |  |  |  |  | 209718535
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Delay |  |  |  |  | 209718534
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Setpoint |  |  |  |  | 209718533
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted Alarm | Over Demand Reactive Power Predicted Alarm | 411060 | MaskedBool | R | 209718785 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Ack Status | Over Demand Reactive Power Predicted-Ack Status | 411079 | MaskedBool | R | 209718786 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Count | Over Demand Reactive Power Predicted-Alarm Count | 413543 | UINT16 | R | 209718794
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Enabled | Over Demand Reactive Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209718787 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Output |  |  |  |  | 209718793
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Priority |  |  |  |  | 209718788
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Delay |  |  |  |  | 209718792
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Setpoint |  |  |  |  | 209718791
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Delay |  |  |  |  | 209718790
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Setpoint |  |  |  |  | 209718789
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present Alarm | Over Demand Reactive Power Present Alarm | 411060 | MaskedBool | R | 209719041 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Ack Status | Over Demand Reactive Power Present-Ack Status | 411079 | MaskedBool | R | 209719042 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Count | Over Demand Reactive Power Present-Alarm Count | 413541 | UINT16 | R | 209719050
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Enabled | Over Demand Reactive Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209719043 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Output |  |  |  |  | 209719049
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Priority |  |  |  |  | 209719044
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Delay |  |  |  |  | 209719048
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Setpoint |  |  |  |  | 209719047
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Delay |  |  |  |  | 209719046
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Setpoint |  |  |  |  | 209719045
|  | Alarms - Over Under | Over Frequency | Over Frequency Alarm | Over Frequency Alarm | 411060 | MaskedBool | R | 209716993 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Ack Status | Over Frequency-Ack Status | 411079 | MaskedBool | R | 209716994 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Count | Over Frequency-Alarm Count | 413547 | UINT16 | R | 209717002
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Enabled | Over Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209716995 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Output |  |  |  |  | 209717001
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Priority |  |  |  |  | 209716996
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Delay |  |  |  |  | 209717000
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Setpoint |  |  |  |  | 209716999
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Delay |  |  |  |  | 209716998
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Setpoint |  |  |  |  | 209716997
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor Alarm | Lagging Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715201 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Ack Status | Lagging Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715202 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Count | Lagging Displacement Power Factor-Alarm Count | 413537 | UINT16 | R | 209715210
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Enabled | Lagging Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715203 | 0x4000 | 16384 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Output |  |  |  |  | 209715209
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Priority |  |  |  |  | 209715204
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Delay |  |  |  |  | 209715208
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Setpoint |  |  |  |  | 209715207
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Delay |  |  |  |  | 209715206
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Setpoint |  |  |  |  | 209715205
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor Alarm | Lagging Power Factor Alarm | 411059 | MaskedBool | R | 209715457 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Ack Status | Lagging Power Factor-Ack Status | 411078 | MaskedBool | R | 209715458 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Count | Lagging Power Factor-Alarm Count | 413535 | UINT16 | R | 209715466
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Enabled | Lagging Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715459 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Output |  |  |  |  | 209715465
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Priority |  |  |  |  | 209715460
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Delay |  |  |  |  | 209715464
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Setpoint |  |  |  |  | 209715463
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Delay |  |  |  |  | 209715462
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Setpoint |  |  |  |  | 209715461
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor Alarm | Leading Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715713 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Ack Status | Leading Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715714 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Count | Leading Displacement Power Factor-Alarm Count | 413536 | UINT16 | R | 209715722
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Enabled | Leading Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715715 | 0x2000 | 8192 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Output |  |  |  |  | 209715721
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Priority |  |  |  |  | 209715716
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Delay |  |  |  |  | 209715720
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Setpoint |  |  |  |  | 209715719
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Delay |  |  |  |  | 209715718
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Setpoint |  |  |  |  | 209715717
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor Alarm | Leading Power Factor Alarm | 411059 | MaskedBool | R | 209715970 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Ack Status | Leading Power Factor-Ack Status | 411078 | MaskedBool | R | 209715969 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Count | Leading Power Factor-Alarm Count | 413534 | UINT16 | R | 209715978
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Enabled | Leading Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715971 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Output |  |  |  |  | 209715977
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Priority |  |  |  |  | 209715972
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Delay |  |  |  |  | 209715976
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Setpoint |  |  |  |  | 209715975
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Delay |  |  |  |  | 209715974
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Setpoint |  |  |  |  | 209715973
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power Alarm | Over Reactive Power Alarm | 411059 | MaskedBool | R | 209718273 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Ack Status | Over Reactive Power-Ack Status | 411078 | MaskedBool | R | 209718274 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Count | Over Reactive Power-Alarm Count | 413532 | UINT16 | R | 209718282
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Enabled | Over Reactive Power-Alarm Enabled | 411040 | MaskedBool | R | 209718275 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Output |  |  |  |  | 209718281
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Priority |  |  |  |  | 209718276
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Delay |  |  |  |  | 209718280
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Setpoint |  |  |  |  | 209718279
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Delay |  |  |  |  | 209718278
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Setpoint |  |  |  |  | 209718277
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage Alarm | Over THD Voltage Alarm | 411060 | MaskedBool | R | 209720833 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Ack Status | Over THD Voltage-Ack Status | 411079 | MaskedBool | R | 209720834 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Count | Over THD Voltage-Alarm Count | 413550 | UINT16 | R | 209720842
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Enabled | Over THD Voltage-Alarm Enabled | 411041 | MaskedBool | R | 209720835 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Output |  |  |  |  | 209720841
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Priority |  |  |  |  | 209720836
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Delay |  |  |  |  | 209720840
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Setpoint |  |  |  |  | 209720839
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Delay |  |  |  |  | 209720838
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Setpoint |  |  |  |  | 209720837
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L Alarm | Over Voltage L-L Alarm | 411059 | MaskedBool | R | 209720321 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Ack Status | Over Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209720322 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Count | Over Voltage L-L-Alarm Count | 413527 | UINT16 | R | 209720330
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Enabled | Over Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209720323 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Output |  |  |  |  | 209720329
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Priority |  |  |  |  | 209720324
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Delay |  |  |  |  | 209720328
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Setpoint |  |  |  |  | 209720327
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Delay |  |  |  |  | 209720326
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Setpoint |  |  |  |  | 209720325
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N Alarm | Over Voltage L-N Alarm | 411059 | MaskedBool | R | 209720577 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Ack Status | Over Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209720578 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Count | Over Voltage L-N-Alarm Count | 413529 | UINT16 | R | 209720586
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Enabled | Over Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209720579 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Output |  |  |  |  | 209720585
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Priority |  |  |  |  | 209720580
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Delay |  |  |  |  | 209720584
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Setpoint |  |  |  |  | 209720583
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Delay |  |  |  |  | 209720582
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Setpoint |  |  |  |  | 209720581
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance Alarm | Voltage Unbalance Alarm | 411060 | MaskedBool | R | 209721089 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Ack Status | Voltage Unbalance-Ack Status | 411079 | MaskedBool | R | 209721090 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Count | Voltage Unbalance-Alarm Count | 413549 | UINT16 | R | 209721098
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Enabled | Voltage Unbalance-Alarm Enabled | 411041 | MaskedBool | R | 209721091 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Output |  |  |  |  | 209721097
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Priority |  |  |  |  | 209721092
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Delay |  |  |  |  | 209721096
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Setpoint |  |  |  |  | 209721095
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Delay |  |  |  |  | 209721094
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Setpoint |  |  |  |  | 209721093
|  | Alarms - Over Under | Phase Loss | Phase Loss Alarm | Phase Loss Alarm | 411060 | MaskedBool | R | 209721345 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Ack Status | Phase Loss-Ack Status | 411079 | MaskedBool | R | 209721346 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Count | Phase Loss-Alarm Count | 413551 | UINT16 | R | 209721354
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Enabled | Phase Loss-Alarm Enabled | 411041 | MaskedBool | R | 209721347 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Output |  |  |  |  | 209721353
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Priority |  |  |  |  | 209721348
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Delay |  |  |  |  | 209721352
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Setpoint |  |  |  |  | 209721351
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Delay |  |  |  |  | 209721350
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Setpoint |  |  |  |  | 209721349
|  | Alarms - Over Under | Under Current Phase | Under Current Phase Alarm | Under Current Phase Alarm | 411059 | MaskedBool | R | 209721601 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Ack Status | Under Current Phase-Ack Status | 411078 | MaskedBool | R | 209721602 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Count | Under Current Phase-Alarm Count | 413524 | UINT16 | R | 209721610
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Enabled | Under Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209721603 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Output |  |  |  |  | 209721609
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Priority |  |  |  |  | 209721604
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Delay |  |  |  |  | 209721608
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Setpoint |  |  |  |  | 209721607
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Delay |  |  |  |  | 209721606
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Setpoint |  |  |  |  | 209721605
|  | Alarms - Over Under | Under Frequency | Under Frequency Alarm | Under Frequency Alarm | 411060 | MaskedBool | R | 209721857 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Ack Status | Under Frequency-Ack Status | 411079 | MaskedBool | R | 209721858 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Count | Under Frequency-Alarm Count | 413548 | UINT16 | R | 209721866
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Enabled | Under Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209721859 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Output |  |  |  |  | 209721865
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Priority |  |  |  |  | 209721860
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Delay |  |  |  |  | 209721864
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Setpoint |  |  |  |  | 209721863
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Delay |  |  |  |  | 209721862
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Setpoint |  |  |  |  | 209721861
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L Alarm | Under Voltage L-L Alarm | 411059 | MaskedBool | R | 209722113 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Ack Status | Under Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209722114 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Count | Under Voltage L-L-Alarm Count | 413528 | UINT16 | R | 209722122
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Enabled | Under Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209722115 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Output |  |  |  |  | 209722121
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Priority |  |  |  |  | 209722116
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Delay |  |  |  |  | 209722120
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Setpoint |  |  |  |  | 209722119
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Delay |  |  |  |  | 209722118
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Setpoint |  |  |  |  | 209722117
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N Alarm | Under Voltage L-N Alarm | 411059 | MaskedBool | R | 209722369 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Ack Status | Under Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209722370 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Count | Under Voltage L-N-Alarm Count | 413530 | UINT16 | R | 209722378
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Enabled | Under Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209722371 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Output |  |  |  |  | 209722377
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Priority |  |  |  |  | 209722372
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Delay |  |  |  |  | 209722376
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Setpoint |  |  |  |  | 209722375
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Delay |  |  |  |  | 209722374
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Setpoint |  |  |  |  | 209722373
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic Alarm | Meter Diagnostic Alarm | 411069 | MaskedBool | R | 208666625 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Ack Status | Meter Diagnostic-Ack Status | 411088 | MaskedBool | R | 208666626 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Count | Meter Diagnostic-Alarm Count | 413625 | UINT16 | R | 208666630
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Enabled | Meter Diagnostic-Alarm Enabled | 411050 | MaskedBool | R | 208666627 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Output |  |  |  |  | 208666629
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Priority |  |  |  |  | 208666628
|  | Alarms - Unary | Meter Power Up | Meter Power Up Alarm | Meter Power Up Alarm | 411069 | MaskedBool | R | 208666881 | 0x0001
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Ack Status | Meter Power Up-Ack Status | 411088 | MaskedBool | R | 208666882 | 0x0001
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Count | Meter Power Up-Alarm Count | 413623 | UINT16 | R | 208666886
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Enabled | Meter Power Up-Alarm Enabled | 411050 | MaskedBool | R | 208666883 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Output |  |  |  |  | 208666885
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Priority |  |  |  |  | 208666884
|  | Alarms - Unary | Meter Reset | Meter Reset Alarm | Meter Reset Alarm | 411069 | MaskedBool | R | 208667137 | 0x0002
|  | Alarms - Unary | Meter Reset | Meter Reset-Ack Status | Meter Reset-Ack Status | 411088 | MaskedBool | R | 208667138 | 0x0002
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Count | Meter Reset-Alarm Count | 413624 | UINT16 | R | 208667142
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Enabled | Meter Reset-Alarm Enabled | 411050 | MaskedBool | R | 208667139 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Output |  |  |  |  | 208667141
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Priority |  |  |  |  | 208667140
|  | Alarms - Unary | Phase Reversal | Phase Reversal Alarm | Phase Reversal Alarm | 411069 | MaskedBool | R | 208667393 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Ack Status | Phase Reversal-Ack Status | 411088 | MaskedBool | R | 208667394 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Count | Phase Reversal-Alarm Count | 413626 | UINT16 | R | 208667398
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Enabled | Phase Reversal-Alarm Enabled | 411050 | MaskedBool | R | 208667395 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Output |  |  |  |  | 208667397
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Priority |  |  |  |  | 208667396
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Ack Status | Digital Alarm DI1 Ack Status | 411089 | MaskedBool | R | 206569474 | 0x0001
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Event Counter | Digital Alarm DI1 Event Counter | 413633 | UINT16 | R | 206569480
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Status | Digital Alarm DI1 Status | 411070 | MaskedBool | R | 206569473 | 0x0001
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Digital Output |  |  |  |  | 206569479
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Dropout Delay |  |  |  |  | 206569478
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Pickup Delay |  |  |  |  | 206569477
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Enabled | Digital Alarm DI1 Enabled | 411051 | MaskedBool | R | 206569475 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Priority |  |  |  |  | 206569476
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Setpoint |  |  |  |  | 206569481
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Ack Status | Digital Alarm DI2 Ack Status | 411089 | MaskedBool | R | 206569730 | 0x0002
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Event Counter | Digital Alarm DI2 Event Counter | 413634 | UINT16 | R | 206569736
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Status | Digital Alarm DI2 Status | 411070 | MaskedBool | R | 206569729 | 0x0002
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Digital Output |  |  |  |  | 206569735
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Dropout Delay |  |  |  |  | 206569734
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Pickup Delay |  |  |  |  | 206569733
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Enabled | Digital Alarm DI2 Enabled | 411051 | MaskedBool | R | 206569731 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Priority |  |  |  |  | 206569732
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Setpoint |  |  |  |  | 206569737
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Ack Status | Digital Alarm DI3 Ack Status | 411089 | MaskedBool | R | 206569986 | 0x0004
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Event Counter | Digital Alarm DI3 Event Counter | 413635 | UINT16 | R | 206569992
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Status | Digital Alarm DI3 Status | 411070 | MaskedBool | R | 206569985 | 0x0004
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Digital Output |  |  |  |  | 206569991
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Dropout Delay |  |  |  |  | 206569990
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Pickup Delay |  |  |  |  | 206569989
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Enabled | Digital Alarm DI3 Enabled | 411051 | MaskedBool | R | 206569987 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Priority |  |  |  |  | 206569988
|  | Alarms - Digital | Digital Alarm DI3 | Digital Alarm DI3 Setpoint |  |  |  |  | 206569993
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Ack Status | Digital Alarm DI4 Ack Status | 411089 | MaskedBool | R | 206570242 | 0x0008
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Event Counter | Digital Alarm DI4 Event Counter | 413636 | UINT16 | R | 206570248
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Status | Digital Alarm DI4 Status | 411070 | MaskedBool | R | 206570241 | 0x0008
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Digital Output |  |  |  |  | 206570247
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Dropout Delay |  |  |  |  | 206570246
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Pickup Delay |  |  |  |  | 206570245
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Enabled | Digital Alarm DI4 Enabled | 411051 | MaskedBool | R | 206570243 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Priority |  |  |  |  | 206570244
|  | Alarms - Digital | Digital Alarm DI4 | Digital Alarm DI4 Setpoint |  |  |  |  | 206570249
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01 | Custom Standard Alarm 01 | 411062 | MaskedBool | R | 252043521 | 0x0001
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Ack Status | Custom Standard Alarm 01-Ack Status | 411081 | MaskedBool | R | 252043522 | 0x0001
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Count | Custom Standard Alarm 01-Count | 413563 | UINT16 | R | 252043523
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Dropout Delay | Custom Standard Alarm 01-Dropout Delay | 414831 | UINT32 | R | 252043530
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Dropout Setpoint | Custom Standard Alarm 01-Dropout Setpoint | 414829 | F32-4321 | R | 252043529
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Enabled | Custom Standard Alarm 01-Enabled | 411043 | MaskedBool | R | 252043524 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Label |  |  |  |  | 252043525
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Output | Custom Standard Alarm 01-Output | 414833 | UINT16 | R | 252043531 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Pickup Delay | Custom Standard Alarm 01-Pickup Delay | 414827 | UINT32 | R | 252043528
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Pickup Setpoint | Custom Standard Alarm 01-Pickup Setpoint | 414825 | F32-4321 | R | 252043527
|  | Alarms - Customs | Custom Standard Alarm 01 | Custom Standard Alarm 01-Priority | Custom Standard Alarm 01-Priority | 414820 | UINT32 | R | 252043526 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02 | Custom Standard Alarm 02 | 411062 | MaskedBool | R | 252043777 | 0x0002
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Ack Status | Custom Standard Alarm 02-Ack Status | 411081 | MaskedBool | R | 252043778 | 0x0002
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Count | Custom Standard Alarm 02-Count | 413564 | UINT16 | R | 252043779
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Dropout Delay | Custom Standard Alarm 02-Dropout Delay | 414871 | UINT32 | R | 252043786
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Dropout Setpoint | Custom Standard Alarm 02-Dropout Setpoint | 414869 | F32-4321 | R | 252043785
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Enabled | Custom Standard Alarm 02-Enabled | 411043 | MaskedBool | R | 252043780 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Label | Custom Standard Alarm 02-Label | 414840 | ASCII | R | 252043781 |  |  |  |  | 20
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Output | Custom Standard Alarm 02-Output | 414873 | UINT16 | R | 252043787 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Pickup Delay | Custom Standard Alarm 02-Pickup Delay | 414867 | UINT32 | R | 252043784
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Pickup Setpoint | Custom Standard Alarm 02-Pickup Setpoint | 414865 | F32-4321 | R | 252043783
|  | Alarms - Customs | Custom Standard Alarm 02 | Custom Standard Alarm 02-Priority | Custom Standard Alarm 02-Priority | 414860 | UINT32 | R | 252043782 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03 | Custom Standard Alarm 03 | 411062 | MaskedBool | R | 252044033 | 0x0004
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Ack Status | Custom Standard Alarm 03-Ack Status | 411081 | MaskedBool | R | 252044034 | 0x0004
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Count | Custom Standard Alarm 03-Count | 413565 | UINT16 | R | 252044035
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Dropout Delay | Custom Standard Alarm 03-Dropout Delay | 414911 | UINT32 | R | 252044042
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Dropout Setpoint | Custom Standard Alarm 03-Dropout Setpoint | 414909 | F32-4321 | R | 252044041
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Enabled | Custom Standard Alarm 03-Enabled | 411043 | MaskedBool | R | 252044036 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Label | Custom Standard Alarm 03-Label | 414880 | ASCII | R | 252044037 |  |  |  |  | 20
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Output | Custom Standard Alarm 03-Output | 414913 | UINT16 | R | 252044043 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Pickup Delay | Custom Standard Alarm 03-Pickup Delay | 414907 | UINT32 | R | 252044040
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Pickup Setpoint | Custom Standard Alarm 03-Pickup Setpoint | 414905 | F32-4321 | R | 252044039
|  | Alarms - Customs | Custom Standard Alarm 03 | Custom Standard Alarm 03-Priority | Custom Standard Alarm 03-Priority | 414900 | UINT32 | R | 252044038 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04 | Custom Standard Alarm 04 | 411062 | MaskedBool | R | 252044289 | 0x0008
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Ack Status | Custom Standard Alarm 04-Ack Status | 411081 | MaskedBool | R | 252044290 | 0x0008
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Count | Custom Standard Alarm 04-Count | 413566 | UINT16 | R | 252044291
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Dropout Delay | Custom Standard Alarm 04-Dropout Delay | 414951 | UINT32 | R | 252044298
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Dropout Setpoint | Custom Standard Alarm 04-Dropout Setpoint | 414949 | F32-4321 | R | 252044297
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Enabled | Custom Standard Alarm 04-Enabled | 411043 | MaskedBool | R | 252044292 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Label | Custom Standard Alarm 04-Label | 414920 | ASCII | R | 252044293 |  |  |  |  | 20
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Output | Custom Standard Alarm 04-Output | 414953 | UINT16 | R | 252044299 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Pickup Delay | Custom Standard Alarm 04-Pickup Delay | 414947 | UINT32 | R | 252044296
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Pickup Setpoint | Custom Standard Alarm 04-Pickup Setpoint | 414945 | F32-4321 | R | 252044295
|  | Alarms - Customs | Custom Standard Alarm 04 | Custom Standard Alarm 04-Priority | Custom Standard Alarm 04-Priority | 414940 | UINT32 | R | 252044294 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05 | Custom Standard Alarm 05 | 411062 | MaskedBool | R | 252044545 | 0x0010
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Ack Status | Custom Standard Alarm 05-Ack Status | 411081 | MaskedBool | R | 252044546 | 0x0010
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Count | Custom Standard Alarm 05-Count | 413567 | UINT16 | R | 252044547
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Dropout Delay | Custom Standard Alarm 05-Dropout Delay | 414991 | UINT32 | R | 252044554
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Dropout Setpoint | Custom Standard Alarm 05-Dropout Setpoint | 414989 | F32-4321 | R | 252044553
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Enabled | Custom Standard Alarm 05-Enabled | 411043 | MaskedBool | R | 252044548 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Label | Custom Standard Alarm 05-Label | 414960 | ASCII | R | 252044549 |  |  |  |  | 20
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Output | Custom Standard Alarm 05-Output | 414993 | UINT16 | R | 252044555 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Pickup Delay | Custom Standard Alarm 05-Pickup Delay | 414987 | UINT32 | R | 252044552
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Pickup Setpoint | Custom Standard Alarm 05-Pickup Setpoint | 414985 | F32-4321 | R | 252044551
|  | Alarms - Customs | Custom Standard Alarm 05 | Custom Standard Alarm 05-Priority | Custom Standard Alarm 05-Priority | 414980 | UINT32 | R | 252044550 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01 | Logic Alarm 01 | 411077 | MaskedBool | R | 253092097 | 0x0001
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Ack Status | Logic Alarm 01-Ack Status | 411096 | MaskedBool | R | 253092098 | 0x0001
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Count | Logic Alarm 01-Count | 413721 | UINT16 | R | 253092099
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Enabled | Logic Alarm 01-Enabled | 411058 | MaskedBool | R | 253092100 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Label |  |  |  |  | 253092101
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Output |  |  |  |  | 253092103
|  | Alarms - Logic | Logic Alarm 01 | Logic Alarm 01-Priority |  |  |  |  | 253092102
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02 | Logic Alarm 02 | 411077 | MaskedBool | R | 253092353 | 0x0002
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Ack Status | Logic Alarm 02-Ack Status | 411096 | MaskedBool | R | 253092354 | 0x0002
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Count | Logic Alarm 02-Count | 413722 | UINT16 | R | 253092355
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Enabled | Logic Alarm 02-Enabled | 411058 | MaskedBool | R | 253092356 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Label |  |  |  |  | 253092357
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Output |  |  |  |  | 253092359
|  | Alarms - Logic | Logic Alarm 02 | Logic Alarm 02-Priority |  |  |  |  | 253092358
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03 | Logic Alarm 03 | 411077 | MaskedBool | R | 253092609 | 0x0004
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Ack Status | Logic Alarm 03-Ack Status | 411096 | MaskedBool | R | 253092610 | 0x0004
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Count | Logic Alarm 03-Count | 413723 | UINT16 | R | 253092611
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Enabled | Logic Alarm 03-Enabled | 411058 | MaskedBool | R | 253092612 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Label |  |  |  |  | 253092613
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Output |  |  |  |  | 253092615
|  | Alarms - Logic | Logic Alarm 03 | Logic Alarm 03-Priority |  |  |  |  | 253092614
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04 | Logic Alarm 04 | 411077 | MaskedBool | R | 253092865 | 0x0008
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Ack Status | Logic Alarm 04-Ack Status | 411096 | MaskedBool | R | 253092866 | 0x0008
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Count | Logic Alarm 04-Count | 413724 | UINT16 | R | 253092867
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Enabled | Logic Alarm 04-Enabled | 411058 | MaskedBool | R | 253092868 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Label |  |  |  |  | 253092869
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Output |  |  |  |  | 253092871
|  | Alarms - Logic | Logic Alarm 04 | Logic Alarm 04-Priority |  |  |  |  | 253092870
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05 | Logic Alarm 05 | 411077 | MaskedBool | R | 253093121 | 0x0010
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Ack Status | Logic Alarm 05-Ack Status | 411096 | MaskedBool | R | 253093122 | 0x0010
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Count | Logic Alarm 05-Count | 413725 | UINT16 | R | 253093123
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Enabled | Logic Alarm 05-Enabled | 411058 | MaskedBool | R | 253093124 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Label |  |  |  |  | 253093125
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Output |  |  |  |  | 253093127
|  | Alarms - Logic | Logic Alarm 05 | Logic Alarm 05-Priority |  |  |  |  | 253093126
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06 | Logic Alarm 06 | 411077 | MaskedBool | R | 253093377 | 0x0020
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Ack Status | Logic Alarm 06-Ack Status | 411096 | MaskedBool | R | 253093378 | 0x0020
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Count | Logic Alarm 06-Count | 413726 | UINT16 | R | 253093379
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Enabled | Logic Alarm 06-Enabled | 411058 | MaskedBool | R | 253093380 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Label |  |  |  |  | 253093381
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Output |  |  |  |  | 253093383
|  | Alarms - Logic | Logic Alarm 06 | Logic Alarm 06-Priority |  |  |  |  | 253093382
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07 | Logic Alarm 07 | 411077 | MaskedBool | R | 253093633 | 0x0040
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Ack Status | Logic Alarm 07-Ack Status | 411096 | MaskedBool | R | 253093634 | 0x0040
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Count | Logic Alarm 07-Count | 413727 | UINT16 | R | 253093635
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Enabled | Logic Alarm 07-Enabled | 411058 | MaskedBool | R | 253093636 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Label |  |  |  |  | 253093637
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Output |  |  |  |  | 253093639
|  | Alarms - Logic | Logic Alarm 07 | Logic Alarm 07-Priority |  |  |  |  | 253093638
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08 | Logic Alarm 08 | 411077 | MaskedBool | R | 253093889 | 0x0080
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Ack Status | Logic Alarm 08-Ack Status | 411096 | MaskedBool | R | 253093890 | 0x0080
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Count | Logic Alarm 08-Count | 413728 | UINT16 | R | 253093891
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Enabled | Logic Alarm 08-Enabled | 411058 | MaskedBool | R | 253093892 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Label |  |  |  |  | 253093893
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Output |  |  |  |  | 253093895
|  | Alarms - Logic | Logic Alarm 08 | Logic Alarm 08-Priority |  |  |  |  | 253093894
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09 | Logic Alarm 09 | 411077 | MaskedBool | R | 253094145 | 0x0100
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Ack Status | Logic Alarm 09-Ack Status | 411096 | MaskedBool | R | 253094146 | 0x0100
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Count | Logic Alarm 09-Count | 413729 | UINT16 | R | 253094147
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Enabled | Logic Alarm 09-Enabled | 411058 | MaskedBool | R | 253094148 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Label |  |  |  |  | 253094149
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Output |  |  |  |  | 253094151
|  | Alarms - Logic | Logic Alarm 09 | Logic Alarm 09-Priority |  |  |  |  | 253094150
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10 | Logic Alarm 10 | 411077 | MaskedBool | R | 253094401 | 0x0200
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Ack Status | Logic Alarm 10-Ack Status | 411096 | MaskedBool | R | 253094402 | 0x0200
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Count | Logic Alarm 10-Count | 413730 | UINT16 | R | 253094403
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Enabled | Logic Alarm 10-Enabled | 411058 | MaskedBool | R | 253094404 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Label |  |  |  |  | 253094405
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Output |  |  |  |  | 253094407
|  | Alarms - Logic | Logic Alarm 10 | Logic Alarm 10-Priority |  |  |  |  | 253094406
|  | Clocks | Clock | CL1 Day | CL1 Day | 401839 | UINT16 | R | 23424 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Hour | CL1 Hour | 401840 | UINT16 | R | 23425 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | 401845 | DateTime3_IEC870_UTC | R | 23421 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Millisecond | CL1 Millisecond | 401843 | UINT16 | R | 23428 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Minute | CL1 Minute | 401841 | UINT16 | R | 23426 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Month | CL1 Month | 401838 | UINT16 | R | 23423 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Second | CL1 Second | 401842 | UINT16 | R | 23427 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | 401845 | DateTime3_IEC870_LOCAL | R | 23420 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Year | CL1 Year | 401837 | UINT16 | R | 23422 |  |  |  |  | 1
DR2 | 900 secs | Currents | Current | Current A | Current A | 403000 | F32-4321 | R | 164626433 |  |  |  |  | 2
DR2 | 900 secs | Currents | Current | Current Avg | Current Avg | 403010 | F32-4321 | R | 164626439 |  |  |  |  | 2
DR2 | 900 secs | Currents | Current | Current B | Current B | 403002 | F32-4321 | R | 164626434 |  |  |  |  | 2
DR2 | 900 secs | Currents | Current | Current C | Current C | 403004 | F32-4321 | R | 164626435 |  |  |  |  | 2
|  | Currents | Current | Current G | Current G | 403008 | F32-4321 | R | 164626437 |  |  |  |  | 2
|  | Currents | Current | Current N | Current N | 403006 | F32-4321 | R | 164626436 |  |  |  |  | 2
|  | Demand Readings and History | Demand Apparent Power A | Demand Apparent Power (KVAD) A - Present | Demand Apparent Power (KVAD) A - Present | 404006 | F32-4321 | R | 254143490
|  | Demand Readings and History | Demand Apparent Power A | Demand Apparent Power A | Demand Apparent Power A | 404004 | F32-4321 | R | 254143489
|  | Demand Readings and History | Demand Apparent Power A | DT Peak Demand Apparent Power A | DT Peak Demand Apparent Power A | 404014 | DateTime3_IEC870_UTC | R | 254143493
|  | Demand Readings and History | Demand Apparent Power A | Peak Demand Apparent Power A | Peak Demand Apparent Power A | 404012 | F32-4321 | R | 254143492
|  | Demand Readings and History | Demand Apparent Power A | Predicted KVA Demand A | Predicted KVA Demand A | 404008 | F32-4321 | R | 254143491
|  | Demand Readings and History | Demand Apparent Power B | Demand Apparent Power (KVAD) B - Present | Demand Apparent Power (KVAD) B - Present | 404054 | F32-4321 | R | 254143746
|  | Demand Readings and History | Demand Apparent Power B | Demand Apparent Power B | Demand Apparent Power B | 404052 | F32-4321 | R | 254143745
|  | Demand Readings and History | Demand Apparent Power B | DT Peak Demand Apparent Power B | DT Peak Demand Apparent Power B | 404060 | DateTime3_IEC870_UTC | R | 254143749
|  | Demand Readings and History | Demand Apparent Power B | Peak Demand Apparent Power B | Peak Demand Apparent Power B | 404058 | F32-4321 | R | 254143748
|  | Demand Readings and History | Demand Apparent Power B | Predicted KVA Demand B | Predicted KVA Demand B | 404056 | F32-4321 | R | 254143747
|  | Demand Readings and History | Demand Apparent Power C | Demand Apparent Power (KVAD) C - Present | Demand Apparent Power (KVAD) C - Present | 404102 | F32-4321 | R | 254144002
|  | Demand Readings and History | Demand Apparent Power C | Demand Apparent Power C | Demand Apparent Power C | 404100 | F32-4321 | R | 254144001
|  | Demand Readings and History | Demand Apparent Power C | DT Peak Demand Apparent Power C | DT Peak Demand Apparent Power C | 404108 | DateTime3_IEC870_UTC | R | 254144005
|  | Demand Readings and History | Demand Apparent Power C | Peak Demand Apparent Power C | Peak Demand Apparent Power C | 404106 | F32-4321 | R | 254144004
|  | Demand Readings and History | Demand Apparent Power C | Predicted KVA Demand C | Predicted KVA Demand C | 404104 | F32-4321 | R | 254144003
|  | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power | Demand Apparent Power | 403796 | F32-4321 | R | 254143233
|  | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power (KVAD) - Present | Demand Apparent Power (KVAD) - Present | 403798 | F32-4321 | R | 254143234
|  | Demand Readings and History | Demand Apparent Power Total | DT Peak Demand Apparent Power | DT Peak Demand Apparent Power | 403804 | DateTime3_IEC870_UTC | R | 166724630
|  | Demand Readings and History | Demand Apparent Power Total | Peak Demand Apparent Power | Peak Demand Apparent Power | 403802 | F32-4321 | R | 254143236
|  | Demand Readings and History | Demand Apparent Power Total | Predicted KVA Demand | Predicted KVA Demand | 403800 | F32-4321 | R | 254143235
DR3 | 900 secs | Demand Readings and History | Demand Current A | Demand Current A | Demand Current A | 403812 | F32-4321 | R | 254144257
|  | Demand Readings and History | Demand Current A | Demand Current A - Present | Demand Current A - Present | 403814 | F32-4321 | R | 254144258
|  | Demand Readings and History | Demand Current A | DT Peak Demand Current A | DT Peak Demand Current A | 403820 | DateTime3_IEC870_UTC | R | 254144261
|  | Demand Readings and History | Demand Current A | Peak Demand Current A | Peak Demand Current A | 403818 | F32-4321 | R | 254144260
|  | Demand Readings and History | Demand Current A | Predicted Demand Current A | Predicted Demand Current A | 403816 | F32-4321 | R | 254144259
DR3 | 900 secs | Demand Readings and History | Demand Current Avg | Demand Current Avg | Demand Current Avg | 403876 | F32-4321 | R | 254145025
|  | Demand Readings and History | Demand Current Avg | Demand Current Avg - Present | Demand Current Avg - Present | 403878 | F32-4321 | R | 254145026
|  | Demand Readings and History | Demand Current Avg | DT Peak Demand Current Avg | DT Peak Demand Current Avg | 403884 | DateTime3_IEC870_UTC | R | 166724877
|  | Demand Readings and History | Demand Current Avg | Peak Demand Current Avg | Peak Demand Current Avg | 403882 | F32-4321 | R | 254145028
|  | Demand Readings and History | Demand Current Avg | Predicted Demand Current Avg | Predicted Demand Current Avg | 403880 | F32-4321 | R | 254145027
DR3 | 900 secs | Demand Readings and History | Demand Current B | Demand Current B | Demand Current B | 403828 | F32-4321 | R | 254144513
|  | Demand Readings and History | Demand Current B | Demand Current B - Present | Demand Current B - Present | 403830 | F32-4321 | R | 254144514
|  | Demand Readings and History | Demand Current B | DT Peak Demand Current B | DT Peak Demand Current B | 403836 | DateTime3_IEC870_UTC | R | 254144517
|  | Demand Readings and History | Demand Current B | Peak Demand Current B | Peak Demand Current B | 403834 | F32-4321 | R | 254144516
|  | Demand Readings and History | Demand Current B | Predicted Demand Current B | Predicted Demand Current B | 403832 | F32-4321 | R | 254144515
DR3 | 900 secs | Demand Readings and History | Demand Current C | Demand Current C | Demand Current C | 403844 | F32-4321 | R | 254144769
|  | Demand Readings and History | Demand Current C | Demand Current C - Present | Demand Current C - Present | 403846 | F32-4321 | R | 254144770
|  | Demand Readings and History | Demand Current C | DT Peak Demand Current C | DT Peak Demand Current C | 403852 | DateTime3_IEC870_UTC | R | 254144773
|  | Demand Readings and History | Demand Current C | Peak Demand Current C | Peak Demand Current C | 403850 | F32-4321 | R | 254144772
|  | Demand Readings and History | Demand Current C | Predicted Demand Current C | Predicted Demand Current C | 403848 | F32-4321 | R | 254144771
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method | Current Demand Calculation Method | 403711 | UINT16 | R | 166723841
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method Code | Current Demand Calculation Method Code | 403711 | UINT16 | R | 166723847
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Interval | Current Demand Elapsed Time in Interval | 403714 | UINT16 | R | 166723844
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Subinterval | Current Demand Elapsed Time in Subinterval | 403715 | UINT16 | R | 166723845
|  | Demand Readings and History | Demand Current Calculation | Current Demand Interval | Current Demand Interval | 403712 | UINT16 | R | 166723842
|  | Demand Readings and History | Demand Current Calculation | Current Demand Sub-Interval | Current Demand Sub-Interval | 403713 | UINT16 | R | 166723843
|  | Demand Readings and History | Demand Current Calculation | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | 403716 | DateTime3_IEC870_UTC | R | 166723846
|  | Demand Readings and History | Demand Current G | Demand Current G | Demand Current G | 403892 | F32-4321 | R | 254145281
|  | Demand Readings and History | Demand Current G | Demand Current G - Present | Demand Current G - Present | 403894 | F32-4321 | R | 254145282
|  | Demand Readings and History | Demand Current G | DT Peak Demand Current G | DT Peak Demand Current G | 403900 | DateTime3_IEC870_UTC | R | 254145285
|  | Demand Readings and History | Demand Current G | Peak Demand Current G | Peak Demand Current G | 403898 | F32-4321 | R | 254145284
|  | Demand Readings and History | Demand Current G | Predicted Demand Current G | Predicted Demand Current G | 403896 | F32-4321 | R | 254145283
|  | Demand Readings and History | Demand Current N | Demand Current N | Demand Current N | 403860 | F32-4321 | R | 254145537
|  | Demand Readings and History | Demand Current N | Demand Current N - Present | Demand Current N - Present | 403862 | F32-4321 | R | 254145538
|  | Demand Readings and History | Demand Current N | DT Peak Demand Current N | DT Peak Demand Current N | 403868 | DateTime3_IEC870_UTC | R | 254145541
|  | Demand Readings and History | Demand Current N | Peak Demand Current N | Peak Demand Current N | 403866 | F32-4321 | R | 254145540
|  | Demand Readings and History | Demand Current N | Predicted Demand Current N | Predicted Demand Current N | 403864 | F32-4321 | R | 254145539
|  | Demand Readings and History | Demand Power Calculation | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | 403706 | DateTime3_IEC870_UTC | R | 166723597
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method | Power Demand Calculation Method | 403701 | UINT16 | R | 166723593
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method Code | Power Demand Calculation Method Code | 403701 | UINT16 | R | 166723596
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Interval | Power Demand Elapsed Time in Interval | 403704 | UINT16 | R | 166723594
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Subinterval | Power Demand Elapsed Time in Subinterval | 403705 | UINT16 | R | 166723595
|  | Demand Readings and History | Demand Power Calculation | Power Demand Interval | Power Demand Interval | 403702 | UINT16 | R | 166723591
|  | Demand Readings and History | Demand Power Calculation | Power Demand Sub-Interval | Power Demand Sub-Interval | 403703 | UINT16 | R | 166723592
|  | Demand Readings and History | Demand Reactive Power A | Demand Reactive Power (KVARD) A - Present | Demand Reactive Power (KVARD) A - Present | 403990 | F32-4321 | R | 254142466
|  | Demand Readings and History | Demand Reactive Power A | Demand Reactive Power A | Demand Reactive Power A | 403988 | F32-4321 | R | 254142465
|  | Demand Readings and History | Demand Reactive Power A | DT Peak Demand Reactive Power A | DT Peak Demand Reactive Power A | 403996 | DateTime3_IEC870_UTC | R | 254142469
|  | Demand Readings and History | Demand Reactive Power A | Peak Demand Reactive Power A | Peak Demand Reactive Power A | 403994 | F32-4321 | R | 254142468
|  | Demand Readings and History | Demand Reactive Power A | Predicted KVAR Demand A | Predicted KVAR Demand A | 403992 | F32-4321 | R | 254142467
|  | Demand Readings and History | Demand Reactive Power B | Demand Reactive Power (KVARD) B - Present | Demand Reactive Power (KVARD) B - Present | 404038 | F32-4321 | R | 254142722
|  | Demand Readings and History | Demand Reactive Power B | Demand Reactive Power B | Demand Reactive Power B | 404036 | F32-4321 | R | 254142721
|  | Demand Readings and History | Demand Reactive Power B | DT Peak Demand Reactive Power B | DT Peak Demand Reactive Power B | 404044 | DateTime3_IEC870_UTC | R | 254142725
|  | Demand Readings and History | Demand Reactive Power B | Peak Demand Reactive Power B | Peak Demand Reactive Power B | 404042 | F32-4321 | R | 254142724
|  | Demand Readings and History | Demand Reactive Power B | Predicted KVAR Demand B | Predicted KVAR Demand B | 404040 | F32-4321 | R | 254142723
|  | Demand Readings and History | Demand Reactive Power C | Demand Reactive Power (KVARD) C - Present | Demand Reactive Power (KVARD) C - Present | 404086 | F32-4321 | R | 254142978
|  | Demand Readings and History | Demand Reactive Power C | Demand Reactive Power C | Demand Reactive Power C | 404084 | F32-4321 | R | 254142977
|  | Demand Readings and History | Demand Reactive Power C | DT Peak Demand Reactive Power C | DT Peak Demand Reactive Power C | 404092 | DateTime3_IEC870_UTC | R | 254142981
|  | Demand Readings and History | Demand Reactive Power C | Peak Demand Reactive Power C | Peak Demand Reactive Power C | 404090 | F32-4321 | R | 254142980
|  | Demand Readings and History | Demand Reactive Power C | Predicted KVAR Demand C | Predicted KVAR Demand C | 404088 | F32-4321 | R | 254142979
DR3 | 900 secs | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power | Demand Reactive Power | 403780 | F32-4321 | R | 254142209
|  | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power (KVARD) - Present | Demand Reactive Power (KVARD) - Present | 403782 | F32-4321 | R | 254142210
|  | Demand Readings and History | Demand Reactive Power Total | DT Peak Demand Reactive Power | DT Peak Demand Reactive Power | 403788 | DateTime3_IEC870_UTC | R | 166724629
|  | Demand Readings and History | Demand Reactive Power Total | Peak Demand Reactive Power | Peak Demand Reactive Power | 403786 | F32-4321 | R | 254142212
|  | Demand Readings and History | Demand Reactive Power Total | Predicted KVAR Demand | Predicted KVAR Demand | 403784 | F32-4321 | R | 254142211
|  | Demand Readings and History | Demand Real Power A | Demand Real Power (KWD) A - Present | Demand Real Power (KWD) A - Present | 403974 | F32-4321 | R | 254141442
DR3 | 900 secs | Demand Readings and History | Demand Real Power A | Demand Real Power A | Demand Real Power A | 403972 | F32-4321 | R | 254141441
|  | Demand Readings and History | Demand Real Power A | DT Peak Demand Real Power A | DT Peak Demand Real Power A | 403980 | DateTime3_IEC870_UTC | R | 254141445
|  | Demand Readings and History | Demand Real Power A | Peak Demand Real Power A | Peak Demand Real Power A | 403978 | F32-4321 | R | 254141444
|  | Demand Readings and History | Demand Real Power A | Predicted KW Demand A | Predicted KW Demand A | 403976 | F32-4321 | R | 254141443
|  | Demand Readings and History | Demand Real Power B | Demand Real Power (KWD) B - Present | Demand Real Power (KWD) B | 404022 | F32-4321 | R | 254141698
DR3 | 900 secs | Demand Readings and History | Demand Real Power B | Demand Real Power B | Demand Real Power B | 404020 | F32-4321 | R | 254141697
|  | Demand Readings and History | Demand Real Power B | DT Peak Demand Real Power B | DT Peak Demand Real Power B | 404028 | DateTime3_IEC870_UTC | R | 254141701
|  | Demand Readings and History | Demand Real Power B | Peak Demand Real Power B | Peak Demand Real Power B | 404026 | F32-4321 | R | 254141700
|  | Demand Readings and History | Demand Real Power B | Predicted KW Demand B | Predicted KW Demand B | 404024 | F32-4321 | R | 254141699
|  | Demand Readings and History | Demand Real Power C | Demand Real Power (KWD) C - Present | Demand Real Power (KWD) C - Present | 404070 | F32-4321 | R | 254141954
DR3 | 900 secs | Demand Readings and History | Demand Real Power C | Demand Real Power C | Demand Real Power C | 404068 | F32-4321 | R | 254141953
|  | Demand Readings and History | Demand Real Power C | DT Peak Demand Real Power C | DT Peak Demand Real Power C | 404076 | DateTime3_IEC870_UTC | R | 254141957
|  | Demand Readings and History | Demand Real Power C | Peak Demand Real Power C | Peak Demand Real Power C | 404074 | F32-4321 | R | 254141956
|  | Demand Readings and History | Demand Real Power C | Predicted KW Demand C | Predicted KW Demand C | 404072 | F32-4321 | R | 254141955
DR3 | 900 secs | Demand Readings and History | Demand Real Power Total | Demand Real Power | Demand Real Power | 403764 | F32-4321 | R | 254141185
|  | Demand Readings and History | Demand Real Power Total | Demand Real Power (KWD) - Present | Demand Real Power (KWD) - Present | 403766 | F32-4321 | R | 254141186
|  | Demand Readings and History | Demand Real Power Total | DT Peak Demand Real Power | DT Peak Demand Real Power | 403772 | DateTime3_IEC870_UTC | R | 166724628
|  | Demand Readings and History | Demand Real Power Total | Peak Demand Real Power | Peak Demand Real Power | 403770 | F32-4321 | R | 254141188
|  | Demand Readings and History | Demand Real Power Total | Predicted KW Demand | Predicted KW Demand | 403768 | F32-4321 | R | 254141187
|  | Digital Input Output | Digital Input 1 | DI1 Control Mode | DI1 Control Mode | 407274 | UINT16 | R | 205520898 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 1 | DI1 Count | DI1 Count | 408915 | UINT32 | R | 205520902
|  | Digital Input Output | Digital Input 1 | DI1 Debounce Time | DI1 Debounce Time | 407295 | UINT16 | R | 205520900
|  | Digital Input Output | Digital Input 1 | DI1 Label | DI1 Label | 407275 | ASCII | R | 205520899 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 1 | DI1 On Time | DI1 On Time | 408917 | UINT32 | R | 205520903
|  | Digital Input Output | Digital Input 1 | DI1 Status | DI1 Status | 408905 | MaskedBool | R | 205520901 | 0x0001
|  | Digital Input Output | Digital Input 1 | DI1 Type | DI1 Type | 407273 | UINT16 | R | 205520897 |  |  |  | DIType
|  | Digital Input Output | Digital Input 2 | DI2 Control Mode | DI2 Control Mode | 407298 | UINT16 | R | 205521154 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 2 | DI2 Count | DI2 Count | 408919 | UINT32 | R | 205521158
|  | Digital Input Output | Digital Input 2 | DI2 Debounce Time | DI2 Debounce Time | 407319 | UINT16 | R | 205521156
|  | Digital Input Output | Digital Input 2 | DI2 Label | DI2 Label | 407299 | ASCII | R | 205521155 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 2 | DI2 On Time | DI2 On Time | 408921 | UINT32 | R | 205521159
|  | Digital Input Output | Digital Input 2 | DI2 Status | DI2 Status | 408905 | MaskedBool | R | 205521157 | 0x0002
|  | Digital Input Output | Digital Input 2 | DI2 Type | DI2 Type | 407297 | UINT16 | R | 205521153 |  |  |  | DIType
|  | Digital Input Output | Digital Input 3 | DI3 Control Mode | DI3 Control Mode | 407322 | UINT16 | R | 205521410 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 3 | DI3 Count | DI3 Count | 408923 | UINT32 | R | 205521414
|  | Digital Input Output | Digital Input 3 | DI3 Debounce Time | DI3 Debounce Time | 407343 | UINT16 | R | 205521412
|  | Digital Input Output | Digital Input 3 | DI3 Label | DI3 Label | 407323 | ASCII | R | 205521411 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 3 | DI3 On Time | DI3 On Time | 408925 | UINT32 | R | 205521415
|  | Digital Input Output | Digital Input 3 | DI3 Status | DI3 Status | 408905 | MaskedBool | R | 205521413 | 0x0004
|  | Digital Input Output | Digital Input 3 | DI3 Type | DI3 Type | 407321 | UINT16 | R | 205521409 |  |  |  | DIType
|  | Digital Input Output | Digital Input 4 | DI4 Control Mode | DI4 Control Mode | 407346 | UINT16 | R | 205521666 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 4 | DI4 Count | DI4 Count | 408927 | UINT32 | R | 205521670
|  | Digital Input Output | Digital Input 4 | DI4 Debounce Time | DI4 Debounce Time | 407367 | UINT16 | R | 205521668
|  | Digital Input Output | Digital Input 4 | DI4 Label | DI4 Label | 407347 | ASCII | R | 205521667 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 4 | DI4 On Time | DI4 On Time | 408929 | UINT32 | R | 205521671
|  | Digital Input Output | Digital Input 4 | DI4 Status | DI4 Status | 408905 | MaskedBool | R | 205521669 | 0x0008
|  | Digital Input Output | Digital Input 4 | DI4 Type | DI4 Type | 407345 | UINT16 | R | 205521665 |  |  |  | DIType
|  | Digital Input Output | Digital Output 1 | DO1 Behavioral Mode | DO1 Behavioral Mode | 409674 | UINT16 | R | 205521927 |  |  |  | DOBehavioralModes
|  | Digital Input Output | Digital Output 1 | DO1 Config On Time | DO1 Config On Time | 409210 | UINT16 | R | 205521923
|  | Digital Input Output | Digital Output 1 | DO1 Control Mode | DO1 Control Mode | 409673 | UINT16 | R | 205521926 |  |  |  | DOControlModes
|  | Digital Input Output | Digital Output 1 | DO1 Count | DO1 Count | 409675 | UINT32 | R | 205521928
|  | Digital Input Output | Digital Output 1 | DO1 Label | DO1 Label | 409188 | ASCII | R | 205521922 |  |  |  |  | 20
|  | Digital Input Output | Digital Output 1 | DO1 On Time | DO1 On Time | 409677 | UINT32 | R | 205521929
|  | Digital Input Output | Digital Output 1 | DO1 Operating Mode | DO1 Operating Mode | 409672 | UINT16 | R | 205521925 |  |  |  | DOOperatingModes
|  | Digital Input Output | Digital Output 1 | DO1 Status | DO1 Status | 409667 | MaskedBool | R | 205521924 | 0x0001
|  | Digital Input Output | Digital Output 1 | DO1 Type | DO1 Type | 409187 | UINT16 | R | 205521921 |  |  |  | DOTypes
|  | Digital Input Output | Digital Output 2 | DO2 Behavioral Mode | DO2 Behavioral Mode | 409682 | UINT16 | R | 205522183 |  |  |  | DOBehavioralModes
|  | Digital Input Output | Digital Output 2 | DO2 Config On Time | DO2 Config On Time | 409234 | UINT16 | R | 205522179
|  | Digital Input Output | Digital Output 2 | DO2 Control Mode | DO2 Control Mode | 409681 | UINT16 | R | 205522182 |  |  |  | DOControlModes
|  | Digital Input Output | Digital Output 2 | DO2 Count | DO2 Count | 409683 | UINT32 | R | 205522184
|  | Digital Input Output | Digital Output 2 | DO2 Label | DO2 Label | 409212 | ASCII | R | 205522178 |  |  |  |  | 20
|  | Digital Input Output | Digital Output 2 | DO2 On Time | DO2 On Time | 409685 | UINT32 | R | 205522185
|  | Digital Input Output | Digital Output 2 | DO2 Operating Mode | DO2 Operating Mode | 409680 | UINT16 | R | 205522181 |  |  |  | DOOperatingModes
|  | Digital Input Output | Digital Output 2 | DO2 Status | DO2 Status | 409667 | MaskedBool | R | 205522180 | 0x0002
|  | Digital Input Output | Digital Output 2 | DO2 Type | DO2 Type | 409211 | UINT16 | R | 205522177 |  |  |  | DOTypes
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Digital Output Association | EPO1 Digital Output Association | 402131 | UINT16 | R | 205522439 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Energy Channel | EPO1 Energy Channel | 402130 | UINT16 | R | 205522438 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Pulse Weight | EPO1 Pulse Weight | 402132 | F32-4321 | R | 205522437
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Digital Output Association | EPO2 Digital Output Association | 402135 | UINT16 | R | 205522690 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Energy Channel | EPO2 Energy Channel | 402134 | UINT16 | R | 205522689 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Pulse Weight | EPO2 Pulse Weight | 402136 | F32-4321 | R | 205522691
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Digital Output Association | EPO3 Digital Output Association | 402139 | UINT16 | R | 205522946 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Energy Channel | EPO3 Energy Channel | 402138 | UINT16 | R | 205522945 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Pulse Weight | EPO3 Pulse Weight | 402140 | F32-4321 | R | 205522947
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Consumption Units | WAGES External Input 1 Consumption Units | 407054 | UINT16 | R | 255189507 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Consumption Units Code | WAGES External Input 1 Consumption Units Code | 407054 | UINT16 | R | 255189529 |  |  |  |  | 1
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Reset Date Time | WAGES External Input 1 Cumulative Reset Date Time | 403554 | DateTime3_IEC870_UTC | R | 255189516 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage | WAGES External Input 1 Cumulative Usage | 403570 | S64-87-21 | R | 255189515 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate A | WAGES External Input 1 Cumulative Usage Rate A | 404388 | S64-87-21 | R | 255189517 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate B | WAGES External Input 1 Cumulative Usage Rate B | 404392 | S64-87-21 | R | 255189518 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate C | WAGES External Input 1 Cumulative Usage Rate C | 404396 | S64-87-21 | R | 255189519 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate D | WAGES External Input 1 Cumulative Usage Rate D | 404400 | S64-87-21 | R | 255189520 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate E | WAGES External Input 1 Cumulative Usage Rate E | 404404 | S64-87-21 | R | 255189521 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate F | WAGES External Input 1 Cumulative Usage Rate F | 404408 | S64-87-21 | R | 255189522 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate G | WAGES External Input 1 Cumulative Usage Rate G | 404412 | S64-87-21 | R | 255189523 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Cumulative Usage Rate H | WAGES External Input 1 Cumulative Usage Rate H | 404416 | S64-87-21 | R | 255189524 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH1 | WAGES External Input 1 Demand Last | WAGES External Input 1 Demand Last | 403908 | F32-4321 | R | 255189510 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Digital Input Association | WAGES External Input 1 Digital Input Association | 407055 | UINT16 | R | 255189508 |  |  |  |  | 1
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Label | WAGES External Input 1 Label | 407032 | ASCII | R | 255189505 |  |  |  |  | 20
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Peak Demand | WAGES External Input 1 Peak Demand | 403914 | F32-4321 | R | 255189513 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Peak Demand Date Time | WAGES External Input 1 Peak Demand Date Time | 403916 | DateTime3_IEC870_UTC | R | 255189514 |  |  |  |  | 4
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Predicted Demand | WAGES External Input 1 Predicted Demand | 403912 | F32-4321 | R | 255189512 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Present Demand | WAGES External Input 1 Present Demand | 403910 | F32-4321 | R | 255189511 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Pulse Weight | WAGES External Input 1 Pulse Weight | 407052 | F32-4321 | R | 255189506 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Rate | WAGES External Input 1 Rate | 403112 | F32-4321 | R | 255189525 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Rate Max | WAGES External Input 1 Rate Max | 428094 | F32-4321 | R | 255189526 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Rate Min | WAGES External Input 1 Rate Min | 427618 | F32-4321 | R | 255189527 |  |  |  |  | 2
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Rate Units | WAGES External Input 1 Rate Units | 403907 | UINT16 | R | 255189509 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH1 | WAGES External Input 1 Rate Units Code | WAGES External Input 1 Rate Units Code | 403907 | UINT16 | R | 255189528 |  |  |  |  | 1
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Consumption Units | WAGES External Input 2 Consumption Units | 407078 | UINT16 | R | 255189763 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Consumption Units Code | WAGES External Input 2 Consumption Units Code | 407078 | UINT16 | R | 255189785 |  |  |  |  | 1
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Reset Date Time | WAGES External Input 2 Cumulative Reset Date Time | 403558 | DateTime3_IEC870_UTC | R | 255189772 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage | WAGES External Input 2 Cumulative Usage | 403574 | S64-87-21 | R | 255189771 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate A | WAGES External Input 2 Cumulative Usage Rate A | 404420 | S64-87-21 | R | 255189773 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate B | WAGES External Input 2 Cumulative Usage Rate B | 404424 | S64-87-21 | R | 255189774 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate C | WAGES External Input 2 Cumulative Usage Rate C | 404428 | S64-87-21 | R | 255189775 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate D | WAGES External Input 2 Cumulative Usage Rate D | 404432 | S64-87-21 | R | 255189776 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate E | WAGES External Input 2 Cumulative Usage Rate E | 404436 | S64-87-21 | R | 255189777 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate F | WAGES External Input 2 Cumulative Usage Rate F | 404440 | S64-87-21 | R | 255189778 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate G | WAGES External Input 2 Cumulative Usage Rate G | 404444 | S64-87-21 | R | 255189779 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Cumulative Usage Rate H | WAGES External Input 2 Cumulative Usage Rate H | 404448 | S64-87-21 | R | 255189780 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH2 | WAGES External Input 2 Demand Last | WAGES External Input 2 Demand Last | 403924 | F32-4321 | R | 255189766 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Digital Input Association | WAGES External Input 2 Digital Input Association | 407079 | UINT16 | R | 255189764 |  |  |  |  | 1
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Label | WAGES External Input 2 Label | 407056 | ASCII | R | 255189761 |  |  |  |  | 20
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Peak Demand | WAGES External Input 2 Peak Demand | 403930 | F32-4321 | R | 255189769 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Peak Demand Date Time | WAGES External Input 2 Peak Demand Date Time | 403932 | DateTime3_IEC870_UTC | R | 255189770 |  |  |  |  | 4
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Predicted Demand | WAGES External Input 2 Predicted Demand | 403928 | F32-4321 | R | 255189768 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Present Demand | WAGES External Input 2 Present Demand | 403926 | F32-4321 | R | 255189767 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Pulse Weight | WAGES External Input 2 Pulse Weight | 407076 | F32-4321 | R | 255189762 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Rate | WAGES External Input 2 Rate | 403114 | F32-4321 | R | 255189781 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Rate Max | WAGES External Input 2 Rate Max | 428096 | F32-4321 | R | 255189782 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Rate Min | WAGES External Input 2 Rate Min | 427620 | F32-4321 | R | 255189783 |  |  |  |  | 2
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Rate Units | WAGES External Input 2 Rate Units | 403923 | UINT16 | R | 255189765 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH2 | WAGES External Input 2 Rate Units Code | WAGES External Input 2 Rate Units Code | 403923 | UINT16 | R | 255189784 |  |  |  |  | 1
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Consumption Units | WAGES External Input 3 Consumption Units | 407102 | UINT16 | R | 255190019 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Consumption Units Code | WAGES External Input 3 Consumption Units Code | 407102 | UINT16 | R | 255190041 |  |  |  |  | 1
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Reset Date Time | WAGES External Input 3 Cumulative Reset Date Time | 403562 | DateTime3_IEC870_UTC | R | 255190028 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage | WAGES External Input 3 Cumulative Usage | 403578 | S64-87-21 | R | 255190027 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate A | WAGES External Input 3 Cumulative Usage Rate A | 404452 | S64-87-21 | R | 255190029 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate B | WAGES External Input 3 Cumulative Usage Rate B | 404456 | S64-87-21 | R | 255190030 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate C | WAGES External Input 3 Cumulative Usage Rate C | 404460 | S64-87-21 | R | 255190031 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate D | WAGES External Input 3 Cumulative Usage Rate D | 404464 | S64-87-21 | R | 255190032 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate E | WAGES External Input 3 Cumulative Usage Rate E | 404468 | S64-87-21 | R | 255190033 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate F | WAGES External Input 3 Cumulative Usage Rate F | 404472 | S64-87-21 | R | 255190034 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate G | WAGES External Input 3 Cumulative Usage Rate G | 404476 | S64-87-21 | R | 255190035 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Cumulative Usage Rate H | WAGES External Input 3 Cumulative Usage Rate H | 404480 | S64-87-21 | R | 255190036 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH3 | WAGES External Input 3 Demand Last | WAGES External Input 3 Demand Last | 403940 | F32-4321 | R | 255190022 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Digital Input Association | WAGES External Input 3 Digital Input Association | 407103 | UINT16 | R | 255190020 |  |  |  |  | 1
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Label | WAGES External Input 3 Label | 407080 | ASCII | R | 255190017 |  |  |  |  | 20
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Peak Demand | WAGES External Input 3 Peak Demand | 403946 | F32-4321 | R | 255190025 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Peak Demand Date Time | WAGES External Input 3 Peak Demand Date Time | 403948 | DateTime3_IEC870_UTC | R | 255190026 |  |  |  |  | 4
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Predicted Demand | WAGES External Input 3 Predicted Demand | 403944 | F32-4321 | R | 255190024 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Present Demand | WAGES External Input 3 Present Demand | 403942 | F32-4321 | R | 255190023 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Pulse Weight | WAGES External Input 3 Pulse Weight | 407100 | F32-4321 | R | 255190018 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Rate | WAGES External Input 3 Rate | 403116 | F32-4321 | R | 255190037 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Rate Max | WAGES External Input 3 Rate Max | 428098 | F32-4321 | R | 255190038 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Rate Min | WAGES External Input 3 Rate Min | 427622 | F32-4321 | R | 255190039 |  |  |  |  | 2
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Rate Units | WAGES External Input 3 Rate Units | 403939 | UINT16 | R | 255190021 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH3 | WAGES External Input 3 Rate Units Code | WAGES External Input 3 Rate Units Code | 403939 | UINT16 | R | 255190040 |  |  |  |  | 1
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Consumption Units | WAGES External Input 4 Consumption Units | 407126 | UINT16 | R | 255190275 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Consumption Units Code | WAGES External Input 4 Consumption Units Code | 407126 | UINT16 | R | 255190297 |  |  |  |  | 1
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Reset Date Time | WAGES External Input 4 Cumulative Reset Date Time | 403566 | DateTime3_IEC870_UTC | R | 255190284 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage | WAGES External Input 4 Cumulative Usage | 403582 | S64-87-21 | R | 255190283 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate A | WAGES External Input 4 Cumulative Usage Rate A | 404484 | S64-87-21 | R | 255190285 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate B | WAGES External Input 4 Cumulative Usage Rate B | 404488 | S64-87-21 | R | 255190286 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate C | WAGES External Input 4 Cumulative Usage Rate C | 404492 | S64-87-21 | R | 255190287 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate D | WAGES External Input 4 Cumulative Usage Rate D | 404496 | S64-87-21 | R | 255190288 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate E | WAGES External Input 4 Cumulative Usage Rate E | 404500 | S64-87-21 | R | 255190289 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate F | WAGES External Input 4 Cumulative Usage Rate F | 404504 | S64-87-21 | R | 255190290 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate G | WAGES External Input 4 Cumulative Usage Rate G | 404508 | S64-87-21 | R | 255190291 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Cumulative Usage Rate H | WAGES External Input 4 Cumulative Usage Rate H | 404512 | S64-87-21 | R | 255190292 |  |  |  |  | 4
DR4 | 900 secs | Input Metering | Input Metering CH4 | WAGES External Input 4 Demand Last | WAGES External Input 4 Demand Last | 403956 | F32-4321 | R | 255190278 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Digital Input Association | WAGES External Input 4 Digital Input Association | 407127 | UINT16 | R | 255190276 |  |  |  |  | 1
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Label | WAGES External Input 4 Label | 407104 | ASCII | R | 255190273 |  |  |  |  | 20
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Peak Demand | WAGES External Input 4 Peak Demand | 403962 | F32-4321 | R | 255190281 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Peak Demand Date Time | WAGES External Input 4 Peak Demand Date Time | 403964 | DateTime3_IEC870_UTC | R | 255190282 |  |  |  |  | 4
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Predicted Demand | WAGES External Input 4 Predicted Demand | 403960 | F32-4321 | R | 255190280 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Present Demand | WAGES External Input 4 Present Demand | 403958 | F32-4321 | R | 255190279 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Pulse Weight | WAGES External Input 4 Pulse Weight | 407124 | F32-4321 | R | 255190274 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Rate | WAGES External Input 4 Rate | 403118 | F32-4321 | R | 255190293 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Rate Max | WAGES External Input 4 Rate Max | 428100 | F32-4321 | R | 255190294 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Rate Min | WAGES External Input 4 Rate Min | 427624 | F32-4321 | R | 255190295 |  |  |  |  | 2
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Rate Units | WAGES External Input 4 Rate Units | 403955 | UINT16 | R | 255190277 |  |  |  | UnitsCode | 1
|  | Input Metering | Input Metering CH4 | WAGES External Input 4 Rate Units Code | WAGES External Input 4 Rate Units Code | 403955 | UINT16 | R | 255190296 |  |  |  |  | 1
|  | Input Metering | Input Metering Demand Calculation | WAGES External Demand Calculation Method | WAGES External Demand Calculation Method | 403721 | UINT16 | R | 255189249
|  | Input Metering | Input Metering Demand Calculation | WAGES External Demand Elapsed Time in Interval | WAGES External Demand Elapsed Time in Interval | 403724 | UINT16 | R | 255189252
|  | Input Metering | Input Metering Demand Calculation | WAGES External Demand Elapsed Time in Subinterval | WAGES External Demand Elapsed Time in Subinterval | 403725 | UINT16 | R | 255189253
|  | Input Metering | Input Metering Demand Calculation | WAGES External Demand Interval | WAGES External Demand Interval | 403722 | UINT16 | R | 255189250
|  | Input Metering | Input Metering Demand Calculation | WAGES External Demand Sub-Interval | WAGES External Demand Sub-Interval | 403723 | UINT16 | R | 255189251
|  | Input Metering | Input Metering Demand Calculation | DT Last Reset Peak Dmd WAGES External | DT Last Reset Peak Dmd WAGES External | 403726 | DateTime3_IEC870_UTC | R | 255189254
|  | Power Meters | Power Meter | PM1 CT Count | PM1 CT Count | 402029 | UINT16 | R | 65555 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Location | PM1 CT Location | 402034 | UINT16 | R | 65554 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Primary N | PM1 CT Primary N | 402032 | UINT16 | R | 65556 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Secondary N | PM1 CT Secondary N | 402033 | UINT16 | R | 65557 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Current | PM1 Nominal Current | 402020 | F32-4321 | R | 65544 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Frequency | PM1 Nominal Frequency | 402017 | UINT16 | R | 65542
|  | Power Meters | Power Meter | PM1 Nominal Phase Rotation | PM1 Nominal Phase Rotation | 402024 | UINT16 | R | 65547 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Power Factor | PM1 Nominal Power Factor | 402022 | PF32 | R | 65545 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Power Factor Load Direction | PM1 Nominal Power Factor Load Direction | 402022 | F32-4321 | R | 65548 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Voltage | PM1 Nominal Voltage | 402018 | F32-4321 | R | 65543 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Connection Type | PM1 VT Connection Type | 402036 | UINT16 | R | 65541 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Count | PM1 VT Count | 402025 | UINT16 | R | 65552 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Location | PM1 VT Location | 402035 | UINT16 | R | 65553 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Volts Mode | PM1 Volts Mode | 402016 | UINT16 | R | 30720 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Primary | PM1 CT Primary | 402030 | UINT16 | R | 65539 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Secondary | PM1 CT Secondary | 402031 | UINT16 | R | 65540 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Primary | PM1 VT Primary | 402026 | F32-4321 | R | 65537 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Secondary | PM1 VT Secondary | 402028 | UINT16 | R | 65538 |  |  |  |  | 1
|  | Diagnostics | Meter | Calibration Error | Calibration Error | 420007 | MaskedBool | R | 157286669 | 0x0010
|  | Diagnostics | Meter | Cause of Last Meter Reset | Cause of Last Meter Reset | 401836 | UINT16 | R | 157286668
|  | Diagnostics | Meter | Clipping Detected | Clipping Detected | 420007 | MaskedBool | R | 157286662 | 0x0020
|  | Diagnostics | Meter | Control Power Outage Counter | Control Power Outage Counter | 401829 | UINT16 | R | 157286670
|  | Diagnostics | Meter | DT Last Control Power Outage | DT Last Control Power Outage | 401830 | DateTime3_IEC870_UTC | R | 157286671
|  | Diagnostics | Meter | DT Last Unit Restart | DT Last Unit Restart | 401824 | DateTime3_IEC870_UTC | R | 157286664
|  | Diagnostics | Meter | Meter Error Detected | Meter Error Detected | 420007 | MaskedBool | R | 157286657 | 0x0001
|  | Diagnostics | Meter | Metering System Restart Counter | Metering System Restart Counter | 401828 | UINT16 | R | 157286665
|  | Diagnostics | Meter | NVRAM Error | NVRAM Error | 420007 | MaskedBool | R | 157286672 | 0x0004
|  | Diagnostics | Meter | Over Run Energy Pulse Output | Over Run Energy Pulse Output | 420007 | MaskedBool | R | 157286663 | 0x0040
|  | Diagnostics | Meter | RAM Error | RAM Error | 420007 | MaskedBool | R | 157286673 | 0x0002
|  | Diagnostics | Meter | RTC Error | RTC Error | 420007 | MaskedBool | R | 157286674 | 0x0008
|  | Energies | Apparent Energy | Apparent Energy | Apparent Energy | 403244 | S64-87-21 | R | 256238595 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Delivered-Received | Apparent Energy Delivered-Received | 403248 | S64-87-21 | R | 256238596 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Into the Load | Apparent Energy Into the Load | 403236 | S64-87-21 | R | 256238593 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Out of the Load | Apparent Energy Out of the Load | 403240 | S64-87-21 | R | 256238594 |  | 1000
|  | Energies | Apparent Energy | Preset Apparent Energy Into the Load | Preset Apparent Energy Into the Load | 420318 | S64-87-21 | R | 256238597 |  | 1000
|  | Energies | Apparent Energy | Preset Apparent Energy Out of the Load | Preset Apparent Energy Out of the Load | 420322 | S64-87-21 | R | 256238598 |  | 1000
|  | Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | 403200 | DateTime3_IEC870_UTC | R | 169869321
|  | Energies | DT Last Reset Accum Energies Preset | DT Last Reset Accum Energies Preset | DT Last Reset Accum Energies Preset | 420282 | DateTime3_IEC870_UTC | R | 221249537
|  | Energies | Reactive Energy | Preset Reactive Energy Into the Load | Preset Reactive Energy Into the Load | 420302 | S64-87-21 | R | 256238341 |  | 1000
|  | Energies | Reactive Energy | Preset Reactive Energy Out of the Load | Preset Reactive Energy Out of the Load | 420306 | S64-87-21 | R | 256238342 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Absolute | Reactive Energy Absolute | 403228 | S64-87-21 | R | 256238339 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Into the Load | Reactive Energy Into the Load | 403220 | S64-87-21 | R | 256238337 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Out of the Load | Reactive Energy Out of the Load | 403224 | S64-87-21 | R | 256238338 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Signed | Reactive Energy Signed | 403232 | S64-87-21 | R | 256238340 |  | 1000
|  | Energies | Real Energy | Preset Real Energy Into the Load | Preset Real Energy Into the Load | 420286 | S64-87-21 | R | 256238085 |  | 1000
|  | Energies | Real Energy | Preset Real Energy Out of the Load | Preset Real Energy Out of the Load | 420290 | S64-87-21 | R | 256238086 |  | 1000
|  | Energies | Real Energy | Real Energy Absolute | Real Energy Absolute | 403212 | S64-87-21 | R | 256238083 |  | 1000
|  | Energies | Real Energy | Real Energy Into the Load | Real Energy Into the Load | 403204 | S64-87-21 | R | 256238081 |  | 1000
|  | Energies | Real Energy | Real Energy Out of the Load | Real Energy Out of the Load | 403208 | S64-87-21 | R | 256238082 |  | 1000
|  | Energies | Real Energy | Real Energy Signed | Real Energy Signed | 403216 | S64-87-21 | R | 256238084 |  | 1000
|  | Maximum Readings | Max Current | Max Current A | Max Current A | 427694 | F32-4321 | R | 177209601 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current Avg | Max Current Avg | 427704 | F32-4321 | R | 177209607 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current B | Max Current B | 427696 | F32-4321 | R | 177209602 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current C | Max Current C | 427698 | F32-4321 | R | 177209604 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current G | Max Current G | 427702 | F32-4321 | R | 177209605 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current N | Max Current N | 427700 | F32-4321 | R | 177209603 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance A | Max Current Unbalance A | 427706 | F32-4321 | R | 177209857 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance B | Max Current Unbalance B | 427708 | F32-4321 | R | 177209858 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance C | Max Current Unbalance C | 427710 | F32-4321 | R | 177209859 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance Worst | Max Current Unbalance Worst | 427712 | F32-4321 | R | 177209860 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A | Max Displacement Power Factor A | 427790 | PF32 | R | 177210113 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A Load Direction | Max Displacement Power Factor A Load Direction | 427790 | F32-4321 | R | 177210114 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B | Max Displacement Power Factor B | 427792 | PF32 | R | 177210369 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B Load Direction | Max Displacement Power Factor B Load Direction | 427792 | F32-4321 | R | 177210370 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C | Max Displacement Power Factor C | 427794 | PF32 | R | 177210625 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C Load Direction | Max Displacement Power Factor C Load Direction | 427794 | F32-4321 | R | 177210626 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total | Max Displacement Power Factor Total | 427796 | PF32 | R | 177211137 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total Load Direction | Max Displacement Power Factor Total Load Direction | 427796 | F32-4321 | R | 177211138 |  |  |  |  | 2
|  | Maximum Readings | Max Frequency | Max Frequency | Max Frequency | 428092 | F32-4321 | R | 177210881 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power A | Max Apparent Power A | 427764 | F32-4321 | R | 177213449 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power B | Max Apparent Power B | 427766 | F32-4321 | R | 177213450 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power C | Max Apparent Power C | 427768 | F32-4321 | R | 177213451 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power Total | Max Apparent Power Total | 427770 | F32-4321 | R | 177213452 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power A | Max Reactive Power A | 427756 | F32-4321 | R | 177213445 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power B | Max Reactive Power B | 427758 | F32-4321 | R | 177213446 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power C | Max Reactive Power C | 427760 | F32-4321 | R | 177213447 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power Total | Max Reactive Power Total | 427762 | F32-4321 | R | 177213448 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power A | Max Real Power A | 427748 | F32-4321 | R | 177213441 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power B | Max Real Power B | 427750 | F32-4321 | R | 177213442 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power C | Max Real Power C | 427752 | F32-4321 | R | 177213443 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power Total | Max Real Power Total | 427754 | F32-4321 | R | 177213444 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A | Max Power Factor A | 427782 | PF32 | R | 177211393 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A Load Direction | Max Power Factor A Load Direction | 427782 | F32-4321 | R | 177211394 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B | Max Power Factor B | 427784 | PF32 | R | 177211649 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B Load Direction | Max Power Factor B Load Direction | 427784 | F32-4321 | R | 177211650 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C | Max Power Factor C | 427786 | PF32 | R | 177211905 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C Load Direction | Max Power Factor C Load Direction | 427786 | F32-4321 | R | 177211906 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total | Max Power Factor Total | 427788 | PF32 | R | 177212161 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total Load Direction | Max Power Factor Total Load Direction | 427788 | F32-4321 | R | 177212162 |  |  |  |  | 2
|  | Maximum Readings | Max Temperature | Max Internal Unit Temperature | Max Internal Unit Temperature | 427638 | F32-4321 | R | 177216001 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current A | Max THD Current A | 427814 | F32-4321 | R | 177214466 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current B | Max THD Current B | 427816 | F32-4321 | R | 177214467 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current C | Max THD Current C | 427818 | F32-4321 | R | 177214468 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current G | Max THD Current G | 427822 | F32-4321 | R | 177214470 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current N | Max THD Current N | 427820 | F32-4321 | R | 177214469 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current A | Max thd_Current A | 427824 | F32-4321 | R | 177214209 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current B | Max thd_Current B | 427826 | F32-4321 | R | 177214210 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current C | Max thd_Current C | 427828 | F32-4321 | R | 177214211 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current G | Max thd_Current G | 427832 | F32-4321 | R | 177214213 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current N | Max thd_Current N | 427830 | F32-4321 | R | 177214212 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-B | Max THD Voltage A-B | 427836 | F32-4321 | R | 177214977 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-N | Max THD Voltage A-N | 427844 | F32-4321 | R | 177214984 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-C | Max THD Voltage B-C | 427838 | F32-4321 | R | 177214978 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-N | Max THD Voltage B-N | 427846 | F32-4321 | R | 177214985 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-A | Max THD Voltage C-A | 427840 | F32-4321 | R | 177214979 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-N | Max THD Voltage C-N | 427848 | F32-4321 | R | 177214986 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-L | Max THD Voltage L-L | 427842 | F32-4321 | R | 177214980 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-N | Max THD Voltage L-N | 427852 | F32-4321 | R | 177214987 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-B | Max thd_Voltage A-B | 427854 | F32-4321 | R | 177214721 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-N | Max thd_Voltage A-N | 427862 | F32-4321 | R | 177214724 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-C | Max thd_Voltage B-C | 427856 | F32-4321 | R | 177214722 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-N | Max thd_Voltage B-N | 427864 | F32-4321 | R | 177214725 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-A | Max thd_Voltage C-A | 427858 | F32-4321 | R | 177214723 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-N | Max thd_Voltage C-N | 427866 | F32-4321 | R | 177214726 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-L | Max thd_Voltage L-L | 427860 | F32-4321 | R | 177214727 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-N | Max thd_Voltage L-N | 427870 | F32-4321 | R | 177214728 |  |  |  |  | 2
|  | Maximum Readings | Max Total Demand Distortion | Max Total Demand Distortion | Max Total Demand Distortion | 427834 | F32-4321 | R | 177209345 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-B | Max Voltage A-B | 427714 | F32-4321 | R | 177215489 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-N | Max Voltage A-N | 427722 | F32-4321 | R | 177215497 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-C | Max Voltage B-C | 427716 | F32-4321 | R | 177215490 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-N | Max Voltage B-N | 427724 | F32-4321 | R | 177215498 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-A | Max Voltage C-A | 427718 | F32-4321 | R | 177215491 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-N | Max Voltage C-N | 427726 | F32-4321 | R | 177215499 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-L Avg | Max Voltage L-L Avg | 427720 | F32-4321 | R | 177215493 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-N Avg | Max Voltage L-N Avg | 427730 | F32-4321 | R | 177215501 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-B | Max Voltage Unbalance A-B | 427732 | F32-4321 | R | 177215745 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-N | Max Voltage Unbalance A-N | 427740 | F32-4321 | R | 177215753 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-C | Max Voltage Unbalance B-C | 427734 | F32-4321 | R | 177215746 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-N | Max Voltage Unbalance B-N | 427742 | F32-4321 | R | 177215754 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-A | Max Voltage Unbalance C-A | 427736 | F32-4321 | R | 177215747 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-N | Max Voltage Unbalance C-N | 427744 | F32-4321 | R | 177215755 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-L Worst | Max Voltage Unbalance L-L Worst | 427738 | F32-4321 | R | 177215748 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-N Worst | Max Voltage Unbalance L-N Worst | 427746 | F32-4321 | R | 177215756 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current A | Min Current A | 427218 | F32-4321 | R | 178258178 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current Avg | Min Current Avg | 427228 | F32-4321 | R | 178258183 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current B | Min Current B | 427220 | F32-4321 | R | 178258179 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current C | Min Current C | 427222 | F32-4321 | R | 178258180 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current G | Min Current G | 427226 | F32-4321 | R | 178258182 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current N | Min Current N | 427224 | F32-4321 | R | 178258181 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance A | Min Current Unbalance A | 427230 | F32-4321 | R | 178258433 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance B | Min Current Unbalance B | 427232 | F32-4321 | R | 178258434 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance C | Min Current Unbalance C | 427234 | F32-4321 | R | 178258435 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance Worst | Min Current Unbalance Worst | 427236 | F32-4321 | R | 178258436 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A | Min Displacement Power Factor A | 427314 | PF32 | R | 178258689 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A Load Direction | Min Displacement Power Factor A Load Direction | 427314 | F32-4321 | R | 178258690 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B | Min Displacement Power Factor B | 427316 | PF32 | R | 178258945 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B Load Direction | Min Displacement Power Factor B Load Direction | 427316 | F32-4321 | R | 178258946 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C | Min Displacement Power Factor C | 427318 | PF32 | R | 178259201 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C Load Direction | Min Displacement Power Factor C Load Direction | 427318 | F32-4321 | R | 178259202 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total | Min Displacement Power Factor Total | 427320 | PF32 | R | 178259713 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total Load Direction | Min Displacement Power Factor Total Load Direction | 427320 | F32-4321 | R | 178259714 |  |  |  |  | 2
|  | Minimum Readings | Min Frequency | Min Frequency | Min Frequency | 427616 | F32-4321 | R | 178259457 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power A | Min Apparent Power A | 427288 | F32-4321 | R | 178262017 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power B | Min Apparent Power B | 427290 | F32-4321 | R | 178262018 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power C | Min Apparent Power C | 427292 | F32-4321 | R | 178262019 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power Total | Min Apparent Power Total | 427294 | F32-4321 | R | 178262020 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power A | Min Reactive Power A | 427280 | F32-4321 | R | 178262022 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power B | Min Reactive Power B | 427282 | F32-4321 | R | 178262023 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power C | Min Reactive Power C | 427284 | F32-4321 | R | 178262024 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power Total | Min Reactive Power Total | 427286 | F32-4321 | R | 178262025 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power A | Min Real Power A | 427272 | F32-4321 | R | 178262027 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power B | Min Real Power B | 427274 | F32-4321 | R | 178262028 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power C | Min Real Power C | 427276 | F32-4321 | R | 178262029 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power Total | Min Real Power Total | 427278 | F32-4321 | R | 178262030 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A | Min Power Factor A | 427306 | PF32 | R | 178259969 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A Load Direction | Min Power Factor A Load Direction | 427306 | F32-4321 | R | 178259970 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B | Min Power Factor B | 427308 | PF32 | R | 178260225 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B Load Direction | Min Power Factor B Load Direction | 427308 | F32-4321 | R | 178260226 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C | Min Power Factor C | 427310 | PF32 | R | 178260481 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C Load Direction | Min Power Factor C Load Direction | 427310 | F32-4321 | R | 178260482 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total | Min Power Factor Total | 427312 | PF32 | R | 178260737 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total Load Direction | Min Power Factor Total Load Direction | 427312 | F32-4321 | R | 178260738 |  |  |  |  | 2
|  | Minimum Readings | Min Temperture | Min Internal Unit Temperature | Min Internal Unit Temperature | 428114 | F32-4321 | R | 178264577 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current A | Min THD Current A | 427338 | F32-4321 | R | 178263042 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current B | Min THD Current B | 427340 | F32-4321 | R | 178263043 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current C | Min THD Current C | 427342 | F32-4321 | R | 178263044 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current G | Min THD Current G | 427346 | F32-4321 | R | 178263041 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current N | Min THD Current N | 427344 | F32-4321 | R | 178263045 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current A | Min thd_Current A | 427348 | F32-4321 | R | 178262785 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current B | Min thd_Current B | 427350 | F32-4321 | R | 178262786 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current C | Min thd_Current C | 427352 | F32-4321 | R | 178262787 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current G | Min thd_Current G | 427356 | F32-4321 | R | 178262789 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current N | Min thd_Current N | 427354 | F32-4321 | R | 178262788 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-B | Min THD Voltage A-B | 427360 | F32-4321 | R | 178263553 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-N | Min THD Voltage A-N | 427368 | F32-4321 | R | 178263556 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-C | Min THD Voltage B-C | 427362 | F32-4321 | R | 178263554 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-N | Min THD Voltage B-N | 427370 | F32-4321 | R | 178263557 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-A | Min THD Voltage C-A | 427364 | F32-4321 | R | 178263555 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-N | Min THD Voltage C-N | 427372 | F32-4321 | R | 178263558 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-L | Min THD Voltage L-L | 427366 | F32-4321 | R | 178263559 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-N | Min THD Voltage L-N | 427376 | F32-4321 | R | 178263563 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-B | Min thd_Voltage A-B | 427378 | F32-4321 | R | 178263297 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-N | Min thd_Voltage A-N | 427386 | F32-4321 | R | 178263300 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-C | Min thd_Voltage B-C | 427380 | F32-4321 | R | 178263298 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-N | Min thd_Voltage B-N | 427388 | F32-4321 | R | 178263301 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-A | Min thd_Voltage C-A | 427382 | F32-4321 | R | 178263299 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-N | Min thd_Voltage C-N | 427390 | F32-4321 | R | 178263302 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-L | Min thd_Voltage L-L | 427384 | F32-4321 | R | 178263303 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-N | Min thd_Voltage L-N | 427394 | F32-4321 | R | 178263304 |  |  |  |  | 2
|  | Minimum Readings | Min Total Demand Distortion | Min Total Demand Distortion | Min Total Demand Distortion | 427358 | F32-4321 | R | 178257921 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-B | Min Voltage A-B | 427238 | F32-4321 | R | 178264065 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-N | Min Voltage A-N | 427246 | F32-4321 | R | 178264068 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-C | Min Voltage B-C | 427240 | F32-4321 | R | 178264066 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-N | Min Voltage B-N | 427248 | F32-4321 | R | 178264069 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-A | Min Voltage C-A | 427242 | F32-4321 | R | 178264067 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-N | Min Voltage C-N | 427250 | F32-4321 | R | 178264070 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-L Avg | Min Voltage L-L Avg | 427244 | F32-4321 | R | 178264072 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-N Avg | Min Voltage L-N Avg | 427254 | F32-4321 | R | 178264077 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-B | Min Voltage Unbalance A-B | 427256 | F32-4321 | R | 178264321 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-N | Min Voltage Unbalance A-N | 427264 | F32-4321 | R | 178264324 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-C | Min Voltage Unbalance B-C | 427258 | F32-4321 | R | 178264322 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-N | Min Voltage Unbalance B-N | 427266 | F32-4321 | R | 178264325 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-A | Min Voltage Unbalance C-A | 427260 | F32-4321 | R | 178264323 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-N | Min Voltage Unbalance C-N | 427268 | F32-4321 | R | 178264326 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-L Worst | Min Voltage Unbalance L-L Worst | 427262 | F32-4321 | R | 178264331 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-N Worst | Min Voltage Unbalance L-N Worst | 427270 | F32-4321 | R | 178264336 |  |  |  |  | 2
|  | Miscellaneous | Active Load Timer | Active Load Timer | Active Load Timer | 402002 | UINT32 | R | 179307265
|  | Miscellaneous | Active Load Timer | Active Load Timer Setpoint | Active Load Timer Setpoint | 402050 | F32-4321 | R | 179307266
|  | Miscellaneous | Cycle Count | Cycle Count | Cycle Count | 402006 | UINT32 | R | 179307521
|  | Miscellaneous | DT Last Reset MinMax | DT Last Reset MinMax | DT Last Reset MinMax | 427214 | DateTime3_IEC870_UTC | R | 179308289
|  | Miscellaneous | DT Last Reset Temperature MinMax | DT Last Reset Temperature MinMax | DT Last Reset Temperature MinMax | 420343 | DateTime3_IEC870_UTC | R | 179308801
|  | Miscellaneous | Frequency | Frequency | Frequency | 403110 | F32-4321 | R | 179307009
|  | Miscellaneous | Internal Unit Temperature | Internal Unit Temperature | Internal Unit Temperature | 403132 | F32-4321 | R | 179309057
|  | Miscellaneous | LED Mode | LED Mode | LED Mode | 402126 | UINT16 | R | 179306753
|  | Miscellaneous | Meter ON Duration | Meter ON Duration | Meter ON Duration | 402004 | UINT32 | R | 179308545 |  | 3600
|  | Miscellaneous | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | 402048 | F32-4321 | R | 179308033
|  | Miscellaneous | Phase Rotation | Phase Rotation | Phase Rotation | 403134 | UINT16 | R | 179306497
|  | Miscellaneous | Revenue Security Status | Revenue Security Status | Revenue Security Status | 401921 | UINT16 | R | 179307777
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A | Displacement Power Factor A | 403086 | PF32 | R | 186647553
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A Load Direction | Displacement Power Factor A Load Direction | 403086 | F32-4321 | R | 186647554
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B | Displacement Power Factor B | 403088 | PF32 | R | 186647809
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B Load Direction | Displacement Power Factor B Load Direction | 403088 | F32-4321 | R | 186647810
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C | Displacement Power Factor C | 403090 | PF32 | R | 186648065
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C Load Direction | Displacement Power Factor C Load Direction | 403090 | F32-4321 | R | 186648066
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total | Displacement Power Factor Total | 403092 | PF32 | R | 186648321
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total Load Direction | Displacement Power Factor Total Load Direction | 403092 | F32-4321 | R | 186648322
|  | Power Factors | Power Factor A | Power Factor A | Power Factor A | 403078 | PF32 | R | 186646529
|  | Power Factors | Power Factor A | Power Factor A Load Direction | Power Factor A Load Direction | 403078 | F32-4321 | R | 186646530
|  | Power Factors | Power Factor B | Power Factor B | Power Factor B | 403080 | PF32 | R | 186646785
|  | Power Factors | Power Factor B | Power Factor B Load Direction | Power Factor B Load Direction | 403080 | F32-4321 | R | 186646786
|  | Power Factors | Power Factor C | Power Factor C | Power Factor C | 403082 | PF32 | R | 186647041
|  | Power Factors | Power Factor C | Power Factor C Load Direction | Power Factor C Load Direction | 403082 | F32-4321 | R | 186647042
DR2 | 900 secs | Power Factors | Power Factor Total | Power Factor Total | Power Factor Total | 403084 | PF32 | R | 186647297
|  | Power Factors | Power Factor Total | Power Factor Total Load Direction | Power Factor Total Load Direction | 403084 | F32-4321 | R | 186647298
|  | Power Quality | Crest Factor Current | Crest Factor Current A | Crest Factor Current A | 421364 | F32-4321 | R | 187699201 |  |  |  |  | 2
|  | Power Quality | Crest Factor Current | Crest Factor Current B | Crest Factor Current B | 421366 | F32-4321 | R | 187699202 |  |  |  |  | 2
|  | Power Quality | Crest Factor Current | Crest Factor Current C | Crest Factor Current C | 421368 | F32-4321 | R | 187699203 |  |  |  |  | 2
|  | Power Quality | Crest Factor Current | Crest Factor Current N | Crest Factor Current N | 421370 | F32-4321 | R | 187699204 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage A-B | Crest Factor Voltage A-B | 421372 | F32-4321 | R | 187699457 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage A-N | Crest Factor Voltage A-N | 421378 | F32-4321 | R | 187699460 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage B-C | Crest Factor Voltage B-C | 421374 | F32-4321 | R | 187699458 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage B-N | Crest Factor Voltage B-N | 421380 | F32-4321 | R | 187699461 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage C-A | Crest Factor Voltage C-A | 421376 | F32-4321 | R | 187699459 |  |  |  |  | 2
|  | Power Quality | Crest Factor Voltage | Crest Factor Voltage C-N | Crest Factor Voltage C-N | 421382 | F32-4321 | R | 187699462 |  |  |  |  | 2
|  | Power Quality | K-Factor A | K-Factor A | K-Factor A | 421358 | F32-4321 | R | 187698433 |  |  |  |  | 2
|  | Power Quality | K-Factor B | K-Factor B | K-Factor B | 421360 | F32-4321 | R | 187698689 |  |  |  |  | 2
|  | Power Quality | K-Factor C | K-Factor C | K-Factor C | 421362 | F32-4321 | R | 187698945 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current A | THD Current A | 421300 | F32-4321 | R | 187696897 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current B | THD Current B | 421302 | F32-4321 | R | 187696898 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current C | THD Current C | 421304 | F32-4321 | R | 187696899 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current G | THD Current G | 421308 | F32-4321 | R | 187696901 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current N | THD Current N | 421306 | F32-4321 | R | 187696900 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage A-B | THD Voltage A-B | 421322 | F32-4321 | R | 187697153 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage A-N | THD Voltage A-N | 421330 | F32-4321 | R | 187697156 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-C | THD Voltage B-C | 421324 | F32-4321 | R | 187697154 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-N | THD Voltage B-N | 421332 | F32-4321 | R | 187697157 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-A | THD Voltage C-A | 421326 | F32-4321 | R | 187697155 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-N | THD Voltage C-N | 421334 | F32-4321 | R | 187697158 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-L | THD Voltage L-L | 421328 | F32-4321 | R | 187697159 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-N | THD Voltage L-N | 421338 | F32-4321 | R | 187697160 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current A | thd_Current A | 421310 | F32-4321 | R | 187697665 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current B | thd_Current B | 421312 | F32-4321 | R | 187697666 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current C | thd_Current C | 421314 | F32-4321 | R | 187697667 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current G | thd_Current G | 421318 | F32-4321 | R | 187697669 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current N | thd_Current N | 421316 | F32-4321 | R | 187697668 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage A-B | thd_Voltage A-B | 421340 | F32-4321 | R | 187697921 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage A-N | thd_Voltage A-N | 421348 | F32-4321 | R | 187697924 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-C | thd_Voltage B-C | 421342 | F32-4321 | R | 187697922 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-N | thd_Voltage B-N | 421350 | F32-4321 | R | 187697925 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-A | thd_Voltage C-A | 421344 | F32-4321 | R | 187697923 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-N | thd_Voltage C-N | 421352 | F32-4321 | R | 187697926 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-L | thd_Voltage L-L | 421346 | F32-4321 | R | 187697927 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-N | thd_Voltage L-N | 421356 | F32-4321 | R | 187697928 |  |  |  |  | 2
|  | Power Quality | Total Demand Distortion | Total Demand Distortion | Total Demand Distortion | 421320 | F32-4321 | R | 187698177 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power A | Apparent Power A | 403070 | F32-4321 | R | 190840841 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power B | Apparent Power B | 403072 | F32-4321 | R | 190840842 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power C | Apparent Power C | 403074 | F32-4321 | R | 190840843 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power Total | Apparent Power Total | 403076 | F32-4321 | R | 190840844 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power A | Reactive Power A | 403062 | F32-4321 | R | 190840837 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power B | Reactive Power B | 403064 | F32-4321 | R | 190840838 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power C | Reactive Power C | 403066 | F32-4321 | R | 190840839 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power Total | Reactive Power Total | 403068 | F32-4321 | R | 190840840 |  |  |  |  | 2
|  | Powers | Real Power | Real Power A | Real Power A | 403054 | F32-4321 | R | 190840833 |  |  |  |  | 2
|  | Powers | Real Power | Real Power B | Real Power B | 403056 | F32-4321 | R | 190840834 |  |  |  |  | 2
|  | Powers | Real Power | Real Power C | Real Power C | 403058 | F32-4321 | R | 190840835 |  |  |  |  | 2
|  | Powers | Real Power | Real Power Total | Real Power Total | 403060 | F32-4321 | R | 190840836 |  |  |  |  | 2
|  | Resets and Triggers | Digital Inputs | DI1 Counter Reset | DI1 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238593
|  | Resets and Triggers | Digital Inputs | DI2 Counter Reset | DI2 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238594
|  | Resets and Triggers | Digital Inputs | DI3 Counter Reset | DI3 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238595
|  | Resets and Triggers | Digital Inputs | DI4 Counter Reset | DI4 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238596
|  | Resets and Triggers | Resets | Accumulated Energy Reset | Accumulated Energy Reset | 405250 | U16-21-ARRAY | CW | 156237828
|  | Resets and Triggers | Resets | All Demand Interval Reset | All Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237839
|  | Resets and Triggers | Resets | Current Demand Interval Reset | Current Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237829
|  | Resets and Triggers | Resets | Current Demand Reset | Current Demand Reset | 405250 | U16-21-ARRAY | CW | 156237837
|  | Resets and Triggers | Resets | Min Max Reset | Min Max Reset | 405250 | U16-21-ARRAY | CW | 156237840
|  | Resets and Triggers | Resets | Peak Demand Current Reset | Peak Demand Current Reset | 405250 | U16-21-ARRAY | CW | 156237825
|  | Resets and Triggers | Resets | Power Demand Interval Reset | Power Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237830
|  | Resets and Triggers | Resets | Reset Active Load Timer | Reset Active Load Timer | 405250 | U16-21-ARRAY | CW | 156237831
|  | Resets and Triggers | Resets | Time of Use Reset | Time of Use Reset | 405250 | U16-21-ARRAY | CW | 156237841
|  | Spectral Components | Current A Harmonics | H1 Current A Angle | H1 Current A Angle | 424432 | F32-4321 | R | 257287938
|  | Spectral Components | Current A Harmonics | H1 Current A Magnitude | H1 Current A Magnitude | 424428 | F32-4321 | R | 257287937
|  | Spectral Components | Current A Harmonics | H1 Current A Magnitude RMS | H1 Current A Magnitude RMS | 424430 | F32-4321 | R | 257288063
|  | Spectral Components | Current A Harmonics | H2 Current A Angle | H2 Current A Angle | 424438 | F32-4321 | R | 257287940
|  | Spectral Components | Current A Harmonics | H2 Current A Magnitude | H2 Current A Magnitude | 424434 | F32-4321 | R | 257287939
|  | Spectral Components | Current A Harmonics | H2 Current A Magnitude RMS | H2 Current A Magnitude RMS | 424436 | F32-4321 | R | 257288064
|  | Spectral Components | Current A Harmonics | H3 Current A Angle | H3 Current A Angle | 424444 | F32-4321 | R | 257287942
|  | Spectral Components | Current A Harmonics | H3 Current A Magnitude | H3 Current A Magnitude | 424440 | F32-4321 | R | 257287941
|  | Spectral Components | Current A Harmonics | H3 Current A Magnitude RMS | H3 Current A Magnitude RMS | 424442 | F32-4321 | R | 257288065
|  | Spectral Components | Current A Harmonics | H4 Current A Angle | H4 Current A Angle | 424450 | F32-4321 | R | 257287944
|  | Spectral Components | Current A Harmonics | H4 Current A Magnitude | H4 Current A Magnitude | 424446 | F32-4321 | R | 257287943
|  | Spectral Components | Current A Harmonics | H4 Current A Magnitude RMS | H4 Current A Magnitude RMS | 424448 | F32-4321 | R | 257288066
|  | Spectral Components | Current A Harmonics | H5 Current A Angle | H5 Current A Angle | 424456 | F32-4321 | R | 257287946
|  | Spectral Components | Current A Harmonics | H5 Current A Magnitude | H5 Current A Magnitude | 424452 | F32-4321 | R | 257287945
|  | Spectral Components | Current A Harmonics | H5 Current A Magnitude RMS | H5 Current A Magnitude RMS | 424454 | F32-4321 | R | 257288067
|  | Spectral Components | Current A Harmonics | H6 Current A Angle | H6 Current A Angle | 424462 | F32-4321 | R | 257287948
|  | Spectral Components | Current A Harmonics | H6 Current A Magnitude | H6 Current A Magnitude | 424458 | F32-4321 | R | 257287947
|  | Spectral Components | Current A Harmonics | H6 Current A Magnitude RMS | H6 Current A Magnitude RMS | 424460 | F32-4321 | R | 257288068
|  | Spectral Components | Current A Harmonics | H7 Current A Angle | H7 Current A Angle | 424468 | F32-4321 | R | 257287950
|  | Spectral Components | Current A Harmonics | H7 Current A Magnitude | H7 Current A Magnitude | 424464 | F32-4321 | R | 257287949
|  | Spectral Components | Current A Harmonics | H7 Current A Magnitude RMS | H7 Current A Magnitude RMS | 424466 | F32-4321 | R | 257288069
|  | Spectral Components | Current A Harmonics | H8 Current A Angle | H8 Current A Angle | 424474 | F32-4321 | R | 257287952
|  | Spectral Components | Current A Harmonics | H8 Current A Magnitude | H8 Current A Magnitude | 424470 | F32-4321 | R | 257287951
|  | Spectral Components | Current A Harmonics | H8 Current A Magnitude RMS | H8 Current A Magnitude RMS | 424472 | F32-4321 | R | 257288070
|  | Spectral Components | Current A Harmonics | H9 Current A Angle | H9 Current A Angle | 424480 | F32-4321 | R | 257287954
|  | Spectral Components | Current A Harmonics | H9 Current A Magnitude | H9 Current A Magnitude | 424476 | F32-4321 | R | 257287953
|  | Spectral Components | Current A Harmonics | H9 Current A Magnitude RMS | H9 Current A Magnitude RMS | 424478 | F32-4321 | R | 257288071
|  | Spectral Components | Current A Harmonics | H10 Current A Angle | H10 Current A Angle | 424486 | F32-4321 | R | 257287956
|  | Spectral Components | Current A Harmonics | H10 Current A Magnitude | H10 Current A Magnitude | 424482 | F32-4321 | R | 257287955
|  | Spectral Components | Current A Harmonics | H10 Current A Magnitude RMS | H10 Current A Magnitude RMS | 424484 | F32-4321 | R | 257288072
|  | Spectral Components | Current A Harmonics | H11 Current A Angle | H11 Current A Angle | 424492 | F32-4321 | R | 257287958
|  | Spectral Components | Current A Harmonics | H11 Current A Magnitude | H11 Current A Magnitude | 424488 | F32-4321 | R | 257287957
|  | Spectral Components | Current A Harmonics | H11 Current A Magnitude RMS | H11 Current A Magnitude RMS | 424490 | F32-4321 | R | 257288073
|  | Spectral Components | Current A Harmonics | H12 Current A Angle | H12 Current A Angle | 424498 | F32-4321 | R | 257287960
|  | Spectral Components | Current A Harmonics | H12 Current A Magnitude | H12 Current A Magnitude | 424494 | F32-4321 | R | 257287959
|  | Spectral Components | Current A Harmonics | H12 Current A Magnitude RMS | H12 Current A Magnitude RMS | 424496 | F32-4321 | R | 257288074
|  | Spectral Components | Current A Harmonics | H13 Current A Angle | H13 Current A Angle | 424504 | F32-4321 | R | 257287962
|  | Spectral Components | Current A Harmonics | H13 Current A Magnitude | H13 Current A Magnitude | 424500 | F32-4321 | R | 257287961
|  | Spectral Components | Current A Harmonics | H13 Current A Magnitude RMS | H13 Current A Magnitude RMS | 424502 | F32-4321 | R | 257288075
|  | Spectral Components | Current A Harmonics | H14 Current A Angle | H14 Current A Angle | 424510 | F32-4321 | R | 257287964
|  | Spectral Components | Current A Harmonics | H14 Current A Magnitude | H14 Current A Magnitude | 424506 | F32-4321 | R | 257287963
|  | Spectral Components | Current A Harmonics | H14 Current A Magnitude RMS | H14 Current A Magnitude RMS | 424508 | F32-4321 | R | 257288076
|  | Spectral Components | Current A Harmonics | H15 Current A Angle | H15 Current A Angle | 424516 | F32-4321 | R | 257287966
|  | Spectral Components | Current A Harmonics | H15 Current A Magnitude | H15 Current A Magnitude | 424512 | F32-4321 | R | 257287965
|  | Spectral Components | Current A Harmonics | H15 Current A Magnitude RMS | H15 Current A Magnitude RMS | 424514 | F32-4321 | R | 257288077
|  | Spectral Components | Current A Harmonics | H16 Current A Angle | H16 Current A Angle | 424522 | F32-4321 | R | 257287968
|  | Spectral Components | Current A Harmonics | H16 Current A Magnitude | H16 Current A Magnitude | 424518 | F32-4321 | R | 257287967
|  | Spectral Components | Current A Harmonics | H16 Current A Magnitude RMS | H16 Current A Magnitude RMS | 424520 | F32-4321 | R | 257288078
|  | Spectral Components | Current A Harmonics | H17 Current A Angle | H17 Current A Angle | 424528 | F32-4321 | R | 257287970
|  | Spectral Components | Current A Harmonics | H17 Current A Magnitude | H17 Current A Magnitude | 424524 | F32-4321 | R | 257287969
|  | Spectral Components | Current A Harmonics | H17 Current A Magnitude RMS | H17 Current A Magnitude RMS | 424526 | F32-4321 | R | 257288079
|  | Spectral Components | Current A Harmonics | H18 Current A Angle | H18 Current A Angle | 424534 | F32-4321 | R | 257287972
|  | Spectral Components | Current A Harmonics | H18 Current A Magnitude | H18 Current A Magnitude | 424530 | F32-4321 | R | 257287971
|  | Spectral Components | Current A Harmonics | H18 Current A Magnitude RMS | H18 Current A Magnitude RMS | 424532 | F32-4321 | R | 257288080
|  | Spectral Components | Current A Harmonics | H19 Current A Angle | H19 Current A Angle | 424540 | F32-4321 | R | 257287974
|  | Spectral Components | Current A Harmonics | H19 Current A Magnitude | H19 Current A Magnitude | 424536 | F32-4321 | R | 257287973
|  | Spectral Components | Current A Harmonics | H19 Current A Magnitude RMS | H19 Current A Magnitude RMS | 424538 | F32-4321 | R | 257288081
|  | Spectral Components | Current A Harmonics | H20 Current A Angle | H20 Current A Angle | 424546 | F32-4321 | R | 257287976
|  | Spectral Components | Current A Harmonics | H20 Current A Magnitude | H20 Current A Magnitude | 424542 | F32-4321 | R | 257287975
|  | Spectral Components | Current A Harmonics | H20 Current A Magnitude RMS | H20 Current A Magnitude RMS | 424544 | F32-4321 | R | 257288082
|  | Spectral Components | Current A Harmonics | H21 Current A Angle | H21 Current A Angle | 424552 | F32-4321 | R | 257287978
|  | Spectral Components | Current A Harmonics | H21 Current A Magnitude | H21 Current A Magnitude | 424548 | F32-4321 | R | 257287977
|  | Spectral Components | Current A Harmonics | H21 Current A Magnitude RMS | H21 Current A Magnitude RMS | 424550 | F32-4321 | R | 257288083
|  | Spectral Components | Current A Harmonics | H22 Current A Angle | H22 Current A Angle | 424558 | F32-4321 | R | 257287980
|  | Spectral Components | Current A Harmonics | H22 Current A Magnitude | H22 Current A Magnitude | 424554 | F32-4321 | R | 257287979
|  | Spectral Components | Current A Harmonics | H22 Current A Magnitude RMS | H22 Current A Magnitude RMS | 424556 | F32-4321 | R | 257288084
|  | Spectral Components | Current A Harmonics | H23 Current A Angle | H23 Current A Angle | 424564 | F32-4321 | R | 257287982
|  | Spectral Components | Current A Harmonics | H23 Current A Magnitude | H23 Current A Magnitude | 424560 | F32-4321 | R | 257287981
|  | Spectral Components | Current A Harmonics | H23 Current A Magnitude RMS | H23 Current A Magnitude RMS | 424562 | F32-4321 | R | 257288085
|  | Spectral Components | Current A Harmonics | H24 Current A Angle | H24 Current A Angle | 424570 | F32-4321 | R | 257287984
|  | Spectral Components | Current A Harmonics | H24 Current A Magnitude | H24 Current A Magnitude | 424566 | F32-4321 | R | 257287983
|  | Spectral Components | Current A Harmonics | H24 Current A Magnitude RMS | H24 Current A Magnitude RMS | 424568 | F32-4321 | R | 257288086
|  | Spectral Components | Current A Harmonics | H25 Current A Angle | H25 Current A Angle | 424576 | F32-4321 | R | 257287986
|  | Spectral Components | Current A Harmonics | H25 Current A Magnitude | H25 Current A Magnitude | 424572 | F32-4321 | R | 257287985
|  | Spectral Components | Current A Harmonics | H25 Current A Magnitude RMS | H25 Current A Magnitude RMS | 424574 | F32-4321 | R | 257288087
|  | Spectral Components | Current A Harmonics | H26 Current A Angle | H26 Current A Angle | 424582 | F32-4321 | R | 257287988
|  | Spectral Components | Current A Harmonics | H26 Current A Magnitude | H26 Current A Magnitude | 424578 | F32-4321 | R | 257287987
|  | Spectral Components | Current A Harmonics | H26 Current A Magnitude RMS | H26 Current A Magnitude RMS | 424580 | F32-4321 | R | 257288088
|  | Spectral Components | Current A Harmonics | H27 Current A Angle | H27 Current A Angle | 424588 | F32-4321 | R | 257287990
|  | Spectral Components | Current A Harmonics | H27 Current A Magnitude | H27 Current A Magnitude | 424584 | F32-4321 | R | 257287989
|  | Spectral Components | Current A Harmonics | H27 Current A Magnitude RMS | H27 Current A Magnitude RMS | 424586 | F32-4321 | R | 257288089
|  | Spectral Components | Current A Harmonics | H28 Current A Angle | H28 Current A Angle | 424594 | F32-4321 | R | 257287992
|  | Spectral Components | Current A Harmonics | H28 Current A Magnitude | H28 Current A Magnitude | 424590 | F32-4321 | R | 257287991
|  | Spectral Components | Current A Harmonics | H28 Current A Magnitude RMS | H28 Current A Magnitude RMS | 424592 | F32-4321 | R | 257288090
|  | Spectral Components | Current A Harmonics | H29 Current A Angle | H29 Current A Angle | 424600 | F32-4321 | R | 257287994
|  | Spectral Components | Current A Harmonics | H29 Current A Magnitude | H29 Current A Magnitude | 424596 | F32-4321 | R | 257287993
|  | Spectral Components | Current A Harmonics | H29 Current A Magnitude RMS | H29 Current A Magnitude RMS | 424598 | F32-4321 | R | 257288091
|  | Spectral Components | Current A Harmonics | H30 Current A Angle | H30 Current A Angle | 424606 | F32-4321 | R | 257287996
|  | Spectral Components | Current A Harmonics | H30 Current A Magnitude | H30 Current A Magnitude | 424602 | F32-4321 | R | 257287995
|  | Spectral Components | Current A Harmonics | H30 Current A Magnitude RMS | H30 Current A Magnitude RMS | 424604 | F32-4321 | R | 257288092
|  | Spectral Components | Current A Harmonics | H31 Current A Angle | H31 Current A Angle | 424612 | F32-4321 | R | 257287998
|  | Spectral Components | Current A Harmonics | H31 Current A Magnitude | H31 Current A Magnitude | 424608 | F32-4321 | R | 257287997
|  | Spectral Components | Current A Harmonics | H31 Current A Magnitude RMS | H31 Current A Magnitude RMS | 424610 | F32-4321 | R | 257288093
|  | Spectral Components | Current A Harmonics | H32 Current A Angle | H32 Current A Angle | 424618 | F32-4321 | R | 257288000
|  | Spectral Components | Current A Harmonics | H32 Current A Magnitude | H32 Current A Magnitude | 424614 | F32-4321 | R | 257287999
|  | Spectral Components | Current A Harmonics | H32 Current A Magnitude RMS | H32 Current A Magnitude RMS | 424616 | F32-4321 | R | 257288094
|  | Spectral Components | Current A Harmonics | H33 Current A Angle | H33 Current A Angle | 424624 | F32-4321 | R | 257288002
|  | Spectral Components | Current A Harmonics | H33 Current A Magnitude | H33 Current A Magnitude | 424620 | F32-4321 | R | 257288001
|  | Spectral Components | Current A Harmonics | H33 Current A Magnitude RMS | H33 Current A Magnitude RMS | 424622 | F32-4321 | R | 257288095
|  | Spectral Components | Current A Harmonics | H34 Current A Angle | H34 Current A Angle | 424630 | F32-4321 | R | 257288004
|  | Spectral Components | Current A Harmonics | H34 Current A Magnitude | H34 Current A Magnitude | 424626 | F32-4321 | R | 257288003
|  | Spectral Components | Current A Harmonics | H34 Current A Magnitude RMS | H34 Current A Magnitude RMS | 424628 | F32-4321 | R | 257288096
|  | Spectral Components | Current A Harmonics | H35 Current A Angle | H35 Current A Angle | 424636 | F32-4321 | R | 257288006
|  | Spectral Components | Current A Harmonics | H35 Current A Magnitude | H35 Current A Magnitude | 424632 | F32-4321 | R | 257288005
|  | Spectral Components | Current A Harmonics | H35 Current A Magnitude RMS | H35 Current A Magnitude RMS | 424634 | F32-4321 | R | 257288097
|  | Spectral Components | Current A Harmonics | H36 Current A Angle | H36 Current A Angle | 424642 | F32-4321 | R | 257288008
|  | Spectral Components | Current A Harmonics | H36 Current A Magnitude | H36 Current A Magnitude | 424638 | F32-4321 | R | 257288007
|  | Spectral Components | Current A Harmonics | H36 Current A Magnitude RMS | H36 Current A Magnitude RMS | 424640 | F32-4321 | R | 257288098
|  | Spectral Components | Current A Harmonics | H37 Current A Angle | H37 Current A Angle | 424648 | F32-4321 | R | 257288010
|  | Spectral Components | Current A Harmonics | H37 Current A Magnitude | H37 Current A Magnitude | 424644 | F32-4321 | R | 257288009
|  | Spectral Components | Current A Harmonics | H37 Current A Magnitude RMS | H37 Current A Magnitude RMS | 424646 | F32-4321 | R | 257288099
|  | Spectral Components | Current A Harmonics | H38 Current A Angle | H38 Current A Angle | 424654 | F32-4321 | R | 257288012
|  | Spectral Components | Current A Harmonics | H38 Current A Magnitude | H38 Current A Magnitude | 424650 | F32-4321 | R | 257288011
|  | Spectral Components | Current A Harmonics | H38 Current A Magnitude RMS | H38 Current A Magnitude RMS | 424652 | F32-4321 | R | 257288100
|  | Spectral Components | Current A Harmonics | H39 Current A Angle | H39 Current A Angle | 424660 | F32-4321 | R | 257288014
|  | Spectral Components | Current A Harmonics | H39 Current A Magnitude | H39 Current A Magnitude | 424656 | F32-4321 | R | 257288013
|  | Spectral Components | Current A Harmonics | H39 Current A Magnitude RMS | H39 Current A Magnitude RMS | 424658 | F32-4321 | R | 257288101
|  | Spectral Components | Current A Harmonics | H40 Current A Angle | H40 Current A Angle | 424666 | F32-4321 | R | 257288016
|  | Spectral Components | Current A Harmonics | H40 Current A Magnitude | H40 Current A Magnitude | 424662 | F32-4321 | R | 257288015
|  | Spectral Components | Current A Harmonics | H40 Current A Magnitude RMS | H40 Current A Magnitude RMS | 424664 | F32-4321 | R | 257288102
|  | Spectral Components | Current A Harmonics | H41 Current A Angle | H41 Current A Angle | 424672 | F32-4321 | R | 257288018
|  | Spectral Components | Current A Harmonics | H41 Current A Magnitude | H41 Current A Magnitude | 424668 | F32-4321 | R | 257288017
|  | Spectral Components | Current A Harmonics | H41 Current A Magnitude RMS | H41 Current A Magnitude RMS | 424670 | F32-4321 | R | 257288103
|  | Spectral Components | Current A Harmonics | H42 Current A Angle | H42 Current A Angle | 424678 | F32-4321 | R | 257288020
|  | Spectral Components | Current A Harmonics | H42 Current A Magnitude | H42 Current A Magnitude | 424674 | F32-4321 | R | 257288019
|  | Spectral Components | Current A Harmonics | H42 Current A Magnitude RMS | H42 Current A Magnitude RMS | 424676 | F32-4321 | R | 257288104
|  | Spectral Components | Current A Harmonics | H43 Current A Angle | H43 Current A Angle | 424684 | F32-4321 | R | 257288022
|  | Spectral Components | Current A Harmonics | H43 Current A Magnitude | H43 Current A Magnitude | 424680 | F32-4321 | R | 257288021
|  | Spectral Components | Current A Harmonics | H43 Current A Magnitude RMS | H43 Current A Magnitude RMS | 424682 | F32-4321 | R | 257288105
|  | Spectral Components | Current A Harmonics | H44 Current A Angle | H44 Current A Angle | 424690 | F32-4321 | R | 257288024
|  | Spectral Components | Current A Harmonics | H44 Current A Magnitude | H44 Current A Magnitude | 424686 | F32-4321 | R | 257288023
|  | Spectral Components | Current A Harmonics | H44 Current A Magnitude RMS | H44 Current A Magnitude RMS | 424688 | F32-4321 | R | 257288106
|  | Spectral Components | Current A Harmonics | H45 Current A Angle | H45 Current A Angle | 424696 | F32-4321 | R | 257288026
|  | Spectral Components | Current A Harmonics | H45 Current A Magnitude | H45 Current A Magnitude | 424692 | F32-4321 | R | 257288025
|  | Spectral Components | Current A Harmonics | H45 Current A Magnitude RMS | H45 Current A Magnitude RMS | 424694 | F32-4321 | R | 257288107
|  | Spectral Components | Current A Harmonics | H46 Current A Angle | H46 Current A Angle | 424702 | F32-4321 | R | 257288028
|  | Spectral Components | Current A Harmonics | H46 Current A Magnitude | H46 Current A Magnitude | 424698 | F32-4321 | R | 257288027
|  | Spectral Components | Current A Harmonics | H46 Current A Magnitude RMS | H46 Current A Magnitude RMS | 424700 | F32-4321 | R | 257288108
|  | Spectral Components | Current A Harmonics | H47 Current A Angle | H47 Current A Angle | 424708 | F32-4321 | R | 257288030
|  | Spectral Components | Current A Harmonics | H47 Current A Magnitude | H47 Current A Magnitude | 424704 | F32-4321 | R | 257288029
|  | Spectral Components | Current A Harmonics | H47 Current A Magnitude RMS | H47 Current A Magnitude RMS | 424706 | F32-4321 | R | 257288109
|  | Spectral Components | Current A Harmonics | H48 Current A Angle | H48 Current A Angle | 424714 | F32-4321 | R | 257288032
|  | Spectral Components | Current A Harmonics | H48 Current A Magnitude | H48 Current A Magnitude | 424710 | F32-4321 | R | 257288031
|  | Spectral Components | Current A Harmonics | H48 Current A Magnitude RMS | H48 Current A Magnitude RMS | 424712 | F32-4321 | R | 257288110
|  | Spectral Components | Current A Harmonics | H49 Current A Angle | H49 Current A Angle | 424720 | F32-4321 | R | 257288034
|  | Spectral Components | Current A Harmonics | H49 Current A Magnitude | H49 Current A Magnitude | 424716 | F32-4321 | R | 257288033
|  | Spectral Components | Current A Harmonics | H49 Current A Magnitude RMS | H49 Current A Magnitude RMS | 424718 | F32-4321 | R | 257288111
|  | Spectral Components | Current A Harmonics | H50 Current A Angle | H50 Current A Angle | 424726 | F32-4321 | R | 257288036
|  | Spectral Components | Current A Harmonics | H50 Current A Magnitude | H50 Current A Magnitude | 424722 | F32-4321 | R | 257288035
|  | Spectral Components | Current A Harmonics | H50 Current A Magnitude RMS | H50 Current A Magnitude RMS | 424724 | F32-4321 | R | 257288112
|  | Spectral Components | Current A Harmonics | H51 Current A Angle | H51 Current A Angle | 424732 | F32-4321 | R | 257288038
|  | Spectral Components | Current A Harmonics | H51 Current A Magnitude | H51 Current A Magnitude | 424728 | F32-4321 | R | 257288037
|  | Spectral Components | Current A Harmonics | H51 Current A Magnitude RMS | H51 Current A Magnitude RMS | 424730 | F32-4321 | R | 257288113
|  | Spectral Components | Current A Harmonics | H52 Current A Angle | H52 Current A Angle | 424738 | F32-4321 | R | 257288040
|  | Spectral Components | Current A Harmonics | H52 Current A Magnitude | H52 Current A Magnitude | 424734 | F32-4321 | R | 257288039
|  | Spectral Components | Current A Harmonics | H52 Current A Magnitude RMS | H52 Current A Magnitude RMS | 424736 | F32-4321 | R | 257288114
|  | Spectral Components | Current A Harmonics | H53 Current A Angle | H53 Current A Angle | 424744 | F32-4321 | R | 257288042
|  | Spectral Components | Current A Harmonics | H53 Current A Magnitude | H53 Current A Magnitude | 424740 | F32-4321 | R | 257288041
|  | Spectral Components | Current A Harmonics | H53 Current A Magnitude RMS | H53 Current A Magnitude RMS | 424742 | F32-4321 | R | 257288115
|  | Spectral Components | Current A Harmonics | H54 Current A Angle | H54 Current A Angle | 424750 | F32-4321 | R | 257288044
|  | Spectral Components | Current A Harmonics | H54 Current A Magnitude | H54 Current A Magnitude | 424746 | F32-4321 | R | 257288043
|  | Spectral Components | Current A Harmonics | H54 Current A Magnitude RMS | H54 Current A Magnitude RMS | 424748 | F32-4321 | R | 257288116
|  | Spectral Components | Current A Harmonics | H55 Current A Angle | H55 Current A Angle | 424756 | F32-4321 | R | 257288046
|  | Spectral Components | Current A Harmonics | H55 Current A Magnitude | H55 Current A Magnitude | 424752 | F32-4321 | R | 257288045
|  | Spectral Components | Current A Harmonics | H55 Current A Magnitude RMS | H55 Current A Magnitude RMS | 424754 | F32-4321 | R | 257288117
|  | Spectral Components | Current A Harmonics | H56 Current A Angle | H56 Current A Angle | 424762 | F32-4321 | R | 257288048
|  | Spectral Components | Current A Harmonics | H56 Current A Magnitude | H56 Current A Magnitude | 424758 | F32-4321 | R | 257288047
|  | Spectral Components | Current A Harmonics | H56 Current A Magnitude RMS | H56 Current A Magnitude RMS | 424760 | F32-4321 | R | 257288118
|  | Spectral Components | Current A Harmonics | H57 Current A Angle | H57 Current A Angle | 424768 | F32-4321 | R | 257288050
|  | Spectral Components | Current A Harmonics | H57 Current A Magnitude | H57 Current A Magnitude | 424764 | F32-4321 | R | 257288049
|  | Spectral Components | Current A Harmonics | H57 Current A Magnitude RMS | H57 Current A Magnitude RMS | 424766 | F32-4321 | R | 257288119
|  | Spectral Components | Current A Harmonics | H58 Current A Angle | H58 Current A Angle | 424774 | F32-4321 | R | 257288052
|  | Spectral Components | Current A Harmonics | H58 Current A Magnitude | H58 Current A Magnitude | 424770 | F32-4321 | R | 257288051
|  | Spectral Components | Current A Harmonics | H58 Current A Magnitude RMS | H58 Current A Magnitude RMS | 424772 | F32-4321 | R | 257288120
|  | Spectral Components | Current A Harmonics | H59 Current A Angle | H59 Current A Angle | 424780 | F32-4321 | R | 257288054
|  | Spectral Components | Current A Harmonics | H59 Current A Magnitude | H59 Current A Magnitude | 424776 | F32-4321 | R | 257288053
|  | Spectral Components | Current A Harmonics | H59 Current A Magnitude RMS | H59 Current A Magnitude RMS | 424778 | F32-4321 | R | 257288121
|  | Spectral Components | Current A Harmonics | H60 Current A Angle | H60 Current A Angle | 424786 | F32-4321 | R | 257288056
|  | Spectral Components | Current A Harmonics | H60 Current A Magnitude | H60 Current A Magnitude | 424782 | F32-4321 | R | 257288055
|  | Spectral Components | Current A Harmonics | H60 Current A Magnitude RMS | H60 Current A Magnitude RMS | 424784 | F32-4321 | R | 257288122
|  | Spectral Components | Current A Harmonics | H61 Current A Angle | H61 Current A Angle | 424792 | F32-4321 | R | 257288058
|  | Spectral Components | Current A Harmonics | H61 Current A Magnitude | H61 Current A Magnitude | 424788 | F32-4321 | R | 257288057
|  | Spectral Components | Current A Harmonics | H61 Current A Magnitude RMS | H61 Current A Magnitude RMS | 424790 | F32-4321 | R | 257288123
|  | Spectral Components | Current A Harmonics | H62 Current A Angle | H62 Current A Angle | 424798 | F32-4321 | R | 257288060
|  | Spectral Components | Current A Harmonics | H62 Current A Magnitude | H62 Current A Magnitude | 424794 | F32-4321 | R | 257288059
|  | Spectral Components | Current A Harmonics | H62 Current A Magnitude RMS | H62 Current A Magnitude RMS | 424796 | F32-4321 | R | 257288124
|  | Spectral Components | Current A Harmonics | H63 Current A Angle | H63 Current A Angle | 424804 | F32-4321 | R | 257288062
|  | Spectral Components | Current A Harmonics | H63 Current A Magnitude | H63 Current A Magnitude | 424800 | F32-4321 | R | 257288061
|  | Spectral Components | Current A Harmonics | H63 Current A Magnitude RMS | H63 Current A Magnitude RMS | 424802 | F32-4321 | R | 257288125
|  | Spectral Components | Current B Harmonics | H1 Current B Angle | H1 Current B Angle | 424820 | F32-4321 | R | 257288194
|  | Spectral Components | Current B Harmonics | H1 Current B Magnitude | H1 Current B Magnitude | 424816 | F32-4321 | R | 257288193
|  | Spectral Components | Current B Harmonics | H1 Current B Magnitude RMS | H1 Current B Magnitude RMS | 424818 | F32-4321 | R | 257288319
|  | Spectral Components | Current B Harmonics | H2 Current B Angle | H2 Current B Angle | 424826 | F32-4321 | R | 257288196
|  | Spectral Components | Current B Harmonics | H2 Current B Magnitude | H2 Current B Magnitude | 424822 | F32-4321 | R | 257288195
|  | Spectral Components | Current B Harmonics | H2 Current B Magnitude RMS | H2 Current B Magnitude RMS | 424824 | F32-4321 | R | 257288320
|  | Spectral Components | Current B Harmonics | H3 Current B Angle | H3 Current B Angle | 424832 | F32-4321 | R | 257288198
|  | Spectral Components | Current B Harmonics | H3 Current B Magnitude | H3 Current B Magnitude | 424828 | F32-4321 | R | 257288197
|  | Spectral Components | Current B Harmonics | H3 Current B Magnitude RMS | H3 Current B Magnitude RMS | 424830 | F32-4321 | R | 257288321
|  | Spectral Components | Current B Harmonics | H4 Current B Angle | H4 Current B Angle | 424838 | F32-4321 | R | 257288200
|  | Spectral Components | Current B Harmonics | H4 Current B Magnitude | H4 Current B Magnitude | 424834 | F32-4321 | R | 257288199
|  | Spectral Components | Current B Harmonics | H4 Current B Magnitude RMS | H4 Current B Magnitude RMS | 424836 | F32-4321 | R | 257288322
|  | Spectral Components | Current B Harmonics | H5 Current B Angle | H5 Current B Angle | 424844 | F32-4321 | R | 257288202
|  | Spectral Components | Current B Harmonics | H5 Current B Magnitude | H5 Current B Magnitude | 424840 | F32-4321 | R | 257288201
|  | Spectral Components | Current B Harmonics | H5 Current B Magnitude RMS | H5 Current B Magnitude RMS | 424842 | F32-4321 | R | 257288323
|  | Spectral Components | Current B Harmonics | H6 Current B Angle | H6 Current B Angle | 424850 | F32-4321 | R | 257288204
|  | Spectral Components | Current B Harmonics | H6 Current B Magnitude | H6 Current B Magnitude | 424846 | F32-4321 | R | 257288203
|  | Spectral Components | Current B Harmonics | H6 Current B Magnitude RMS | H6 Current B Magnitude RMS | 424848 | F32-4321 | R | 257288324
|  | Spectral Components | Current B Harmonics | H7 Current B Angle | H7 Current B Angle | 424856 | F32-4321 | R | 257288206
|  | Spectral Components | Current B Harmonics | H7 Current B Magnitude | H7 Current B Magnitude | 424852 | F32-4321 | R | 257288205
|  | Spectral Components | Current B Harmonics | H7 Current B Magnitude RMS | H7 Current B Magnitude RMS | 424854 | F32-4321 | R | 257288325
|  | Spectral Components | Current B Harmonics | H8 Current B Angle | H8 Current B Angle | 424862 | F32-4321 | R | 257288208
|  | Spectral Components | Current B Harmonics | H8 Current B Magnitude | H8 Current B Magnitude | 424858 | F32-4321 | R | 257288207
|  | Spectral Components | Current B Harmonics | H8 Current B Magnitude RMS | H8 Current B Magnitude RMS | 424860 | F32-4321 | R | 257288326
|  | Spectral Components | Current B Harmonics | H9 Current B Angle | H9 Current B Angle | 424868 | F32-4321 | R | 257288210
|  | Spectral Components | Current B Harmonics | H9 Current B Magnitude | H9 Current B Magnitude | 424864 | F32-4321 | R | 257288209
|  | Spectral Components | Current B Harmonics | H9 Current B Magnitude RMS | H9 Current B Magnitude RMS | 424866 | F32-4321 | R | 257288327
|  | Spectral Components | Current B Harmonics | H10 Current B Angle | H10 Current B Angle | 424874 | F32-4321 | R | 257288212
|  | Spectral Components | Current B Harmonics | H10 Current B Magnitude | H10 Current B Magnitude | 424870 | F32-4321 | R | 257288211
|  | Spectral Components | Current B Harmonics | H10 Current B Magnitude RMS | H10 Current B Magnitude RMS | 424872 | F32-4321 | R | 257288328
|  | Spectral Components | Current B Harmonics | H11 Current B Angle | H11 Current B Angle | 424880 | F32-4321 | R | 257288214
|  | Spectral Components | Current B Harmonics | H11 Current B Magnitude | H11 Current B Magnitude | 424876 | F32-4321 | R | 257288213
|  | Spectral Components | Current B Harmonics | H11 Current B Magnitude RMS | H11 Current B Magnitude RMS | 424878 | F32-4321 | R | 257288329
|  | Spectral Components | Current B Harmonics | H12 Current B Angle | H12 Current B Angle | 424886 | F32-4321 | R | 257288216
|  | Spectral Components | Current B Harmonics | H12 Current B Magnitude | H12 Current B Magnitude | 424882 | F32-4321 | R | 257288215
|  | Spectral Components | Current B Harmonics | H12 Current B Magnitude RMS | H12 Current B Magnitude RMS | 424884 | F32-4321 | R | 257288330
|  | Spectral Components | Current B Harmonics | H13 Current B Angle | H13 Current B Angle | 424892 | F32-4321 | R | 257288218
|  | Spectral Components | Current B Harmonics | H13 Current B Magnitude | H13 Current B Magnitude | 424888 | F32-4321 | R | 257288217
|  | Spectral Components | Current B Harmonics | H13 Current B Magnitude RMS | H13 Current B Magnitude RMS | 424890 | F32-4321 | R | 257288331
|  | Spectral Components | Current B Harmonics | H14 Current B Angle | H14 Current B Angle | 424898 | F32-4321 | R | 257288220
|  | Spectral Components | Current B Harmonics | H14 Current B Magnitude | H14 Current B Magnitude | 424894 | F32-4321 | R | 257288219
|  | Spectral Components | Current B Harmonics | H14 Current B Magnitude RMS | H14 Current B Magnitude RMS | 424896 | F32-4321 | R | 257288332
|  | Spectral Components | Current B Harmonics | H15 Current B Angle | H15 Current B Angle | 424904 | F32-4321 | R | 257288222
|  | Spectral Components | Current B Harmonics | H15 Current B Magnitude | H15 Current B Magnitude | 424900 | F32-4321 | R | 257288221
|  | Spectral Components | Current B Harmonics | H15 Current B Magnitude RMS | H15 Current B Magnitude RMS | 424902 | F32-4321 | R | 257288333
|  | Spectral Components | Current B Harmonics | H16 Current B Angle | H16 Current B Angle | 424910 | F32-4321 | R | 257288224
|  | Spectral Components | Current B Harmonics | H16 Current B Magnitude | H16 Current B Magnitude | 424906 | F32-4321 | R | 257288223
|  | Spectral Components | Current B Harmonics | H16 Current B Magnitude RMS | H16 Current B Magnitude RMS | 424908 | F32-4321 | R | 257288334
|  | Spectral Components | Current B Harmonics | H17 Current B Angle | H17 Current B Angle | 424916 | F32-4321 | R | 257288226
|  | Spectral Components | Current B Harmonics | H17 Current B Magnitude | H17 Current B Magnitude | 424912 | F32-4321 | R | 257288225
|  | Spectral Components | Current B Harmonics | H17 Current B Magnitude RMS | H17 Current B Magnitude RMS | 424914 | F32-4321 | R | 257288335
|  | Spectral Components | Current B Harmonics | H18 Current B Angle | H18 Current B Angle | 424922 | F32-4321 | R | 257288228
|  | Spectral Components | Current B Harmonics | H18 Current B Magnitude | H18 Current B Magnitude | 424918 | F32-4321 | R | 257288227
|  | Spectral Components | Current B Harmonics | H18 Current B Magnitude RMS | H18 Current B Magnitude RMS | 424920 | F32-4321 | R | 257288336
|  | Spectral Components | Current B Harmonics | H19 Current B Angle | H19 Current B Angle | 424928 | F32-4321 | R | 257288230
|  | Spectral Components | Current B Harmonics | H19 Current B Magnitude | H19 Current B Magnitude | 424924 | F32-4321 | R | 257288229
|  | Spectral Components | Current B Harmonics | H19 Current B Magnitude RMS | H19 Current B Magnitude RMS | 424926 | F32-4321 | R | 257288337
|  | Spectral Components | Current B Harmonics | H20 Current B Angle | H20 Current B Angle | 424934 | F32-4321 | R | 257288232
|  | Spectral Components | Current B Harmonics | H20 Current B Magnitude | H20 Current B Magnitude | 424930 | F32-4321 | R | 257288231
|  | Spectral Components | Current B Harmonics | H20 Current B Magnitude RMS | H20 Current B Magnitude RMS | 424932 | F32-4321 | R | 257288338
|  | Spectral Components | Current B Harmonics | H21 Current B Angle | H21 Current B Angle | 424940 | F32-4321 | R | 257288234
|  | Spectral Components | Current B Harmonics | H21 Current B Magnitude | H21 Current B Magnitude | 424936 | F32-4321 | R | 257288233
|  | Spectral Components | Current B Harmonics | H21 Current B Magnitude RMS | H21 Current B Magnitude RMS | 424938 | F32-4321 | R | 257288339
|  | Spectral Components | Current B Harmonics | H22 Current B Angle | H22 Current B Angle | 424946 | F32-4321 | R | 257288236
|  | Spectral Components | Current B Harmonics | H22 Current B Magnitude | H22 Current B Magnitude | 424942 | F32-4321 | R | 257288235
|  | Spectral Components | Current B Harmonics | H22 Current B Magnitude RMS | H22 Current B Magnitude RMS | 424944 | F32-4321 | R | 257288340
|  | Spectral Components | Current B Harmonics | H23 Current B Angle | H23 Current B Angle | 424952 | F32-4321 | R | 257288238
|  | Spectral Components | Current B Harmonics | H23 Current B Magnitude | H23 Current B Magnitude | 424948 | F32-4321 | R | 257288237
|  | Spectral Components | Current B Harmonics | H23 Current B Magnitude RMS | H23 Current B Magnitude RMS | 424950 | F32-4321 | R | 257288341
|  | Spectral Components | Current B Harmonics | H24 Current B Angle | H24 Current B Angle | 424958 | F32-4321 | R | 257288240
|  | Spectral Components | Current B Harmonics | H24 Current B Magnitude | H24 Current B Magnitude | 424954 | F32-4321 | R | 257288239
|  | Spectral Components | Current B Harmonics | H24 Current B Magnitude RMS | H24 Current B Magnitude RMS | 424956 | F32-4321 | R | 257288342
|  | Spectral Components | Current B Harmonics | H25 Current B Angle | H25 Current B Angle | 424964 | F32-4321 | R | 257288242
|  | Spectral Components | Current B Harmonics | H25 Current B Magnitude | H25 Current B Magnitude | 424960 | F32-4321 | R | 257288241
|  | Spectral Components | Current B Harmonics | H25 Current B Magnitude RMS | H25 Current B Magnitude RMS | 424962 | F32-4321 | R | 257288343
|  | Spectral Components | Current B Harmonics | H26 Current B Angle | H26 Current B Angle | 424970 | F32-4321 | R | 257288244
|  | Spectral Components | Current B Harmonics | H26 Current B Magnitude | H26 Current B Magnitude | 424966 | F32-4321 | R | 257288243
|  | Spectral Components | Current B Harmonics | H26 Current B Magnitude RMS | H26 Current B Magnitude RMS | 424968 | F32-4321 | R | 257288344
|  | Spectral Components | Current B Harmonics | H27 Current B Angle | H27 Current B Angle | 424976 | F32-4321 | R | 257288246
|  | Spectral Components | Current B Harmonics | H27 Current B Magnitude | H27 Current B Magnitude | 424972 | F32-4321 | R | 257288245
|  | Spectral Components | Current B Harmonics | H27 Current B Magnitude RMS | H27 Current B Magnitude RMS | 424974 | F32-4321 | R | 257288345
|  | Spectral Components | Current B Harmonics | H28 Current B Angle | H28 Current B Angle | 424982 | F32-4321 | R | 257288248
|  | Spectral Components | Current B Harmonics | H28 Current B Magnitude | H28 Current B Magnitude | 424978 | F32-4321 | R | 257288247
|  | Spectral Components | Current B Harmonics | H28 Current B Magnitude RMS | H28 Current B Magnitude RMS | 424980 | F32-4321 | R | 257288346
|  | Spectral Components | Current B Harmonics | H29 Current B Angle | H29 Current B Angle | 424988 | F32-4321 | R | 257288250
|  | Spectral Components | Current B Harmonics | H29 Current B Magnitude | H29 Current B Magnitude | 424984 | F32-4321 | R | 257288249
|  | Spectral Components | Current B Harmonics | H29 Current B Magnitude RMS | H29 Current B Magnitude RMS | 424986 | F32-4321 | R | 257288347
|  | Spectral Components | Current B Harmonics | H30 Current B Angle | H30 Current B Angle | 424994 | F32-4321 | R | 257288252
|  | Spectral Components | Current B Harmonics | H30 Current B Magnitude | H30 Current B Magnitude | 424990 | F32-4321 | R | 257288251
|  | Spectral Components | Current B Harmonics | H30 Current B Magnitude RMS | H30 Current B Magnitude RMS | 424992 | F32-4321 | R | 257288348
|  | Spectral Components | Current B Harmonics | H31 Current B Angle | H31 Current B Angle | 425000 | F32-4321 | R | 257288254
|  | Spectral Components | Current B Harmonics | H31 Current B Magnitude | H31 Current B Magnitude | 424996 | F32-4321 | R | 257288253
|  | Spectral Components | Current B Harmonics | H31 Current B Magnitude RMS | H31 Current B Magnitude RMS | 424998 | F32-4321 | R | 257288349
|  | Spectral Components | Current B Harmonics | H32 Current B Angle | H32 Current B Angle | 425006 | F32-4321 | R | 257288256
|  | Spectral Components | Current B Harmonics | H32 Current B Magnitude | H32 Current B Magnitude | 425002 | F32-4321 | R | 257288255
|  | Spectral Components | Current B Harmonics | H32 Current B Magnitude RMS | H32 Current B Magnitude RMS | 425004 | F32-4321 | R | 257288350
|  | Spectral Components | Current B Harmonics | H33 Current B Angle | H33 Current B Angle | 425012 | F32-4321 | R | 257288258
|  | Spectral Components | Current B Harmonics | H33 Current B Magnitude | H33 Current B Magnitude | 425008 | F32-4321 | R | 257288257
|  | Spectral Components | Current B Harmonics | H33 Current B Magnitude RMS | H33 Current B Magnitude RMS | 425010 | F32-4321 | R | 257288351
|  | Spectral Components | Current B Harmonics | H34 Current B Angle | H34 Current B Angle | 425018 | F32-4321 | R | 257288260
|  | Spectral Components | Current B Harmonics | H34 Current B Magnitude | H34 Current B Magnitude | 425014 | F32-4321 | R | 257288259
|  | Spectral Components | Current B Harmonics | H34 Current B Magnitude RMS | H34 Current B Magnitude RMS | 425016 | F32-4321 | R | 257288352
|  | Spectral Components | Current B Harmonics | H35 Current B Angle | H35 Current B Angle | 425024 | F32-4321 | R | 257288262
|  | Spectral Components | Current B Harmonics | H35 Current B Magnitude | H35 Current B Magnitude | 425020 | F32-4321 | R | 257288261
|  | Spectral Components | Current B Harmonics | H35 Current B Magnitude RMS | H35 Current B Magnitude RMS | 425022 | F32-4321 | R | 257288353
|  | Spectral Components | Current B Harmonics | H36 Current B Angle | H36 Current B Angle | 425030 | F32-4321 | R | 257288264
|  | Spectral Components | Current B Harmonics | H36 Current B Magnitude | H36 Current B Magnitude | 425026 | F32-4321 | R | 257288263
|  | Spectral Components | Current B Harmonics | H36 Current B Magnitude RMS | H36 Current B Magnitude RMS | 425028 | F32-4321 | R | 257288354
|  | Spectral Components | Current B Harmonics | H37 Current B Angle | H37 Current B Angle | 425036 | F32-4321 | R | 257288266
|  | Spectral Components | Current B Harmonics | H37 Current B Magnitude | H37 Current B Magnitude | 425032 | F32-4321 | R | 257288265
|  | Spectral Components | Current B Harmonics | H37 Current B Magnitude RMS | H37 Current B Magnitude RMS | 425034 | F32-4321 | R | 257288355
|  | Spectral Components | Current B Harmonics | H38 Current B Angle | H38 Current B Angle | 425042 | F32-4321 | R | 257288268
|  | Spectral Components | Current B Harmonics | H38 Current B Magnitude | H38 Current B Magnitude | 425038 | F32-4321 | R | 257288267
|  | Spectral Components | Current B Harmonics | H38 Current B Magnitude RMS | H38 Current B Magnitude RMS | 425040 | F32-4321 | R | 257288356
|  | Spectral Components | Current B Harmonics | H39 Current B Angle | H39 Current B Angle | 425048 | F32-4321 | R | 257288270
|  | Spectral Components | Current B Harmonics | H39 Current B Magnitude | H39 Current B Magnitude | 425044 | F32-4321 | R | 257288269
|  | Spectral Components | Current B Harmonics | H39 Current B Magnitude RMS | H39 Current B Magnitude RMS | 425046 | F32-4321 | R | 257288357
|  | Spectral Components | Current B Harmonics | H40 Current B Angle | H40 Current B Angle | 425054 | F32-4321 | R | 257288272
|  | Spectral Components | Current B Harmonics | H40 Current B Magnitude | H40 Current B Magnitude | 425050 | F32-4321 | R | 257288271
|  | Spectral Components | Current B Harmonics | H40 Current B Magnitude RMS | H40 Current B Magnitude RMS | 425052 | F32-4321 | R | 257288358
|  | Spectral Components | Current B Harmonics | H41 Current B Angle | H41 Current B Angle | 425060 | F32-4321 | R | 257288274
|  | Spectral Components | Current B Harmonics | H41 Current B Magnitude | H41 Current B Magnitude | 425056 | F32-4321 | R | 257288273
|  | Spectral Components | Current B Harmonics | H41 Current B Magnitude RMS | H41 Current B Magnitude RMS | 425058 | F32-4321 | R | 257288359
|  | Spectral Components | Current B Harmonics | H42 Current B Angle | H42 Current B Angle | 425066 | F32-4321 | R | 257288276
|  | Spectral Components | Current B Harmonics | H42 Current B Magnitude | H42 Current B Magnitude | 425062 | F32-4321 | R | 257288275
|  | Spectral Components | Current B Harmonics | H42 Current B Magnitude RMS | H42 Current B Magnitude RMS | 425064 | F32-4321 | R | 257288360
|  | Spectral Components | Current B Harmonics | H43 Current B Angle | H43 Current B Angle | 425072 | F32-4321 | R | 257288278
|  | Spectral Components | Current B Harmonics | H43 Current B Magnitude | H43 Current B Magnitude | 425068 | F32-4321 | R | 257288277
|  | Spectral Components | Current B Harmonics | H43 Current B Magnitude RMS | H43 Current B Magnitude RMS | 425070 | F32-4321 | R | 257288361
|  | Spectral Components | Current B Harmonics | H44 Current B Angle | H44 Current B Angle | 425078 | F32-4321 | R | 257288280
|  | Spectral Components | Current B Harmonics | H44 Current B Magnitude | H44 Current B Magnitude | 425074 | F32-4321 | R | 257288279
|  | Spectral Components | Current B Harmonics | H44 Current B Magnitude RMS | H44 Current B Magnitude RMS | 425076 | F32-4321 | R | 257288362
|  | Spectral Components | Current B Harmonics | H45 Current B Angle | H45 Current B Angle | 425084 | F32-4321 | R | 257288282
|  | Spectral Components | Current B Harmonics | H45 Current B Magnitude | H45 Current B Magnitude | 425080 | F32-4321 | R | 257288281
|  | Spectral Components | Current B Harmonics | H45 Current B Magnitude RMS | H45 Current B Magnitude RMS | 425082 | F32-4321 | R | 257288363
|  | Spectral Components | Current B Harmonics | H46 Current B Angle | H46 Current B Angle | 425090 | F32-4321 | R | 257288284
|  | Spectral Components | Current B Harmonics | H46 Current B Magnitude | H46 Current B Magnitude | 425086 | F32-4321 | R | 257288283
|  | Spectral Components | Current B Harmonics | H46 Current B Magnitude RMS | H46 Current B Magnitude RMS | 425088 | F32-4321 | R | 257288364
|  | Spectral Components | Current B Harmonics | H47 Current B Angle | H47 Current B Angle | 425096 | F32-4321 | R | 257288286
|  | Spectral Components | Current B Harmonics | H47 Current B Magnitude | H47 Current B Magnitude | 425092 | F32-4321 | R | 257288285
|  | Spectral Components | Current B Harmonics | H47 Current B Magnitude RMS | H47 Current B Magnitude RMS | 425094 | F32-4321 | R | 257288365
|  | Spectral Components | Current B Harmonics | H48 Current B Angle | H48 Current B Angle | 425102 | F32-4321 | R | 257288288
|  | Spectral Components | Current B Harmonics | H48 Current B Magnitude | H48 Current B Magnitude | 425098 | F32-4321 | R | 257288287
|  | Spectral Components | Current B Harmonics | H48 Current B Magnitude RMS | H48 Current B Magnitude RMS | 425100 | F32-4321 | R | 257288366
|  | Spectral Components | Current B Harmonics | H49 Current B Angle | H49 Current B Angle | 425108 | F32-4321 | R | 257288290
|  | Spectral Components | Current B Harmonics | H49 Current B Magnitude | H49 Current B Magnitude | 425104 | F32-4321 | R | 257288289
|  | Spectral Components | Current B Harmonics | H49 Current B Magnitude RMS | H49 Current B Magnitude RMS | 425106 | F32-4321 | R | 257288367
|  | Spectral Components | Current B Harmonics | H50 Current B Angle | H50 Current B Angle | 425114 | F32-4321 | R | 257288292
|  | Spectral Components | Current B Harmonics | H50 Current B Magnitude | H50 Current B Magnitude | 425110 | F32-4321 | R | 257288291
|  | Spectral Components | Current B Harmonics | H50 Current B Magnitude RMS | H50 Current B Magnitude RMS | 425112 | F32-4321 | R | 257288368
|  | Spectral Components | Current B Harmonics | H51 Current B Angle | H51 Current B Angle | 425120 | F32-4321 | R | 257288294
|  | Spectral Components | Current B Harmonics | H51 Current B Magnitude | H51 Current B Magnitude | 425116 | F32-4321 | R | 257288293
|  | Spectral Components | Current B Harmonics | H51 Current B Magnitude RMS | H51 Current B Magnitude RMS | 425118 | F32-4321 | R | 257288369
|  | Spectral Components | Current B Harmonics | H52 Current B Angle | H52 Current B Angle | 425126 | F32-4321 | R | 257288296
|  | Spectral Components | Current B Harmonics | H52 Current B Magnitude | H52 Current B Magnitude | 425122 | F32-4321 | R | 257288295
|  | Spectral Components | Current B Harmonics | H52 Current B Magnitude RMS | H52 Current B Magnitude RMS | 425124 | F32-4321 | R | 257288370
|  | Spectral Components | Current B Harmonics | H53 Current B Angle | H53 Current B Angle | 425132 | F32-4321 | R | 257288298
|  | Spectral Components | Current B Harmonics | H53 Current B Magnitude | H53 Current B Magnitude | 425128 | F32-4321 | R | 257288297
|  | Spectral Components | Current B Harmonics | H53 Current B Magnitude RMS | H53 Current B Magnitude RMS | 425130 | F32-4321 | R | 257288371
|  | Spectral Components | Current B Harmonics | H54 Current B Angle | H54 Current B Angle | 425138 | F32-4321 | R | 257288300
|  | Spectral Components | Current B Harmonics | H54 Current B Magnitude | H54 Current B Magnitude | 425134 | F32-4321 | R | 257288299
|  | Spectral Components | Current B Harmonics | H54 Current B Magnitude RMS | H54 Current B Magnitude RMS | 425136 | F32-4321 | R | 257288372
|  | Spectral Components | Current B Harmonics | H55 Current B Angle | H55 Current B Angle | 425144 | F32-4321 | R | 257288302
|  | Spectral Components | Current B Harmonics | H55 Current B Magnitude | H55 Current B Magnitude | 425140 | F32-4321 | R | 257288301
|  | Spectral Components | Current B Harmonics | H55 Current B Magnitude RMS | H55 Current B Magnitude RMS | 425142 | F32-4321 | R | 257288373
|  | Spectral Components | Current B Harmonics | H56 Current B Angle | H56 Current B Angle | 425150 | F32-4321 | R | 257288304
|  | Spectral Components | Current B Harmonics | H56 Current B Magnitude | H56 Current B Magnitude | 425146 | F32-4321 | R | 257288303
|  | Spectral Components | Current B Harmonics | H56 Current B Magnitude RMS | H56 Current B Magnitude RMS | 425148 | F32-4321 | R | 257288374
|  | Spectral Components | Current B Harmonics | H57 Current B Angle | H57 Current B Angle | 425156 | F32-4321 | R | 257288306
|  | Spectral Components | Current B Harmonics | H57 Current B Magnitude | H57 Current B Magnitude | 425152 | F32-4321 | R | 257288305
|  | Spectral Components | Current B Harmonics | H57 Current B Magnitude RMS | H57 Current B Magnitude RMS | 425154 | F32-4321 | R | 257288375
|  | Spectral Components | Current B Harmonics | H58 Current B Angle | H58 Current B Angle | 425162 | F32-4321 | R | 257288308
|  | Spectral Components | Current B Harmonics | H58 Current B Magnitude | H58 Current B Magnitude | 425158 | F32-4321 | R | 257288307
|  | Spectral Components | Current B Harmonics | H58 Current B Magnitude RMS | H58 Current B Magnitude RMS | 425160 | F32-4321 | R | 257288376
|  | Spectral Components | Current B Harmonics | H59 Current B Angle | H59 Current B Angle | 425168 | F32-4321 | R | 257288310
|  | Spectral Components | Current B Harmonics | H59 Current B Magnitude | H59 Current B Magnitude | 425164 | F32-4321 | R | 257288309
|  | Spectral Components | Current B Harmonics | H59 Current B Magnitude RMS | H59 Current B Magnitude RMS | 425166 | F32-4321 | R | 257288377
|  | Spectral Components | Current B Harmonics | H60 Current B Angle | H60 Current B Angle | 425174 | F32-4321 | R | 257288312
|  | Spectral Components | Current B Harmonics | H60 Current B Magnitude | H60 Current B Magnitude | 425170 | F32-4321 | R | 257288311
|  | Spectral Components | Current B Harmonics | H60 Current B Magnitude RMS | H60 Current B Magnitude RMS | 425172 | F32-4321 | R | 257288378
|  | Spectral Components | Current B Harmonics | H61 Current B Angle | H61 Current B Angle | 425180 | F32-4321 | R | 257288314
|  | Spectral Components | Current B Harmonics | H61 Current B Magnitude | H61 Current B Magnitude | 425176 | F32-4321 | R | 257288313
|  | Spectral Components | Current B Harmonics | H61 Current B Magnitude RMS | H61 Current B Magnitude RMS | 425178 | F32-4321 | R | 257288379
|  | Spectral Components | Current B Harmonics | H62 Current B Angle | H62 Current B Angle | 425186 | F32-4321 | R | 257288316
|  | Spectral Components | Current B Harmonics | H62 Current B Magnitude | H62 Current B Magnitude | 425182 | F32-4321 | R | 257288315
|  | Spectral Components | Current B Harmonics | H62 Current B Magnitude RMS | H62 Current B Magnitude RMS | 425184 | F32-4321 | R | 257288380
|  | Spectral Components | Current B Harmonics | H63 Current B Angle | H63 Current B Angle | 425192 | F32-4321 | R | 257288318
|  | Spectral Components | Current B Harmonics | H63 Current B Magnitude | H63 Current B Magnitude | 425188 | F32-4321 | R | 257288317
|  | Spectral Components | Current B Harmonics | H63 Current B Magnitude RMS | H63 Current B Magnitude RMS | 425190 | F32-4321 | R | 257288381
|  | Spectral Components | Current C Harmonics | H1 Current C Angle | H1 Current C Angle | 425208 | F32-4321 | R | 257288450
|  | Spectral Components | Current C Harmonics | H1 Current C Magnitude | H1 Current C Magnitude | 425204 | F32-4321 | R | 257288449
|  | Spectral Components | Current C Harmonics | H1 Current C Magnitude RMS | H1 Current C Magnitude RMS | 425206 | F32-4321 | R | 257288575
|  | Spectral Components | Current C Harmonics | H2 Current C Angle | H2 Current C Angle | 425214 | F32-4321 | R | 257288452
|  | Spectral Components | Current C Harmonics | H2 Current C Magnitude | H2 Current C Magnitude | 425210 | F32-4321 | R | 257288451
|  | Spectral Components | Current C Harmonics | H2 Current C Magnitude RMS | H2 Current C Magnitude RMS | 425212 | F32-4321 | R | 257288576
|  | Spectral Components | Current C Harmonics | H3 Current C Angle | H3 Current C Angle | 425220 | F32-4321 | R | 257288454
|  | Spectral Components | Current C Harmonics | H3 Current C Magnitude | H3 Current C Magnitude | 425216 | F32-4321 | R | 257288453
|  | Spectral Components | Current C Harmonics | H3 Current C Magnitude RMS | H3 Current C Magnitude RMS | 425218 | F32-4321 | R | 257288577
|  | Spectral Components | Current C Harmonics | H4 Current C Angle | H4 Current C Angle | 425226 | F32-4321 | R | 257288456
|  | Spectral Components | Current C Harmonics | H4 Current C Magnitude | H4 Current C Magnitude | 425222 | F32-4321 | R | 257288455
|  | Spectral Components | Current C Harmonics | H4 Current C Magnitude RMS | H4 Current C Magnitude RMS | 425224 | F32-4321 | R | 257288578
|  | Spectral Components | Current C Harmonics | H5 Current C Angle | H5 Current C Angle | 425232 | F32-4321 | R | 257288458
|  | Spectral Components | Current C Harmonics | H5 Current C Magnitude | H5 Current C Magnitude | 425228 | F32-4321 | R | 257288457
|  | Spectral Components | Current C Harmonics | H5 Current C Magnitude RMS | H5 Current C Magnitude RMS | 425230 | F32-4321 | R | 257288579
|  | Spectral Components | Current C Harmonics | H6 Current C Angle | H6 Current C Angle | 425238 | F32-4321 | R | 257288460
|  | Spectral Components | Current C Harmonics | H6 Current C Magnitude | H6 Current C Magnitude | 425234 | F32-4321 | R | 257288459
|  | Spectral Components | Current C Harmonics | H6 Current C Magnitude RMS | H6 Current C Magnitude RMS | 425236 | F32-4321 | R | 257288580
|  | Spectral Components | Current C Harmonics | H7 Current C Angle | H7 Current C Angle | 425244 | F32-4321 | R | 257288462
|  | Spectral Components | Current C Harmonics | H7 Current C Magnitude | H7 Current C Magnitude | 425240 | F32-4321 | R | 257288461
|  | Spectral Components | Current C Harmonics | H7 Current C Magnitude RMS | H7 Current C Magnitude RMS | 425242 | F32-4321 | R | 257288581
|  | Spectral Components | Current C Harmonics | H8 Current C Angle | H8 Current C Angle | 425250 | F32-4321 | R | 257288464
|  | Spectral Components | Current C Harmonics | H8 Current C Magnitude | H8 Current C Magnitude | 425246 | F32-4321 | R | 257288463
|  | Spectral Components | Current C Harmonics | H8 Current C Magnitude RMS | H8 Current C Magnitude RMS | 425248 | F32-4321 | R | 257288582
|  | Spectral Components | Current C Harmonics | H9 Current C Angle | H9 Current C Angle | 425256 | F32-4321 | R | 257288466
|  | Spectral Components | Current C Harmonics | H9 Current C Magnitude | H9 Current C Magnitude | 425252 | F32-4321 | R | 257288465
|  | Spectral Components | Current C Harmonics | H9 Current C Magnitude RMS | H9 Current C Magnitude RMS | 425254 | F32-4321 | R | 257288583
|  | Spectral Components | Current C Harmonics | H10 Current C Angle | H10 Current C Angle | 425262 | F32-4321 | R | 257288468
|  | Spectral Components | Current C Harmonics | H10 Current C Magnitude | H10 Current C Magnitude | 425258 | F32-4321 | R | 257288467
|  | Spectral Components | Current C Harmonics | H10 Current C Magnitude RMS | H10 Current C Magnitude RMS | 425260 | F32-4321 | R | 257288584
|  | Spectral Components | Current C Harmonics | H11 Current C Angle | H11 Current C Angle | 425268 | F32-4321 | R | 257288470
|  | Spectral Components | Current C Harmonics | H11 Current C Magnitude | H11 Current C Magnitude | 425264 | F32-4321 | R | 257288469
|  | Spectral Components | Current C Harmonics | H11 Current C Magnitude RMS | H11 Current C Magnitude RMS | 425266 | F32-4321 | R | 257288585
|  | Spectral Components | Current C Harmonics | H12 Current C Angle | H12 Current C Angle | 425274 | F32-4321 | R | 257288472
|  | Spectral Components | Current C Harmonics | H12 Current C Magnitude | H12 Current C Magnitude | 425270 | F32-4321 | R | 257288471
|  | Spectral Components | Current C Harmonics | H12 Current C Magnitude RMS | H12 Current C Magnitude RMS | 425272 | F32-4321 | R | 257288586
|  | Spectral Components | Current C Harmonics | H13 Current C Angle | H13 Current C Angle | 425280 | F32-4321 | R | 257288474
|  | Spectral Components | Current C Harmonics | H13 Current C Magnitude | H13 Current C Magnitude | 425276 | F32-4321 | R | 257288473
|  | Spectral Components | Current C Harmonics | H13 Current C Magnitude RMS | H13 Current C Magnitude RMS | 425278 | F32-4321 | R | 257288587
|  | Spectral Components | Current C Harmonics | H14 Current C Angle | H14 Current C Angle | 425286 | F32-4321 | R | 257288476
|  | Spectral Components | Current C Harmonics | H14 Current C Magnitude | H14 Current C Magnitude | 425282 | F32-4321 | R | 257288475
|  | Spectral Components | Current C Harmonics | H14 Current C Magnitude RMS | H14 Current C Magnitude RMS | 425284 | F32-4321 | R | 257288588
|  | Spectral Components | Current C Harmonics | H15 Current C Angle | H15 Current C Angle | 425292 | F32-4321 | R | 257288478
|  | Spectral Components | Current C Harmonics | H15 Current C Magnitude | H15 Current C Magnitude | 425288 | F32-4321 | R | 257288477
|  | Spectral Components | Current C Harmonics | H15 Current C Magnitude RMS | H15 Current C Magnitude RMS | 425290 | F32-4321 | R | 257288589
|  | Spectral Components | Current C Harmonics | H16 Current C Angle | H16 Current C Angle | 425298 | F32-4321 | R | 257288480
|  | Spectral Components | Current C Harmonics | H16 Current C Magnitude | H16 Current C Magnitude | 425294 | F32-4321 | R | 257288479
|  | Spectral Components | Current C Harmonics | H16 Current C Magnitude RMS | H16 Current C Magnitude RMS | 425296 | F32-4321 | R | 257288590
|  | Spectral Components | Current C Harmonics | H17 Current C Angle | H17 Current C Angle | 425304 | F32-4321 | R | 257288482
|  | Spectral Components | Current C Harmonics | H17 Current C Magnitude | H17 Current C Magnitude | 425300 | F32-4321 | R | 257288481
|  | Spectral Components | Current C Harmonics | H17 Current C Magnitude RMS | H17 Current C Magnitude RMS | 425302 | F32-4321 | R | 257288591
|  | Spectral Components | Current C Harmonics | H18 Current C Angle | H18 Current C Angle | 425310 | F32-4321 | R | 257288484
|  | Spectral Components | Current C Harmonics | H18 Current C Magnitude | H18 Current C Magnitude | 425306 | F32-4321 | R | 257288483
|  | Spectral Components | Current C Harmonics | H18 Current C Magnitude RMS | H18 Current C Magnitude RMS | 425308 | F32-4321 | R | 257288592
|  | Spectral Components | Current C Harmonics | H19 Current C Angle | H19 Current C Angle | 425316 | F32-4321 | R | 257288486
|  | Spectral Components | Current C Harmonics | H19 Current C Magnitude | H19 Current C Magnitude | 425312 | F32-4321 | R | 257288485
|  | Spectral Components | Current C Harmonics | H19 Current C Magnitude RMS | H19 Current C Magnitude RMS | 425314 | F32-4321 | R | 257288593
|  | Spectral Components | Current C Harmonics | H20 Current C Angle | H20 Current C Angle | 425322 | F32-4321 | R | 257288488
|  | Spectral Components | Current C Harmonics | H20 Current C Magnitude | H20 Current C Magnitude | 425318 | F32-4321 | R | 257288487
|  | Spectral Components | Current C Harmonics | H20 Current C Magnitude RMS | H20 Current C Magnitude RMS | 425320 | F32-4321 | R | 257288594
|  | Spectral Components | Current C Harmonics | H21 Current C Angle | H21 Current C Angle | 425328 | F32-4321 | R | 257288490
|  | Spectral Components | Current C Harmonics | H21 Current C Magnitude | H21 Current C Magnitude | 425324 | F32-4321 | R | 257288489
|  | Spectral Components | Current C Harmonics | H21 Current C Magnitude RMS | H21 Current C Magnitude RMS | 425326 | F32-4321 | R | 257288595
|  | Spectral Components | Current C Harmonics | H22 Current C Angle | H22 Current C Angle | 425334 | F32-4321 | R | 257288492
|  | Spectral Components | Current C Harmonics | H22 Current C Magnitude | H22 Current C Magnitude | 425330 | F32-4321 | R | 257288491
|  | Spectral Components | Current C Harmonics | H22 Current C Magnitude RMS | H22 Current C Magnitude RMS | 425332 | F32-4321 | R | 257288596
|  | Spectral Components | Current C Harmonics | H23 Current C Angle | H23 Current C Angle | 425340 | F32-4321 | R | 257288494
|  | Spectral Components | Current C Harmonics | H23 Current C Magnitude | H23 Current C Magnitude | 425336 | F32-4321 | R | 257288493
|  | Spectral Components | Current C Harmonics | H23 Current C Magnitude RMS | H23 Current C Magnitude RMS | 425338 | F32-4321 | R | 257288597
|  | Spectral Components | Current C Harmonics | H24 Current C Angle | H24 Current C Angle | 425346 | F32-4321 | R | 257288496
|  | Spectral Components | Current C Harmonics | H24 Current C Magnitude | H24 Current C Magnitude | 425342 | F32-4321 | R | 257288495
|  | Spectral Components | Current C Harmonics | H24 Current C Magnitude RMS | H24 Current C Magnitude RMS | 425344 | F32-4321 | R | 257288598
|  | Spectral Components | Current C Harmonics | H25 Current C Angle | H25 Current C Angle | 425352 | F32-4321 | R | 257288498
|  | Spectral Components | Current C Harmonics | H25 Current C Magnitude | H25 Current C Magnitude | 425348 | F32-4321 | R | 257288497
|  | Spectral Components | Current C Harmonics | H25 Current C Magnitude RMS | H25 Current C Magnitude RMS | 425350 | F32-4321 | R | 257288599
|  | Spectral Components | Current C Harmonics | H26 Current C Angle | H26 Current C Angle | 425358 | F32-4321 | R | 257288500
|  | Spectral Components | Current C Harmonics | H26 Current C Magnitude | H26 Current C Magnitude | 425354 | F32-4321 | R | 257288499
|  | Spectral Components | Current C Harmonics | H26 Current C Magnitude RMS | H26 Current C Magnitude RMS | 425356 | F32-4321 | R | 257288600
|  | Spectral Components | Current C Harmonics | H27 Current C Angle | H27 Current C Angle | 425364 | F32-4321 | R | 257288502
|  | Spectral Components | Current C Harmonics | H27 Current C Magnitude | H27 Current C Magnitude | 425360 | F32-4321 | R | 257288501
|  | Spectral Components | Current C Harmonics | H27 Current C Magnitude RMS | H27 Current C Magnitude RMS | 425362 | F32-4321 | R | 257288601
|  | Spectral Components | Current C Harmonics | H28 Current C Angle | H28 Current C Angle | 425370 | F32-4321 | R | 257288504
|  | Spectral Components | Current C Harmonics | H28 Current C Magnitude | H28 Current C Magnitude | 425366 | F32-4321 | R | 257288503
|  | Spectral Components | Current C Harmonics | H28 Current C Magnitude RMS | H28 Current C Magnitude RMS | 425368 | F32-4321 | R | 257288602
|  | Spectral Components | Current C Harmonics | H29 Current C Angle | H29 Current C Angle | 425376 | F32-4321 | R | 257288506
|  | Spectral Components | Current C Harmonics | H29 Current C Magnitude | H29 Current C Magnitude | 425372 | F32-4321 | R | 257288505
|  | Spectral Components | Current C Harmonics | H29 Current C Magnitude RMS | H29 Current C Magnitude RMS | 425374 | F32-4321 | R | 257288603
|  | Spectral Components | Current C Harmonics | H30 Current C Angle | H30 Current C Angle | 425382 | F32-4321 | R | 257288508
|  | Spectral Components | Current C Harmonics | H30 Current C Magnitude | H30 Current C Magnitude | 425378 | F32-4321 | R | 257288507
|  | Spectral Components | Current C Harmonics | H30 Current C Magnitude RMS | H30 Current C Magnitude RMS | 425380 | F32-4321 | R | 257288604
|  | Spectral Components | Current C Harmonics | H31 Current C Angle | H31 Current C Angle | 425388 | F32-4321 | R | 257288510
|  | Spectral Components | Current C Harmonics | H31 Current C Magnitude | H31 Current C Magnitude | 425384 | F32-4321 | R | 257288509
|  | Spectral Components | Current C Harmonics | H31 Current C Magnitude RMS | H31 Current C Magnitude RMS | 425386 | F32-4321 | R | 257288605
|  | Spectral Components | Current C Harmonics | H32 Current C Angle | H32 Current C Angle | 425394 | F32-4321 | R | 257288512
|  | Spectral Components | Current C Harmonics | H32 Current C Magnitude | H32 Current C Magnitude | 425390 | F32-4321 | R | 257288511
|  | Spectral Components | Current C Harmonics | H32 Current C Magnitude RMS | H32 Current C Magnitude RMS | 425392 | F32-4321 | R | 257288606
|  | Spectral Components | Current C Harmonics | H33 Current C Angle | H33 Current C Angle | 425400 | F32-4321 | R | 257288514
|  | Spectral Components | Current C Harmonics | H33 Current C Magnitude | H33 Current C Magnitude | 425396 | F32-4321 | R | 257288513
|  | Spectral Components | Current C Harmonics | H33 Current C Magnitude RMS | H33 Current C Magnitude RMS | 425398 | F32-4321 | R | 257288607
|  | Spectral Components | Current C Harmonics | H34 Current C Angle | H34 Current C Angle | 425406 | F32-4321 | R | 257288516
|  | Spectral Components | Current C Harmonics | H34 Current C Magnitude | H34 Current C Magnitude | 425402 | F32-4321 | R | 257288515
|  | Spectral Components | Current C Harmonics | H34 Current C Magnitude RMS | H34 Current C Magnitude RMS | 425404 | F32-4321 | R | 257288608
|  | Spectral Components | Current C Harmonics | H35 Current C Angle | H35 Current C Angle | 425412 | F32-4321 | R | 257288518
|  | Spectral Components | Current C Harmonics | H35 Current C Magnitude | H35 Current C Magnitude | 425408 | F32-4321 | R | 257288517
|  | Spectral Components | Current C Harmonics | H35 Current C Magnitude RMS | H35 Current C Magnitude RMS | 425410 | F32-4321 | R | 257288609
|  | Spectral Components | Current C Harmonics | H36 Current C Angle | H36 Current C Angle | 425418 | F32-4321 | R | 257288520
|  | Spectral Components | Current C Harmonics | H36 Current C Magnitude | H36 Current C Magnitude | 425414 | F32-4321 | R | 257288519
|  | Spectral Components | Current C Harmonics | H36 Current C Magnitude RMS | H36 Current C Magnitude RMS | 425416 | F32-4321 | R | 257288610
|  | Spectral Components | Current C Harmonics | H37 Current C Angle | H37 Current C Angle | 425424 | F32-4321 | R | 257288522
|  | Spectral Components | Current C Harmonics | H37 Current C Magnitude | H37 Current C Magnitude | 425420 | F32-4321 | R | 257288521
|  | Spectral Components | Current C Harmonics | H37 Current C Magnitude RMS | H37 Current C Magnitude RMS | 425422 | F32-4321 | R | 257288611
|  | Spectral Components | Current C Harmonics | H38 Current C Angle | H38 Current C Angle | 425430 | F32-4321 | R | 257288524
|  | Spectral Components | Current C Harmonics | H38 Current C Magnitude | H38 Current C Magnitude | 425426 | F32-4321 | R | 257288523
|  | Spectral Components | Current C Harmonics | H38 Current C Magnitude RMS | H38 Current C Magnitude RMS | 425428 | F32-4321 | R | 257288612
|  | Spectral Components | Current C Harmonics | H39 Current C Angle | H39 Current C Angle | 425436 | F32-4321 | R | 257288526
|  | Spectral Components | Current C Harmonics | H39 Current C Magnitude | H39 Current C Magnitude | 425432 | F32-4321 | R | 257288525
|  | Spectral Components | Current C Harmonics | H39 Current C Magnitude RMS | H39 Current C Magnitude RMS | 425434 | F32-4321 | R | 257288613
|  | Spectral Components | Current C Harmonics | H40 Current C Angle | H40 Current C Angle | 425442 | F32-4321 | R | 257288528
|  | Spectral Components | Current C Harmonics | H40 Current C Magnitude | H40 Current C Magnitude | 425438 | F32-4321 | R | 257288527
|  | Spectral Components | Current C Harmonics | H40 Current C Magnitude RMS | H40 Current C Magnitude RMS | 425440 | F32-4321 | R | 257288614
|  | Spectral Components | Current C Harmonics | H41 Current C Angle | H41 Current C Angle | 425448 | F32-4321 | R | 257288530
|  | Spectral Components | Current C Harmonics | H41 Current C Magnitude | H41 Current C Magnitude | 425444 | F32-4321 | R | 257288529
|  | Spectral Components | Current C Harmonics | H41 Current C Magnitude RMS | H41 Current C Magnitude RMS | 425446 | F32-4321 | R | 257288615
|  | Spectral Components | Current C Harmonics | H42 Current C Angle | H42 Current C Angle | 425454 | F32-4321 | R | 257288532
|  | Spectral Components | Current C Harmonics | H42 Current C Magnitude | H42 Current C Magnitude | 425450 | F32-4321 | R | 257288531
|  | Spectral Components | Current C Harmonics | H42 Current C Magnitude RMS | H42 Current C Magnitude RMS | 425452 | F32-4321 | R | 257288616
|  | Spectral Components | Current C Harmonics | H43 Current C Angle | H43 Current C Angle | 425460 | F32-4321 | R | 257288534
|  | Spectral Components | Current C Harmonics | H43 Current C Magnitude | H43 Current C Magnitude | 425456 | F32-4321 | R | 257288533
|  | Spectral Components | Current C Harmonics | H43 Current C Magnitude RMS | H43 Current C Magnitude RMS | 425458 | F32-4321 | R | 257288617
|  | Spectral Components | Current C Harmonics | H44 Current C Angle | H44 Current C Angle | 425466 | F32-4321 | R | 257288536
|  | Spectral Components | Current C Harmonics | H44 Current C Magnitude | H44 Current C Magnitude | 425462 | F32-4321 | R | 257288535
|  | Spectral Components | Current C Harmonics | H44 Current C Magnitude RMS | H44 Current C Magnitude RMS | 425464 | F32-4321 | R | 257288618
|  | Spectral Components | Current C Harmonics | H45 Current C Angle | H45 Current C Angle | 425472 | F32-4321 | R | 257288538
|  | Spectral Components | Current C Harmonics | H45 Current C Magnitude | H45 Current C Magnitude | 425468 | F32-4321 | R | 257288537
|  | Spectral Components | Current C Harmonics | H45 Current C Magnitude RMS | H45 Current C Magnitude RMS | 425470 | F32-4321 | R | 257288619
|  | Spectral Components | Current C Harmonics | H46 Current C Angle | H46 Current C Angle | 425478 | F32-4321 | R | 257288540
|  | Spectral Components | Current C Harmonics | H46 Current C Magnitude | H46 Current C Magnitude | 425474 | F32-4321 | R | 257288539
|  | Spectral Components | Current C Harmonics | H46 Current C Magnitude RMS | H46 Current C Magnitude RMS | 425476 | F32-4321 | R | 257288620
|  | Spectral Components | Current C Harmonics | H47 Current C Angle | H47 Current C Angle | 425484 | F32-4321 | R | 257288542
|  | Spectral Components | Current C Harmonics | H47 Current C Magnitude | H47 Current C Magnitude | 425480 | F32-4321 | R | 257288541
|  | Spectral Components | Current C Harmonics | H47 Current C Magnitude RMS | H47 Current C Magnitude RMS | 425482 | F32-4321 | R | 257288621
|  | Spectral Components | Current C Harmonics | H48 Current C Angle | H48 Current C Angle | 425490 | F32-4321 | R | 257288544
|  | Spectral Components | Current C Harmonics | H48 Current C Magnitude | H48 Current C Magnitude | 425486 | F32-4321 | R | 257288543
|  | Spectral Components | Current C Harmonics | H48 Current C Magnitude RMS | H48 Current C Magnitude RMS | 425488 | F32-4321 | R | 257288622
|  | Spectral Components | Current C Harmonics | H49 Current C Angle | H49 Current C Angle | 425496 | F32-4321 | R | 257288546
|  | Spectral Components | Current C Harmonics | H49 Current C Magnitude | H49 Current C Magnitude | 425492 | F32-4321 | R | 257288545
|  | Spectral Components | Current C Harmonics | H49 Current C Magnitude RMS | H49 Current C Magnitude RMS | 425494 | F32-4321 | R | 257288623
|  | Spectral Components | Current C Harmonics | H50 Current C Angle | H50 Current C Angle | 425502 | F32-4321 | R | 257288548
|  | Spectral Components | Current C Harmonics | H50 Current C Magnitude | H50 Current C Magnitude | 425498 | F32-4321 | R | 257288547
|  | Spectral Components | Current C Harmonics | H50 Current C Magnitude RMS | H50 Current C Magnitude RMS | 425500 | F32-4321 | R | 257288624
|  | Spectral Components | Current C Harmonics | H51 Current C Angle | H51 Current C Angle | 425508 | F32-4321 | R | 257288550
|  | Spectral Components | Current C Harmonics | H51 Current C Magnitude | H51 Current C Magnitude | 425504 | F32-4321 | R | 257288549
|  | Spectral Components | Current C Harmonics | H51 Current C Magnitude RMS | H51 Current C Magnitude RMS | 425506 | F32-4321 | R | 257288625
|  | Spectral Components | Current C Harmonics | H52 Current C Angle | H52 Current C Angle | 425514 | F32-4321 | R | 257288552
|  | Spectral Components | Current C Harmonics | H52 Current C Magnitude | H52 Current C Magnitude | 425510 | F32-4321 | R | 257288551
|  | Spectral Components | Current C Harmonics | H52 Current C Magnitude RMS | H52 Current C Magnitude RMS | 425512 | F32-4321 | R | 257288626
|  | Spectral Components | Current C Harmonics | H53 Current C Angle | H53 Current C Angle | 425520 | F32-4321 | R | 257288554
|  | Spectral Components | Current C Harmonics | H53 Current C Magnitude | H53 Current C Magnitude | 425516 | F32-4321 | R | 257288553
|  | Spectral Components | Current C Harmonics | H53 Current C Magnitude RMS | H53 Current C Magnitude RMS | 425518 | F32-4321 | R | 257288627
|  | Spectral Components | Current C Harmonics | H54 Current C Angle | H54 Current C Angle | 425526 | F32-4321 | R | 257288556
|  | Spectral Components | Current C Harmonics | H54 Current C Magnitude | H54 Current C Magnitude | 425522 | F32-4321 | R | 257288555
|  | Spectral Components | Current C Harmonics | H54 Current C Magnitude RMS | H54 Current C Magnitude RMS | 425524 | F32-4321 | R | 257288628
|  | Spectral Components | Current C Harmonics | H55 Current C Angle | H55 Current C Angle | 425532 | F32-4321 | R | 257288558
|  | Spectral Components | Current C Harmonics | H55 Current C Magnitude | H55 Current C Magnitude | 425528 | F32-4321 | R | 257288557
|  | Spectral Components | Current C Harmonics | H55 Current C Magnitude RMS | H55 Current C Magnitude RMS | 425530 | F32-4321 | R | 257288629
|  | Spectral Components | Current C Harmonics | H56 Current C Angle | H56 Current C Angle | 425538 | F32-4321 | R | 257288560
|  | Spectral Components | Current C Harmonics | H56 Current C Magnitude | H56 Current C Magnitude | 425534 | F32-4321 | R | 257288559
|  | Spectral Components | Current C Harmonics | H56 Current C Magnitude RMS | H56 Current C Magnitude RMS | 425536 | F32-4321 | R | 257288630
|  | Spectral Components | Current C Harmonics | H57 Current C Angle | H57 Current C Angle | 425544 | F32-4321 | R | 257288562
|  | Spectral Components | Current C Harmonics | H57 Current C Magnitude | H57 Current C Magnitude | 425540 | F32-4321 | R | 257288561
|  | Spectral Components | Current C Harmonics | H57 Current C Magnitude RMS | H57 Current C Magnitude RMS | 425542 | F32-4321 | R | 257288631
|  | Spectral Components | Current C Harmonics | H58 Current C Angle | H58 Current C Angle | 425550 | F32-4321 | R | 257288564
|  | Spectral Components | Current C Harmonics | H58 Current C Magnitude | H58 Current C Magnitude | 425546 | F32-4321 | R | 257288563
|  | Spectral Components | Current C Harmonics | H58 Current C Magnitude RMS | H58 Current C Magnitude RMS | 425548 | F32-4321 | R | 257288632
|  | Spectral Components | Current C Harmonics | H59 Current C Angle | H59 Current C Angle | 425556 | F32-4321 | R | 257288566
|  | Spectral Components | Current C Harmonics | H59 Current C Magnitude | H59 Current C Magnitude | 425552 | F32-4321 | R | 257288565
|  | Spectral Components | Current C Harmonics | H59 Current C Magnitude RMS | H59 Current C Magnitude RMS | 425554 | F32-4321 | R | 257288633
|  | Spectral Components | Current C Harmonics | H60 Current C Angle | H60 Current C Angle | 425562 | F32-4321 | R | 257288568
|  | Spectral Components | Current C Harmonics | H60 Current C Magnitude | H60 Current C Magnitude | 425558 | F32-4321 | R | 257288567
|  | Spectral Components | Current C Harmonics | H60 Current C Magnitude RMS | H60 Current C Magnitude RMS | 425560 | F32-4321 | R | 257288634
|  | Spectral Components | Current C Harmonics | H61 Current C Angle | H61 Current C Angle | 425568 | F32-4321 | R | 257288570
|  | Spectral Components | Current C Harmonics | H61 Current C Magnitude | H61 Current C Magnitude | 425564 | F32-4321 | R | 257288569
|  | Spectral Components | Current C Harmonics | H61 Current C Magnitude RMS | H61 Current C Magnitude RMS | 425566 | F32-4321 | R | 257288635
|  | Spectral Components | Current C Harmonics | H62 Current C Angle | H62 Current C Angle | 425574 | F32-4321 | R | 257288572
|  | Spectral Components | Current C Harmonics | H62 Current C Magnitude | H62 Current C Magnitude | 425570 | F32-4321 | R | 257288571
|  | Spectral Components | Current C Harmonics | H62 Current C Magnitude RMS | H62 Current C Magnitude RMS | 425572 | F32-4321 | R | 257288636
|  | Spectral Components | Current C Harmonics | H63 Current C Angle | H63 Current C Angle | 425580 | F32-4321 | R | 257288574
|  | Spectral Components | Current C Harmonics | H63 Current C Magnitude | H63 Current C Magnitude | 425576 | F32-4321 | R | 257288573
|  | Spectral Components | Current C Harmonics | H63 Current C Magnitude RMS | H63 Current C Magnitude RMS | 425578 | F32-4321 | R | 257288637
|  | Spectral Components | Current G Harmonics | H1 Current G Angle | H1 Current G Angle | 425984 | F32-4321 | R | 257288962
|  | Spectral Components | Current G Harmonics | H1 Current G Magnitude | H1 Current G Magnitude | 425980 | F32-4321 | R | 257288961
|  | Spectral Components | Current G Harmonics | H1 Current G Magnitude RMS | H1 Current G Magnitude RMS | 425982 | F32-4321 | R | 257289087
|  | Spectral Components | Current G Harmonics | H2 Current G Angle | H2 Current G Angle | 425990 | F32-4321 | R | 257288964
|  | Spectral Components | Current G Harmonics | H2 Current G Magnitude | H2 Current G Magnitude | 425986 | F32-4321 | R | 257288963
|  | Spectral Components | Current G Harmonics | H2 Current G Magnitude RMS | H2 Current G Magnitude RMS | 425988 | F32-4321 | R | 257289088
|  | Spectral Components | Current G Harmonics | H3 Current G Angle | H3 Current G Angle | 425996 | F32-4321 | R | 257288966
|  | Spectral Components | Current G Harmonics | H3 Current G Magnitude | H3 Current G Magnitude | 425992 | F32-4321 | R | 257288965
|  | Spectral Components | Current G Harmonics | H3 Current G Magnitude RMS | H3 Current G Magnitude RMS | 425994 | F32-4321 | R | 257289089
|  | Spectral Components | Current G Harmonics | H4 Current G Angle | H4 Current G Angle | 426002 | F32-4321 | R | 257288968
|  | Spectral Components | Current G Harmonics | H4 Current G Magnitude | H4 Current G Magnitude | 425998 | F32-4321 | R | 257288967
|  | Spectral Components | Current G Harmonics | H4 Current G Magnitude RMS | H4 Current G Magnitude RMS | 426000 | F32-4321 | R | 257289090
|  | Spectral Components | Current G Harmonics | H5 Current G Angle | H5 Current G Angle | 426008 | F32-4321 | R | 257288970
|  | Spectral Components | Current G Harmonics | H5 Current G Magnitude | H5 Current G Magnitude | 426004 | F32-4321 | R | 257288969
|  | Spectral Components | Current G Harmonics | H5 Current G Magnitude RMS | H5 Current G Magnitude RMS | 426006 | F32-4321 | R | 257289091
|  | Spectral Components | Current G Harmonics | H6 Current G Angle | H6 Current G Angle | 426014 | F32-4321 | R | 257288972
|  | Spectral Components | Current G Harmonics | H6 Current G Magnitude | H6 Current G Magnitude | 426010 | F32-4321 | R | 257288971
|  | Spectral Components | Current G Harmonics | H6 Current G Magnitude RMS | H6 Current G Magnitude RMS | 426012 | F32-4321 | R | 257289092
|  | Spectral Components | Current G Harmonics | H7 Current G Angle | H7 Current G Angle | 426020 | F32-4321 | R | 257288974
|  | Spectral Components | Current G Harmonics | H7 Current G Magnitude | H7 Current G Magnitude | 426016 | F32-4321 | R | 257288973
|  | Spectral Components | Current G Harmonics | H7 Current G Magnitude RMS | H7 Current G Magnitude RMS | 426018 | F32-4321 | R | 257289093
|  | Spectral Components | Current G Harmonics | H8 Current G Angle | H8 Current G Angle | 426026 | F32-4321 | R | 257288976
|  | Spectral Components | Current G Harmonics | H8 Current G Magnitude | H8 Current G Magnitude | 426022 | F32-4321 | R | 257288975
|  | Spectral Components | Current G Harmonics | H8 Current G Magnitude RMS | H8 Current G Magnitude RMS | 426024 | F32-4321 | R | 257289094
|  | Spectral Components | Current G Harmonics | H9 Current G Angle | H9 Current G Angle | 426032 | F32-4321 | R | 257288978
|  | Spectral Components | Current G Harmonics | H9 Current G Magnitude | H9 Current G Magnitude | 426028 | F32-4321 | R | 257288977
|  | Spectral Components | Current G Harmonics | H9 Current G Magnitude RMS | H9 Current G Magnitude RMS | 426030 | F32-4321 | R | 257289095
|  | Spectral Components | Current G Harmonics | H10 Current G Angle | H10 Current G Angle | 426038 | F32-4321 | R | 257288980
|  | Spectral Components | Current G Harmonics | H10 Current G Magnitude | H10 Current G Magnitude | 426034 | F32-4321 | R | 257288979
|  | Spectral Components | Current G Harmonics | H10 Current G Magnitude RMS | H10 Current G Magnitude RMS | 426036 | F32-4321 | R | 257289096
|  | Spectral Components | Current G Harmonics | H11 Current G Angle | H11 Current G Angle | 426044 | F32-4321 | R | 257288982
|  | Spectral Components | Current G Harmonics | H11 Current G Magnitude | H11 Current G Magnitude | 426040 | F32-4321 | R | 257288981
|  | Spectral Components | Current G Harmonics | H11 Current G Magnitude RMS | H11 Current G Magnitude RMS | 426042 | F32-4321 | R | 257289097
|  | Spectral Components | Current G Harmonics | H12 Current G Angle | H12 Current G Angle | 426050 | F32-4321 | R | 257288984
|  | Spectral Components | Current G Harmonics | H12 Current G Magnitude | H12 Current G Magnitude | 426046 | F32-4321 | R | 257288983
|  | Spectral Components | Current G Harmonics | H12 Current G Magnitude RMS | H12 Current G Magnitude RMS | 426048 | F32-4321 | R | 257289098
|  | Spectral Components | Current G Harmonics | H13 Current G Angle | H13 Current G Angle | 426056 | F32-4321 | R | 257288986
|  | Spectral Components | Current G Harmonics | H13 Current G Magnitude | H13 Current G Magnitude | 426052 | F32-4321 | R | 257288985
|  | Spectral Components | Current G Harmonics | H13 Current G Magnitude RMS | H13 Current G Magnitude RMS | 426054 | F32-4321 | R | 257289099
|  | Spectral Components | Current G Harmonics | H14 Current G Angle | H14 Current G Angle | 426062 | F32-4321 | R | 257288988
|  | Spectral Components | Current G Harmonics | H14 Current G Magnitude | H14 Current G Magnitude | 426058 | F32-4321 | R | 257288987
|  | Spectral Components | Current G Harmonics | H14 Current G Magnitude RMS | H14 Current G Magnitude RMS | 426060 | F32-4321 | R | 257289100
|  | Spectral Components | Current G Harmonics | H15 Current G Angle | H15 Current G Angle | 426068 | F32-4321 | R | 257288990
|  | Spectral Components | Current G Harmonics | H15 Current G Magnitude | H15 Current G Magnitude | 426064 | F32-4321 | R | 257288989
|  | Spectral Components | Current G Harmonics | H15 Current G Magnitude RMS | H15 Current G Magnitude RMS | 426066 | F32-4321 | R | 257289101
|  | Spectral Components | Current G Harmonics | H16 Current G Angle | H16 Current G Angle | 426074 | F32-4321 | R | 257288992
|  | Spectral Components | Current G Harmonics | H16 Current G Magnitude | H16 Current G Magnitude | 426070 | F32-4321 | R | 257288991
|  | Spectral Components | Current G Harmonics | H16 Current G Magnitude RMS | H16 Current G Magnitude RMS | 426072 | F32-4321 | R | 257289102
|  | Spectral Components | Current G Harmonics | H17 Current G Angle | H17 Current G Angle | 426080 | F32-4321 | R | 257288994
|  | Spectral Components | Current G Harmonics | H17 Current G Magnitude | H17 Current G Magnitude | 426076 | F32-4321 | R | 257288993
|  | Spectral Components | Current G Harmonics | H17 Current G Magnitude RMS | H17 Current G Magnitude RMS | 426078 | F32-4321 | R | 257289103
|  | Spectral Components | Current G Harmonics | H18 Current G Angle | H18 Current G Angle | 426086 | F32-4321 | R | 257288996
|  | Spectral Components | Current G Harmonics | H18 Current G Magnitude | H18 Current G Magnitude | 426082 | F32-4321 | R | 257288995
|  | Spectral Components | Current G Harmonics | H18 Current G Magnitude RMS | H18 Current G Magnitude RMS | 426084 | F32-4321 | R | 257289104
|  | Spectral Components | Current G Harmonics | H19 Current G Angle | H19 Current G Angle | 426092 | F32-4321 | R | 257288998
|  | Spectral Components | Current G Harmonics | H19 Current G Magnitude | H19 Current G Magnitude | 426088 | F32-4321 | R | 257288997
|  | Spectral Components | Current G Harmonics | H19 Current G Magnitude RMS | H19 Current G Magnitude RMS | 426090 | F32-4321 | R | 257289105
|  | Spectral Components | Current G Harmonics | H20 Current G Angle | H20 Current G Angle | 426098 | F32-4321 | R | 257289000
|  | Spectral Components | Current G Harmonics | H20 Current G Magnitude | H20 Current G Magnitude | 426094 | F32-4321 | R | 257288999
|  | Spectral Components | Current G Harmonics | H20 Current G Magnitude RMS | H20 Current G Magnitude RMS | 426096 | F32-4321 | R | 257289106
|  | Spectral Components | Current G Harmonics | H21 Current G Angle | H21 Current G Angle | 426104 | F32-4321 | R | 257289002
|  | Spectral Components | Current G Harmonics | H21 Current G Magnitude | H21 Current G Magnitude | 426100 | F32-4321 | R | 257289001
|  | Spectral Components | Current G Harmonics | H21 Current G Magnitude RMS | H21 Current G Magnitude RMS | 426102 | F32-4321 | R | 257289107
|  | Spectral Components | Current G Harmonics | H22 Current G Angle | H22 Current G Angle | 426110 | F32-4321 | R | 257289004
|  | Spectral Components | Current G Harmonics | H22 Current G Magnitude | H22 Current G Magnitude | 426106 | F32-4321 | R | 257289003
|  | Spectral Components | Current G Harmonics | H22 Current G Magnitude RMS | H22 Current G Magnitude RMS | 426108 | F32-4321 | R | 257289108
|  | Spectral Components | Current G Harmonics | H23 Current G Angle | H23 Current G Angle | 426116 | F32-4321 | R | 257289006
|  | Spectral Components | Current G Harmonics | H23 Current G Magnitude | H23 Current G Magnitude | 426112 | F32-4321 | R | 257289005
|  | Spectral Components | Current G Harmonics | H23 Current G Magnitude RMS | H23 Current G Magnitude RMS | 426114 | F32-4321 | R | 257289109
|  | Spectral Components | Current G Harmonics | H24 Current G Angle | H24 Current G Angle | 426122 | F32-4321 | R | 257289008
|  | Spectral Components | Current G Harmonics | H24 Current G Magnitude | H24 Current G Magnitude | 426118 | F32-4321 | R | 257289007
|  | Spectral Components | Current G Harmonics | H24 Current G Magnitude RMS | H24 Current G Magnitude RMS | 426120 | F32-4321 | R | 257289110
|  | Spectral Components | Current G Harmonics | H25 Current G Angle | H25 Current G Angle | 426128 | F32-4321 | R | 257289010
|  | Spectral Components | Current G Harmonics | H25 Current G Magnitude | H25 Current G Magnitude | 426124 | F32-4321 | R | 257289009
|  | Spectral Components | Current G Harmonics | H25 Current G Magnitude RMS | H25 Current G Magnitude RMS | 426126 | F32-4321 | R | 257289111
|  | Spectral Components | Current G Harmonics | H26 Current G Angle | H26 Current G Angle | 426134 | F32-4321 | R | 257289012
|  | Spectral Components | Current G Harmonics | H26 Current G Magnitude | H26 Current G Magnitude | 426130 | F32-4321 | R | 257289011
|  | Spectral Components | Current G Harmonics | H26 Current G Magnitude RMS | H26 Current G Magnitude RMS | 426132 | F32-4321 | R | 257289112
|  | Spectral Components | Current G Harmonics | H27 Current G Angle | H27 Current G Angle | 426140 | F32-4321 | R | 257289014
|  | Spectral Components | Current G Harmonics | H27 Current G Magnitude | H27 Current G Magnitude | 426136 | F32-4321 | R | 257289013
|  | Spectral Components | Current G Harmonics | H27 Current G Magnitude RMS | H27 Current G Magnitude RMS | 426138 | F32-4321 | R | 257289113
|  | Spectral Components | Current G Harmonics | H28 Current G Angle | H28 Current G Angle | 426146 | F32-4321 | R | 257289016
|  | Spectral Components | Current G Harmonics | H28 Current G Magnitude | H28 Current G Magnitude | 426142 | F32-4321 | R | 257289015
|  | Spectral Components | Current G Harmonics | H28 Current G Magnitude RMS | H28 Current G Magnitude RMS | 426144 | F32-4321 | R | 257289114
|  | Spectral Components | Current G Harmonics | H29 Current G Angle | H29 Current G Angle | 426152 | F32-4321 | R | 257289018
|  | Spectral Components | Current G Harmonics | H29 Current G Magnitude | H29 Current G Magnitude | 426148 | F32-4321 | R | 257289017
|  | Spectral Components | Current G Harmonics | H29 Current G Magnitude RMS | H29 Current G Magnitude RMS | 426150 | F32-4321 | R | 257289115
|  | Spectral Components | Current G Harmonics | H30 Current G Angle | H30 Current G Angle | 426158 | F32-4321 | R | 257289020
|  | Spectral Components | Current G Harmonics | H30 Current G Magnitude | H30 Current G Magnitude | 426154 | F32-4321 | R | 257289019
|  | Spectral Components | Current G Harmonics | H30 Current G Magnitude RMS | H30 Current G Magnitude RMS | 426156 | F32-4321 | R | 257289116
|  | Spectral Components | Current G Harmonics | H31 Current G Angle | H31 Current G Angle | 426164 | F32-4321 | R | 257289022
|  | Spectral Components | Current G Harmonics | H31 Current G Magnitude | H31 Current G Magnitude | 426160 | F32-4321 | R | 257289021
|  | Spectral Components | Current G Harmonics | H31 Current G Magnitude RMS | H31 Current G Magnitude RMS | 426162 | F32-4321 | R | 257289117
|  | Spectral Components | Current G Harmonics | H32 Current G Angle | H32 Current G Angle | 426170 | F32-4321 | R | 257289024
|  | Spectral Components | Current G Harmonics | H32 Current G Magnitude | H32 Current G Magnitude | 426166 | F32-4321 | R | 257289023
|  | Spectral Components | Current G Harmonics | H32 Current G Magnitude RMS | H32 Current G Magnitude RMS | 426168 | F32-4321 | R | 257289118
|  | Spectral Components | Current G Harmonics | H33 Current G Angle | H33 Current G Angle | 426176 | F32-4321 | R | 257289026
|  | Spectral Components | Current G Harmonics | H33 Current G Magnitude | H33 Current G Magnitude | 426172 | F32-4321 | R | 257289025
|  | Spectral Components | Current G Harmonics | H33 Current G Magnitude RMS | H33 Current G Magnitude RMS | 426174 | F32-4321 | R | 257289119
|  | Spectral Components | Current G Harmonics | H34 Current G Angle | H34 Current G Angle | 426182 | F32-4321 | R | 257289028
|  | Spectral Components | Current G Harmonics | H34 Current G Magnitude | H34 Current G Magnitude | 426178 | F32-4321 | R | 257289027
|  | Spectral Components | Current G Harmonics | H34 Current G Magnitude RMS | H34 Current G Magnitude RMS | 426180 | F32-4321 | R | 257289120
|  | Spectral Components | Current G Harmonics | H35 Current G Angle | H35 Current G Angle | 426188 | F32-4321 | R | 257289030
|  | Spectral Components | Current G Harmonics | H35 Current G Magnitude | H35 Current G Magnitude | 426184 | F32-4321 | R | 257289029
|  | Spectral Components | Current G Harmonics | H35 Current G Magnitude RMS | H35 Current G Magnitude RMS | 426186 | F32-4321 | R | 257289121
|  | Spectral Components | Current G Harmonics | H36 Current G Angle | H36 Current G Angle | 426194 | F32-4321 | R | 257289032
|  | Spectral Components | Current G Harmonics | H36 Current G Magnitude | H36 Current G Magnitude | 426190 | F32-4321 | R | 257289031
|  | Spectral Components | Current G Harmonics | H36 Current G Magnitude RMS | H36 Current G Magnitude RMS | 426192 | F32-4321 | R | 257289122
|  | Spectral Components | Current G Harmonics | H37 Current G Angle | H37 Current G Angle | 426200 | F32-4321 | R | 257289034
|  | Spectral Components | Current G Harmonics | H37 Current G Magnitude | H37 Current G Magnitude | 426196 | F32-4321 | R | 257289033
|  | Spectral Components | Current G Harmonics | H37 Current G Magnitude RMS | H37 Current G Magnitude RMS | 426198 | F32-4321 | R | 257289123
|  | Spectral Components | Current G Harmonics | H38 Current G Angle | H38 Current G Angle | 426206 | F32-4321 | R | 257289036
|  | Spectral Components | Current G Harmonics | H38 Current G Magnitude | H38 Current G Magnitude | 426202 | F32-4321 | R | 257289035
|  | Spectral Components | Current G Harmonics | H38 Current G Magnitude RMS | H38 Current G Magnitude RMS | 426204 | F32-4321 | R | 257289124
|  | Spectral Components | Current G Harmonics | H39 Current G Angle | H39 Current G Angle | 426212 | F32-4321 | R | 257289038
|  | Spectral Components | Current G Harmonics | H39 Current G Magnitude | H39 Current G Magnitude | 426208 | F32-4321 | R | 257289037
|  | Spectral Components | Current G Harmonics | H39 Current G Magnitude RMS | H39 Current G Magnitude RMS | 426210 | F32-4321 | R | 257289125
|  | Spectral Components | Current G Harmonics | H40 Current G Angle | H40 Current G Angle | 426218 | F32-4321 | R | 257289040
|  | Spectral Components | Current G Harmonics | H40 Current G Magnitude | H40 Current G Magnitude | 426214 | F32-4321 | R | 257289039
|  | Spectral Components | Current G Harmonics | H40 Current G Magnitude RMS | H40 Current G Magnitude RMS | 426216 | F32-4321 | R | 257289126
|  | Spectral Components | Current G Harmonics | H41 Current G Angle | H41 Current G Angle | 426224 | F32-4321 | R | 257289042
|  | Spectral Components | Current G Harmonics | H41 Current G Magnitude | H41 Current G Magnitude | 426220 | F32-4321 | R | 257289041
|  | Spectral Components | Current G Harmonics | H41 Current G Magnitude RMS | H41 Current G Magnitude RMS | 426222 | F32-4321 | R | 257289127
|  | Spectral Components | Current G Harmonics | H42 Current G Angle | H42 Current G Angle | 426230 | F32-4321 | R | 257289044
|  | Spectral Components | Current G Harmonics | H42 Current G Magnitude | H42 Current G Magnitude | 426226 | F32-4321 | R | 257289043
|  | Spectral Components | Current G Harmonics | H42 Current G Magnitude RMS | H42 Current G Magnitude RMS | 426228 | F32-4321 | R | 257289128
|  | Spectral Components | Current G Harmonics | H43 Current G Angle | H43 Current G Angle | 426236 | F32-4321 | R | 257289046
|  | Spectral Components | Current G Harmonics | H43 Current G Magnitude | H43 Current G Magnitude | 426232 | F32-4321 | R | 257289045
|  | Spectral Components | Current G Harmonics | H43 Current G Magnitude RMS | H43 Current G Magnitude RMS | 426234 | F32-4321 | R | 257289129
|  | Spectral Components | Current G Harmonics | H44 Current G Angle | H44 Current G Angle | 426242 | F32-4321 | R | 257289048
|  | Spectral Components | Current G Harmonics | H44 Current G Magnitude | H44 Current G Magnitude | 426238 | F32-4321 | R | 257289047
|  | Spectral Components | Current G Harmonics | H44 Current G Magnitude RMS | H44 Current G Magnitude RMS | 426240 | F32-4321 | R | 257289130
|  | Spectral Components | Current G Harmonics | H45 Current G Angle | H45 Current G Angle | 426248 | F32-4321 | R | 257289050
|  | Spectral Components | Current G Harmonics | H45 Current G Magnitude | H45 Current G Magnitude | 426244 | F32-4321 | R | 257289049
|  | Spectral Components | Current G Harmonics | H45 Current G Magnitude RMS | H45 Current G Magnitude RMS | 426246 | F32-4321 | R | 257289131
|  | Spectral Components | Current G Harmonics | H46 Current G Angle | H46 Current G Angle | 426254 | F32-4321 | R | 257289052
|  | Spectral Components | Current G Harmonics | H46 Current G Magnitude | H46 Current G Magnitude | 426250 | F32-4321 | R | 257289051
|  | Spectral Components | Current G Harmonics | H46 Current G Magnitude RMS | H46 Current G Magnitude RMS | 426252 | F32-4321 | R | 257289132
|  | Spectral Components | Current G Harmonics | H47 Current G Angle | H47 Current G Angle | 426260 | F32-4321 | R | 257289054
|  | Spectral Components | Current G Harmonics | H47 Current G Magnitude | H47 Current G Magnitude | 426256 | F32-4321 | R | 257289053
|  | Spectral Components | Current G Harmonics | H47 Current G Magnitude RMS | H47 Current G Magnitude RMS | 426258 | F32-4321 | R | 257289133
|  | Spectral Components | Current G Harmonics | H48 Current G Angle | H48 Current G Angle | 426266 | F32-4321 | R | 257289056
|  | Spectral Components | Current G Harmonics | H48 Current G Magnitude | H48 Current G Magnitude | 426262 | F32-4321 | R | 257289055
|  | Spectral Components | Current G Harmonics | H48 Current G Magnitude RMS | H48 Current G Magnitude RMS | 426264 | F32-4321 | R | 257289134
|  | Spectral Components | Current G Harmonics | H49 Current G Angle | H49 Current G Angle | 426272 | F32-4321 | R | 257289058
|  | Spectral Components | Current G Harmonics | H49 Current G Magnitude | H49 Current G Magnitude | 426268 | F32-4321 | R | 257289057
|  | Spectral Components | Current G Harmonics | H49 Current G Magnitude RMS | H49 Current G Magnitude RMS | 426270 | F32-4321 | R | 257289135
|  | Spectral Components | Current G Harmonics | H50 Current G Angle | H50 Current G Angle | 426278 | F32-4321 | R | 257289060
|  | Spectral Components | Current G Harmonics | H50 Current G Magnitude | H50 Current G Magnitude | 426274 | F32-4321 | R | 257289059
|  | Spectral Components | Current G Harmonics | H50 Current G Magnitude RMS | H50 Current G Magnitude RMS | 426276 | F32-4321 | R | 257289136
|  | Spectral Components | Current G Harmonics | H51 Current G Angle | H51 Current G Angle | 426284 | F32-4321 | R | 257289062
|  | Spectral Components | Current G Harmonics | H51 Current G Magnitude | H51 Current G Magnitude | 426280 | F32-4321 | R | 257289061
|  | Spectral Components | Current G Harmonics | H51 Current G Magnitude RMS | H51 Current G Magnitude RMS | 426282 | F32-4321 | R | 257289137
|  | Spectral Components | Current G Harmonics | H52 Current G Angle | H52 Current G Angle | 426290 | F32-4321 | R | 257289064
|  | Spectral Components | Current G Harmonics | H52 Current G Magnitude | H52 Current G Magnitude | 426286 | F32-4321 | R | 257289063
|  | Spectral Components | Current G Harmonics | H52 Current G Magnitude RMS | H52 Current G Magnitude RMS | 426288 | F32-4321 | R | 257289138
|  | Spectral Components | Current G Harmonics | H53 Current G Angle | H53 Current G Angle | 426296 | F32-4321 | R | 257289066
|  | Spectral Components | Current G Harmonics | H53 Current G Magnitude | H53 Current G Magnitude | 426292 | F32-4321 | R | 257289065
|  | Spectral Components | Current G Harmonics | H53 Current G Magnitude RMS | H53 Current G Magnitude RMS | 426294 | F32-4321 | R | 257289139
|  | Spectral Components | Current G Harmonics | H54 Current G Angle | H54 Current G Angle | 426302 | F32-4321 | R | 257289068
|  | Spectral Components | Current G Harmonics | H54 Current G Magnitude | H54 Current G Magnitude | 426298 | F32-4321 | R | 257289067
|  | Spectral Components | Current G Harmonics | H54 Current G Magnitude RMS | H54 Current G Magnitude RMS | 426300 | F32-4321 | R | 257289140
|  | Spectral Components | Current G Harmonics | H55 Current G Angle | H55 Current G Angle | 426308 | F32-4321 | R | 257289070
|  | Spectral Components | Current G Harmonics | H55 Current G Magnitude | H55 Current G Magnitude | 426304 | F32-4321 | R | 257289069
|  | Spectral Components | Current G Harmonics | H55 Current G Magnitude RMS | H55 Current G Magnitude RMS | 426306 | F32-4321 | R | 257289141
|  | Spectral Components | Current G Harmonics | H56 Current G Angle | H56 Current G Angle | 426314 | F32-4321 | R | 257289072
|  | Spectral Components | Current G Harmonics | H56 Current G Magnitude | H56 Current G Magnitude | 426310 | F32-4321 | R | 257289071
|  | Spectral Components | Current G Harmonics | H56 Current G Magnitude RMS | H56 Current G Magnitude RMS | 426312 | F32-4321 | R | 257289142
|  | Spectral Components | Current G Harmonics | H57 Current G Angle | H57 Current G Angle | 426320 | F32-4321 | R | 257289074
|  | Spectral Components | Current G Harmonics | H57 Current G Magnitude | H57 Current G Magnitude | 426316 | F32-4321 | R | 257289073
|  | Spectral Components | Current G Harmonics | H57 Current G Magnitude RMS | H57 Current G Magnitude RMS | 426318 | F32-4321 | R | 257289143
|  | Spectral Components | Current G Harmonics | H58 Current G Angle | H58 Current G Angle | 426326 | F32-4321 | R | 257289076
|  | Spectral Components | Current G Harmonics | H58 Current G Magnitude | H58 Current G Magnitude | 426322 | F32-4321 | R | 257289075
|  | Spectral Components | Current G Harmonics | H58 Current G Magnitude RMS | H58 Current G Magnitude RMS | 426324 | F32-4321 | R | 257289144
|  | Spectral Components | Current G Harmonics | H59 Current G Angle | H59 Current G Angle | 426332 | F32-4321 | R | 257289078
|  | Spectral Components | Current G Harmonics | H59 Current G Magnitude | H59 Current G Magnitude | 426328 | F32-4321 | R | 257289077
|  | Spectral Components | Current G Harmonics | H59 Current G Magnitude RMS | H59 Current G Magnitude RMS | 426330 | F32-4321 | R | 257289145
|  | Spectral Components | Current G Harmonics | H60 Current G Angle | H60 Current G Angle | 426338 | F32-4321 | R | 257289080
|  | Spectral Components | Current G Harmonics | H60 Current G Magnitude | H60 Current G Magnitude | 426334 | F32-4321 | R | 257289079
|  | Spectral Components | Current G Harmonics | H60 Current G Magnitude RMS | H60 Current G Magnitude RMS | 426336 | F32-4321 | R | 257289146
|  | Spectral Components | Current G Harmonics | H61 Current G Angle | H61 Current G Angle | 426344 | F32-4321 | R | 257289082
|  | Spectral Components | Current G Harmonics | H61 Current G Magnitude | H61 Current G Magnitude | 426340 | F32-4321 | R | 257289081
|  | Spectral Components | Current G Harmonics | H61 Current G Magnitude RMS | H61 Current G Magnitude RMS | 426342 | F32-4321 | R | 257289147
|  | Spectral Components | Current G Harmonics | H62 Current G Angle | H62 Current G Angle | 426350 | F32-4321 | R | 257289084
|  | Spectral Components | Current G Harmonics | H62 Current G Magnitude | H62 Current G Magnitude | 426346 | F32-4321 | R | 257289083
|  | Spectral Components | Current G Harmonics | H62 Current G Magnitude RMS | H62 Current G Magnitude RMS | 426348 | F32-4321 | R | 257289148
|  | Spectral Components | Current G Harmonics | H63 Current G Angle | H63 Current G Angle | 426356 | F32-4321 | R | 257289086
|  | Spectral Components | Current G Harmonics | H63 Current G Magnitude | H63 Current G Magnitude | 426352 | F32-4321 | R | 257289085
|  | Spectral Components | Current G Harmonics | H63 Current G Magnitude RMS | H63 Current G Magnitude RMS | 426354 | F32-4321 | R | 257289149
|  | Spectral Components | Current N Harmonics | H1 Current N Angle | H1 Current N Angle | 425596 | F32-4321 | R | 257288706
|  | Spectral Components | Current N Harmonics | H1 Current N Magnitude | H1 Current N Magnitude | 425592 | F32-4321 | R | 257288705
|  | Spectral Components | Current N Harmonics | H1 Current N Magnitude RMS | H1 Current N Magnitude RMS | 425594 | F32-4321 | R | 257288831
|  | Spectral Components | Current N Harmonics | H2 Current N Angle | H2 Current N Angle | 425602 | F32-4321 | R | 257288708
|  | Spectral Components | Current N Harmonics | H2 Current N Magnitude | H2 Current N Magnitude | 425598 | F32-4321 | R | 257288707
|  | Spectral Components | Current N Harmonics | H2 Current N Magnitude RMS | H2 Current N Magnitude RMS | 425600 | F32-4321 | R | 257288832
|  | Spectral Components | Current N Harmonics | H3 Current N Angle | H3 Current N Angle | 425608 | F32-4321 | R | 257288710
|  | Spectral Components | Current N Harmonics | H3 Current N Magnitude | H3 Current N Magnitude | 425604 | F32-4321 | R | 257288709
|  | Spectral Components | Current N Harmonics | H3 Current N Magnitude RMS | H3 Current N Magnitude RMS | 425606 | F32-4321 | R | 257288833
|  | Spectral Components | Current N Harmonics | H4 Current N Angle | H4 Current N Angle | 425614 | F32-4321 | R | 257288712
|  | Spectral Components | Current N Harmonics | H4 Current N Magnitude | H4 Current N Magnitude | 425610 | F32-4321 | R | 257288711
|  | Spectral Components | Current N Harmonics | H4 Current N Magnitude RMS | H4 Current N Magnitude RMS | 425612 | F32-4321 | R | 257288834
|  | Spectral Components | Current N Harmonics | H5 Current N Angle | H5 Current N Angle | 425620 | F32-4321 | R | 257288714
|  | Spectral Components | Current N Harmonics | H5 Current N Magnitude | H5 Current N Magnitude | 425616 | F32-4321 | R | 257288713
|  | Spectral Components | Current N Harmonics | H5 Current N Magnitude RMS | H5 Current N Magnitude RMS | 425618 | F32-4321 | R | 257288835
|  | Spectral Components | Current N Harmonics | H6 Current N Angle | H6 Current N Angle | 425626 | F32-4321 | R | 257288716
|  | Spectral Components | Current N Harmonics | H6 Current N Magnitude | H6 Current N Magnitude | 425622 | F32-4321 | R | 257288715
|  | Spectral Components | Current N Harmonics | H6 Current N Magnitude RMS | H6 Current N Magnitude RMS | 425624 | F32-4321 | R | 257288836
|  | Spectral Components | Current N Harmonics | H7 Current N Angle | H7 Current N Angle | 425632 | F32-4321 | R | 257288718
|  | Spectral Components | Current N Harmonics | H7 Current N Magnitude | H7 Current N Magnitude | 425628 | F32-4321 | R | 257288717
|  | Spectral Components | Current N Harmonics | H7 Current N Magnitude RMS | H7 Current N Magnitude RMS | 425630 | F32-4321 | R | 257288837
|  | Spectral Components | Current N Harmonics | H8 Current N Angle | H8 Current N Angle | 425638 | F32-4321 | R | 257288720
|  | Spectral Components | Current N Harmonics | H8 Current N Magnitude | H8 Current N Magnitude | 425634 | F32-4321 | R | 257288719
|  | Spectral Components | Current N Harmonics | H8 Current N Magnitude RMS | H8 Current N Magnitude RMS | 425636 | F32-4321 | R | 257288838
|  | Spectral Components | Current N Harmonics | H9 Current N Angle | H9 Current N Angle | 425644 | F32-4321 | R | 257288722
|  | Spectral Components | Current N Harmonics | H9 Current N Magnitude | H9 Current N Magnitude | 425640 | F32-4321 | R | 257288721
|  | Spectral Components | Current N Harmonics | H9 Current N Magnitude RMS | H9 Current N Magnitude RMS | 425642 | F32-4321 | R | 257288839
|  | Spectral Components | Current N Harmonics | H10 Current N Angle | H10 Current N Angle | 425650 | F32-4321 | R | 257288724
|  | Spectral Components | Current N Harmonics | H10 Current N Magnitude | H10 Current N Magnitude | 425646 | F32-4321 | R | 257288723
|  | Spectral Components | Current N Harmonics | H10 Current N Magnitude RMS | H10 Current N Magnitude RMS | 425648 | F32-4321 | R | 257288840
|  | Spectral Components | Current N Harmonics | H11 Current N Angle | H11 Current N Angle | 425656 | F32-4321 | R | 257288726
|  | Spectral Components | Current N Harmonics | H11 Current N Magnitude | H11 Current N Magnitude | 425652 | F32-4321 | R | 257288725
|  | Spectral Components | Current N Harmonics | H11 Current N Magnitude RMS | H11 Current N Magnitude RMS | 425654 | F32-4321 | R | 257288841
|  | Spectral Components | Current N Harmonics | H12 Current N Angle | H12 Current N Angle | 425662 | F32-4321 | R | 257288728
|  | Spectral Components | Current N Harmonics | H12 Current N Magnitude | H12 Current N Magnitude | 425658 | F32-4321 | R | 257288727
|  | Spectral Components | Current N Harmonics | H12 Current N Magnitude RMS | H12 Current N Magnitude RMS | 425660 | F32-4321 | R | 257288842
|  | Spectral Components | Current N Harmonics | H13 Current N Angle | H13 Current N Angle | 425668 | F32-4321 | R | 257288730
|  | Spectral Components | Current N Harmonics | H13 Current N Magnitude | H13 Current N Magnitude | 425664 | F32-4321 | R | 257288729
|  | Spectral Components | Current N Harmonics | H13 Current N Magnitude RMS | H13 Current N Magnitude RMS | 425666 | F32-4321 | R | 257288843
|  | Spectral Components | Current N Harmonics | H14 Current N Angle | H14 Current N Angle | 425674 | F32-4321 | R | 257288732
|  | Spectral Components | Current N Harmonics | H14 Current N Magnitude | H14 Current N Magnitude | 425670 | F32-4321 | R | 257288731
|  | Spectral Components | Current N Harmonics | H14 Current N Magnitude RMS | H14 Current N Magnitude RMS | 425672 | F32-4321 | R | 257288844
|  | Spectral Components | Current N Harmonics | H15 Current N Angle | H15 Current N Angle | 425680 | F32-4321 | R | 257288734
|  | Spectral Components | Current N Harmonics | H15 Current N Magnitude | H15 Current N Magnitude | 425676 | F32-4321 | R | 257288733
|  | Spectral Components | Current N Harmonics | H15 Current N Magnitude RMS | H15 Current N Magnitude RMS | 425678 | F32-4321 | R | 257288845
|  | Spectral Components | Current N Harmonics | H16 Current N Angle | H16 Current N Angle | 425686 | F32-4321 | R | 257288736
|  | Spectral Components | Current N Harmonics | H16 Current N Magnitude | H16 Current N Magnitude | 425682 | F32-4321 | R | 257288735
|  | Spectral Components | Current N Harmonics | H16 Current N Magnitude RMS | H16 Current N Magnitude RMS | 425684 | F32-4321 | R | 257288846
|  | Spectral Components | Current N Harmonics | H17 Current N Angle | H17 Current N Angle | 425692 | F32-4321 | R | 257288738
|  | Spectral Components | Current N Harmonics | H17 Current N Magnitude | H17 Current N Magnitude | 425688 | F32-4321 | R | 257288737
|  | Spectral Components | Current N Harmonics | H17 Current N Magnitude RMS | H17 Current N Magnitude RMS | 425690 | F32-4321 | R | 257288847
|  | Spectral Components | Current N Harmonics | H18 Current N Angle | H18 Current N Angle | 425698 | F32-4321 | R | 257288740
|  | Spectral Components | Current N Harmonics | H18 Current N Magnitude | H18 Current N Magnitude | 425694 | F32-4321 | R | 257288739
|  | Spectral Components | Current N Harmonics | H18 Current N Magnitude RMS | H18 Current N Magnitude RMS | 425696 | F32-4321 | R | 257288848
|  | Spectral Components | Current N Harmonics | H19 Current N Angle | H19 Current N Angle | 425704 | F32-4321 | R | 257288742
|  | Spectral Components | Current N Harmonics | H19 Current N Magnitude | H19 Current N Magnitude | 425700 | F32-4321 | R | 257288741
|  | Spectral Components | Current N Harmonics | H19 Current N Magnitude RMS | H19 Current N Magnitude RMS | 425702 | F32-4321 | R | 257288849
|  | Spectral Components | Current N Harmonics | H20 Current N Angle | H20 Current N Angle | 425710 | F32-4321 | R | 257288744
|  | Spectral Components | Current N Harmonics | H20 Current N Magnitude | H20 Current N Magnitude | 425706 | F32-4321 | R | 257288743
|  | Spectral Components | Current N Harmonics | H20 Current N Magnitude RMS | H20 Current N Magnitude RMS | 425708 | F32-4321 | R | 257288850
|  | Spectral Components | Current N Harmonics | H21 Current N Angle | H21 Current N Angle | 425716 | F32-4321 | R | 257288746
|  | Spectral Components | Current N Harmonics | H21 Current N Magnitude | H21 Current N Magnitude | 425712 | F32-4321 | R | 257288745
|  | Spectral Components | Current N Harmonics | H21 Current N Magnitude RMS | H21 Current N Magnitude RMS | 425714 | F32-4321 | R | 257288851
|  | Spectral Components | Current N Harmonics | H22 Current N Angle | H22 Current N Angle | 425722 | F32-4321 | R | 257288748
|  | Spectral Components | Current N Harmonics | H22 Current N Magnitude | H22 Current N Magnitude | 425718 | F32-4321 | R | 257288747
|  | Spectral Components | Current N Harmonics | H22 Current N Magnitude RMS | H22 Current N Magnitude RMS | 425720 | F32-4321 | R | 257288852
|  | Spectral Components | Current N Harmonics | H23 Current N Angle | H23 Current N Angle | 425728 | F32-4321 | R | 257288750
|  | Spectral Components | Current N Harmonics | H23 Current N Magnitude | H23 Current N Magnitude | 425724 | F32-4321 | R | 257288749
|  | Spectral Components | Current N Harmonics | H23 Current N Magnitude RMS | H23 Current N Magnitude RMS | 425726 | F32-4321 | R | 257288853
|  | Spectral Components | Current N Harmonics | H24 Current N Angle | H24 Current N Angle | 425734 | F32-4321 | R | 257288752
|  | Spectral Components | Current N Harmonics | H24 Current N Magnitude | H24 Current N Magnitude | 425730 | F32-4321 | R | 257288751
|  | Spectral Components | Current N Harmonics | H24 Current N Magnitude RMS | H24 Current N Magnitude RMS | 425732 | F32-4321 | R | 257288854
|  | Spectral Components | Current N Harmonics | H25 Current N Angle | H25 Current N Angle | 425740 | F32-4321 | R | 257288754
|  | Spectral Components | Current N Harmonics | H25 Current N Magnitude | H25 Current N Magnitude | 425736 | F32-4321 | R | 257288753
|  | Spectral Components | Current N Harmonics | H25 Current N Magnitude RMS | H25 Current N Magnitude RMS | 425738 | F32-4321 | R | 257288855
|  | Spectral Components | Current N Harmonics | H26 Current N Angle | H26 Current N Angle | 425746 | F32-4321 | R | 257288756
|  | Spectral Components | Current N Harmonics | H26 Current N Magnitude | H26 Current N Magnitude | 425742 | F32-4321 | R | 257288755
|  | Spectral Components | Current N Harmonics | H26 Current N Magnitude RMS | H26 Current N Magnitude RMS | 425744 | F32-4321 | R | 257288856
|  | Spectral Components | Current N Harmonics | H27 Current N Angle | H27 Current N Angle | 425752 | F32-4321 | R | 257288758
|  | Spectral Components | Current N Harmonics | H27 Current N Magnitude | H27 Current N Magnitude | 425748 | F32-4321 | R | 257288757
|  | Spectral Components | Current N Harmonics | H27 Current N Magnitude RMS | H27 Current N Magnitude RMS | 425750 | F32-4321 | R | 257288857
|  | Spectral Components | Current N Harmonics | H28 Current N Angle | H28 Current N Angle | 425758 | F32-4321 | R | 257288760
|  | Spectral Components | Current N Harmonics | H28 Current N Magnitude | H28 Current N Magnitude | 425754 | F32-4321 | R | 257288759
|  | Spectral Components | Current N Harmonics | H28 Current N Magnitude RMS | H28 Current N Magnitude RMS | 425756 | F32-4321 | R | 257288858
|  | Spectral Components | Current N Harmonics | H29 Current N Angle | H29 Current N Angle | 425764 | F32-4321 | R | 257288762
|  | Spectral Components | Current N Harmonics | H29 Current N Magnitude | H29 Current N Magnitude | 425760 | F32-4321 | R | 257288761
|  | Spectral Components | Current N Harmonics | H29 Current N Magnitude RMS | H29 Current N Magnitude RMS | 425762 | F32-4321 | R | 257288859
|  | Spectral Components | Current N Harmonics | H30 Current N Angle | H30 Current N Angle | 425770 | F32-4321 | R | 257288764
|  | Spectral Components | Current N Harmonics | H30 Current N Magnitude | H30 Current N Magnitude | 425766 | F32-4321 | R | 257288763
|  | Spectral Components | Current N Harmonics | H30 Current N Magnitude RMS | H30 Current N Magnitude RMS | 425768 | F32-4321 | R | 257288860
|  | Spectral Components | Current N Harmonics | H31 Current N Angle | H31 Current N Angle | 425776 | F32-4321 | R | 257288766
|  | Spectral Components | Current N Harmonics | H31 Current N Magnitude | H31 Current N Magnitude | 425772 | F32-4321 | R | 257288765
|  | Spectral Components | Current N Harmonics | H31 Current N Magnitude RMS | H31 Current N Magnitude RMS | 425774 | F32-4321 | R | 257288861
|  | Spectral Components | Current N Harmonics | H32 Current N Angle | H32 Current N Angle | 425782 | F32-4321 | R | 257288768
|  | Spectral Components | Current N Harmonics | H32 Current N Magnitude | H32 Current N Magnitude | 425778 | F32-4321 | R | 257288767
|  | Spectral Components | Current N Harmonics | H32 Current N Magnitude RMS | H32 Current N Magnitude RMS | 425780 | F32-4321 | R | 257288862
|  | Spectral Components | Current N Harmonics | H33 Current N Angle | H33 Current N Angle | 425788 | F32-4321 | R | 257288770
|  | Spectral Components | Current N Harmonics | H33 Current N Magnitude | H33 Current N Magnitude | 425784 | F32-4321 | R | 257288769
|  | Spectral Components | Current N Harmonics | H33 Current N Magnitude RMS | H33 Current N Magnitude RMS | 425786 | F32-4321 | R | 257288863
|  | Spectral Components | Current N Harmonics | H34 Current N Angle | H34 Current N Angle | 425794 | F32-4321 | R | 257288772
|  | Spectral Components | Current N Harmonics | H34 Current N Magnitude | H34 Current N Magnitude | 425790 | F32-4321 | R | 257288771
|  | Spectral Components | Current N Harmonics | H34 Current N Magnitude RMS | H34 Current N Magnitude RMS | 425792 | F32-4321 | R | 257288864
|  | Spectral Components | Current N Harmonics | H35 Current N Angle | H35 Current N Angle | 425800 | F32-4321 | R | 257288774
|  | Spectral Components | Current N Harmonics | H35 Current N Magnitude | H35 Current N Magnitude | 425796 | F32-4321 | R | 257288773
|  | Spectral Components | Current N Harmonics | H35 Current N Magnitude RMS | H35 Current N Magnitude RMS | 425798 | F32-4321 | R | 257288865
|  | Spectral Components | Current N Harmonics | H36 Current N Angle | H36 Current N Angle | 425806 | F32-4321 | R | 257288776
|  | Spectral Components | Current N Harmonics | H36 Current N Magnitude | H36 Current N Magnitude | 425802 | F32-4321 | R | 257288775
|  | Spectral Components | Current N Harmonics | H36 Current N Magnitude RMS | H36 Current N Magnitude RMS | 425804 | F32-4321 | R | 257288866
|  | Spectral Components | Current N Harmonics | H37 Current N Angle | H37 Current N Angle | 425812 | F32-4321 | R | 257288778
|  | Spectral Components | Current N Harmonics | H37 Current N Magnitude | H37 Current N Magnitude | 425808 | F32-4321 | R | 257288777
|  | Spectral Components | Current N Harmonics | H37 Current N Magnitude RMS | H37 Current N Magnitude RMS | 425810 | F32-4321 | R | 257288867
|  | Spectral Components | Current N Harmonics | H38 Current N Angle | H38 Current N Angle | 425818 | F32-4321 | R | 257288780
|  | Spectral Components | Current N Harmonics | H38 Current N Magnitude | H38 Current N Magnitude | 425814 | F32-4321 | R | 257288779
|  | Spectral Components | Current N Harmonics | H38 Current N Magnitude RMS | H38 Current N Magnitude RMS | 425816 | F32-4321 | R | 257288868
|  | Spectral Components | Current N Harmonics | H39 Current N Angle | H39 Current N Angle | 425824 | F32-4321 | R | 257288782
|  | Spectral Components | Current N Harmonics | H39 Current N Magnitude | H39 Current N Magnitude | 425820 | F32-4321 | R | 257288781
|  | Spectral Components | Current N Harmonics | H39 Current N Magnitude RMS | H39 Current N Magnitude RMS | 425822 | F32-4321 | R | 257288869
|  | Spectral Components | Current N Harmonics | H40 Current N Angle | H40 Current N Angle | 425830 | F32-4321 | R | 257288784
|  | Spectral Components | Current N Harmonics | H40 Current N Magnitude | H40 Current N Magnitude | 425826 | F32-4321 | R | 257288783
|  | Spectral Components | Current N Harmonics | H40 Current N Magnitude RMS | H40 Current N Magnitude RMS | 425828 | F32-4321 | R | 257288870
|  | Spectral Components | Current N Harmonics | H41 Current N Angle | H41 Current N Angle | 425836 | F32-4321 | R | 257288786
|  | Spectral Components | Current N Harmonics | H41 Current N Magnitude | H41 Current N Magnitude | 425832 | F32-4321 | R | 257288785
|  | Spectral Components | Current N Harmonics | H41 Current N Magnitude RMS | H41 Current N Magnitude RMS | 425834 | F32-4321 | R | 257288871
|  | Spectral Components | Current N Harmonics | H42 Current N Angle | H42 Current N Angle | 425842 | F32-4321 | R | 257288788
|  | Spectral Components | Current N Harmonics | H42 Current N Magnitude | H42 Current N Magnitude | 425838 | F32-4321 | R | 257288787
|  | Spectral Components | Current N Harmonics | H42 Current N Magnitude RMS | H42 Current N Magnitude RMS | 425840 | F32-4321 | R | 257288872
|  | Spectral Components | Current N Harmonics | H43 Current N Angle | H43 Current N Angle | 425848 | F32-4321 | R | 257288790
|  | Spectral Components | Current N Harmonics | H43 Current N Magnitude | H43 Current N Magnitude | 425844 | F32-4321 | R | 257288789
|  | Spectral Components | Current N Harmonics | H43 Current N Magnitude RMS | H43 Current N Magnitude RMS | 425846 | F32-4321 | R | 257288873
|  | Spectral Components | Current N Harmonics | H44 Current N Angle | H44 Current N Angle | 425854 | F32-4321 | R | 257288792
|  | Spectral Components | Current N Harmonics | H44 Current N Magnitude | H44 Current N Magnitude | 425850 | F32-4321 | R | 257288791
|  | Spectral Components | Current N Harmonics | H44 Current N Magnitude RMS | H44 Current N Magnitude RMS | 425852 | F32-4321 | R | 257288874
|  | Spectral Components | Current N Harmonics | H45 Current N Angle | H45 Current N Angle | 425860 | F32-4321 | R | 257288794
|  | Spectral Components | Current N Harmonics | H45 Current N Magnitude | H45 Current N Magnitude | 425856 | F32-4321 | R | 257288793
|  | Spectral Components | Current N Harmonics | H45 Current N Magnitude RMS | H45 Current N Magnitude RMS | 425858 | F32-4321 | R | 257288875
|  | Spectral Components | Current N Harmonics | H46 Current N Angle | H46 Current N Angle | 425866 | F32-4321 | R | 257288796
|  | Spectral Components | Current N Harmonics | H46 Current N Magnitude | H46 Current N Magnitude | 425862 | F32-4321 | R | 257288795
|  | Spectral Components | Current N Harmonics | H46 Current N Magnitude RMS | H46 Current N Magnitude RMS | 425864 | F32-4321 | R | 257288876
|  | Spectral Components | Current N Harmonics | H47 Current N Angle | H47 Current N Angle | 425872 | F32-4321 | R | 257288798
|  | Spectral Components | Current N Harmonics | H47 Current N Magnitude | H47 Current N Magnitude | 425868 | F32-4321 | R | 257288797
|  | Spectral Components | Current N Harmonics | H47 Current N Magnitude RMS | H47 Current N Magnitude RMS | 425870 | F32-4321 | R | 257288877
|  | Spectral Components | Current N Harmonics | H48 Current N Angle | H48 Current N Angle | 425878 | F32-4321 | R | 257288800
|  | Spectral Components | Current N Harmonics | H48 Current N Magnitude | H48 Current N Magnitude | 425874 | F32-4321 | R | 257288799
|  | Spectral Components | Current N Harmonics | H48 Current N Magnitude RMS | H48 Current N Magnitude RMS | 425876 | F32-4321 | R | 257288878
|  | Spectral Components | Current N Harmonics | H49 Current N Angle | H49 Current N Angle | 425884 | F32-4321 | R | 257288802
|  | Spectral Components | Current N Harmonics | H49 Current N Magnitude | H49 Current N Magnitude | 425880 | F32-4321 | R | 257288801
|  | Spectral Components | Current N Harmonics | H49 Current N Magnitude RMS | H49 Current N Magnitude RMS | 425882 | F32-4321 | R | 257288879
|  | Spectral Components | Current N Harmonics | H50 Current N Angle | H50 Current N Angle | 425890 | F32-4321 | R | 257288804
|  | Spectral Components | Current N Harmonics | H50 Current N Magnitude | H50 Current N Magnitude | 425886 | F32-4321 | R | 257288803
|  | Spectral Components | Current N Harmonics | H50 Current N Magnitude RMS | H50 Current N Magnitude RMS | 425888 | F32-4321 | R | 257288880
|  | Spectral Components | Current N Harmonics | H51 Current N Angle | H51 Current N Angle | 425896 | F32-4321 | R | 257288806
|  | Spectral Components | Current N Harmonics | H51 Current N Magnitude | H51 Current N Magnitude | 425892 | F32-4321 | R | 257288805
|  | Spectral Components | Current N Harmonics | H51 Current N Magnitude RMS | H51 Current N Magnitude RMS | 425894 | F32-4321 | R | 257288881
|  | Spectral Components | Current N Harmonics | H52 Current N Angle | H52 Current N Angle | 425902 | F32-4321 | R | 257288808
|  | Spectral Components | Current N Harmonics | H52 Current N Magnitude | H52 Current N Magnitude | 425898 | F32-4321 | R | 257288807
|  | Spectral Components | Current N Harmonics | H52 Current N Magnitude RMS | H52 Current N Magnitude RMS | 425900 | F32-4321 | R | 257288882
|  | Spectral Components | Current N Harmonics | H53 Current N Angle | H53 Current N Angle | 425908 | F32-4321 | R | 257288810
|  | Spectral Components | Current N Harmonics | H53 Current N Magnitude | H53 Current N Magnitude | 425904 | F32-4321 | R | 257288809
|  | Spectral Components | Current N Harmonics | H53 Current N Magnitude RMS | H53 Current N Magnitude RMS | 425906 | F32-4321 | R | 257288883
|  | Spectral Components | Current N Harmonics | H54 Current N Angle | H54 Current N Angle | 425914 | F32-4321 | R | 257288812
|  | Spectral Components | Current N Harmonics | H54 Current N Magnitude | H54 Current N Magnitude | 425910 | F32-4321 | R | 257288811
|  | Spectral Components | Current N Harmonics | H54 Current N Magnitude RMS | H54 Current N Magnitude RMS | 425912 | F32-4321 | R | 257288884
|  | Spectral Components | Current N Harmonics | H55 Current N Angle | H55 Current N Angle | 425920 | F32-4321 | R | 257288814
|  | Spectral Components | Current N Harmonics | H55 Current N Magnitude | H55 Current N Magnitude | 425916 | F32-4321 | R | 257288813
|  | Spectral Components | Current N Harmonics | H55 Current N Magnitude RMS | H55 Current N Magnitude RMS | 425918 | F32-4321 | R | 257288885
|  | Spectral Components | Current N Harmonics | H56 Current N Angle | H56 Current N Angle | 425926 | F32-4321 | R | 257288816
|  | Spectral Components | Current N Harmonics | H56 Current N Magnitude | H56 Current N Magnitude | 425922 | F32-4321 | R | 257288815
|  | Spectral Components | Current N Harmonics | H56 Current N Magnitude RMS | H56 Current N Magnitude RMS | 425924 | F32-4321 | R | 257288886
|  | Spectral Components | Current N Harmonics | H57 Current N Angle | H57 Current N Angle | 425932 | F32-4321 | R | 257288818
|  | Spectral Components | Current N Harmonics | H57 Current N Magnitude | H57 Current N Magnitude | 425928 | F32-4321 | R | 257288817
|  | Spectral Components | Current N Harmonics | H57 Current N Magnitude RMS | H57 Current N Magnitude RMS | 425930 | F32-4321 | R | 257288887
|  | Spectral Components | Current N Harmonics | H58 Current N Angle | H58 Current N Angle | 425938 | F32-4321 | R | 257288820
|  | Spectral Components | Current N Harmonics | H58 Current N Magnitude | H58 Current N Magnitude | 425934 | F32-4321 | R | 257288819
|  | Spectral Components | Current N Harmonics | H58 Current N Magnitude RMS | H58 Current N Magnitude RMS | 425936 | F32-4321 | R | 257288888
|  | Spectral Components | Current N Harmonics | H59 Current N Angle | H59 Current N Angle | 425944 | F32-4321 | R | 257288822
|  | Spectral Components | Current N Harmonics | H59 Current N Magnitude | H59 Current N Magnitude | 425940 | F32-4321 | R | 257288821
|  | Spectral Components | Current N Harmonics | H59 Current N Magnitude RMS | H59 Current N Magnitude RMS | 425942 | F32-4321 | R | 257288889
|  | Spectral Components | Current N Harmonics | H60 Current N Angle | H60 Current N Angle | 425950 | F32-4321 | R | 257288824
|  | Spectral Components | Current N Harmonics | H60 Current N Magnitude | H60 Current N Magnitude | 425946 | F32-4321 | R | 257288823
|  | Spectral Components | Current N Harmonics | H60 Current N Magnitude RMS | H60 Current N Magnitude RMS | 425948 | F32-4321 | R | 257288890
|  | Spectral Components | Current N Harmonics | H61 Current N Angle | H61 Current N Angle | 425956 | F32-4321 | R | 257288826
|  | Spectral Components | Current N Harmonics | H61 Current N Magnitude | H61 Current N Magnitude | 425952 | F32-4321 | R | 257288825
|  | Spectral Components | Current N Harmonics | H61 Current N Magnitude RMS | H61 Current N Magnitude RMS | 425954 | F32-4321 | R | 257288891
|  | Spectral Components | Current N Harmonics | H62 Current N Angle | H62 Current N Angle | 425962 | F32-4321 | R | 257288828
|  | Spectral Components | Current N Harmonics | H62 Current N Magnitude | H62 Current N Magnitude | 425958 | F32-4321 | R | 257288827
|  | Spectral Components | Current N Harmonics | H62 Current N Magnitude RMS | H62 Current N Magnitude RMS | 425960 | F32-4321 | R | 257288892
|  | Spectral Components | Current N Harmonics | H63 Current N Angle | H63 Current N Angle | 425968 | F32-4321 | R | 257288830
|  | Spectral Components | Current N Harmonics | H63 Current N Magnitude | H63 Current N Magnitude | 425964 | F32-4321 | R | 257288829
|  | Spectral Components | Current N Harmonics | H63 Current N Magnitude RMS | H63 Current N Magnitude RMS | 425966 | F32-4321 | R | 257288893
|  | Spectral Components | Voltage A-B Harmonics | H1 Voltage A-B Angle | H1 Voltage A-B Angle | 421716 | F32-4321 | R | 257286402
|  | Spectral Components | Voltage A-B Harmonics | H1 Voltage A-B Magnitude | H1 Voltage A-B Magnitude | 421712 | F32-4321 | R | 257286401
|  | Spectral Components | Voltage A-B Harmonics | H1 Voltage A-B Magnitude RMS | H1 Voltage A-B Magnitude RMS | 421714 | F32-4321 | R | 257286527
|  | Spectral Components | Voltage A-B Harmonics | H2 Voltage A-B Angle | H2 Voltage A-B Angle | 421722 | F32-4321 | R | 257286404
|  | Spectral Components | Voltage A-B Harmonics | H2 Voltage A-B Magnitude | H2 Voltage A-B Magnitude | 421718 | F32-4321 | R | 257286403
|  | Spectral Components | Voltage A-B Harmonics | H2 Voltage A-B Magnitude RMS | H2 Voltage A-B Magnitude RMS | 421720 | F32-4321 | R | 257286528
|  | Spectral Components | Voltage A-B Harmonics | H3 Voltage A-B Angle | H3 Voltage A-B Angle | 421728 | F32-4321 | R | 257286406
|  | Spectral Components | Voltage A-B Harmonics | H3 Voltage A-B Magnitude | H3 Voltage A-B Magnitude | 421724 | F32-4321 | R | 257286405
|  | Spectral Components | Voltage A-B Harmonics | H3 Voltage A-B Magnitude RMS | H3 Voltage A-B Magnitude RMS | 421726 | F32-4321 | R | 257286529
|  | Spectral Components | Voltage A-B Harmonics | H4 Voltage A-B Angle | H4 Voltage A-B Angle | 421734 | F32-4321 | R | 257286408
|  | Spectral Components | Voltage A-B Harmonics | H4 Voltage A-B Magnitude | H4 Voltage A-B Magnitude | 421730 | F32-4321 | R | 257286407
|  | Spectral Components | Voltage A-B Harmonics | H4 Voltage A-B Magnitude RMS | H4 Voltage A-B Magnitude RMS | 421732 | F32-4321 | R | 257286530
|  | Spectral Components | Voltage A-B Harmonics | H5 Voltage A-B Angle | H5 Voltage A-B Angle | 421740 | F32-4321 | R | 257286410
|  | Spectral Components | Voltage A-B Harmonics | H5 Voltage A-B Magnitude | H5 Voltage A-B Magnitude | 421736 | F32-4321 | R | 257286409
|  | Spectral Components | Voltage A-B Harmonics | H5 Voltage A-B Magnitude RMS | H5 Voltage A-B Magnitude RMS | 421738 | F32-4321 | R | 257286531
|  | Spectral Components | Voltage A-B Harmonics | H6 Voltage A-B Angle | H6 Voltage A-B Angle | 421746 | F32-4321 | R | 257286412
|  | Spectral Components | Voltage A-B Harmonics | H6 Voltage A-B Magnitude | H6 Voltage A-B Magnitude | 421742 | F32-4321 | R | 257286411
|  | Spectral Components | Voltage A-B Harmonics | H6 Voltage A-B Magnitude RMS | H6 Voltage A-B Magnitude RMS | 421744 | F32-4321 | R | 257286532
|  | Spectral Components | Voltage A-B Harmonics | H7 Voltage A-B Angle | H7 Voltage A-B Angle | 421752 | F32-4321 | R | 257286414
|  | Spectral Components | Voltage A-B Harmonics | H7 Voltage A-B Magnitude | H7 Voltage A-B Magnitude | 421748 | F32-4321 | R | 257286413
|  | Spectral Components | Voltage A-B Harmonics | H7 Voltage A-B Magnitude RMS | H7 Voltage A-B Magnitude RMS | 421750 | F32-4321 | R | 257286533
|  | Spectral Components | Voltage A-B Harmonics | H8 Voltage A-B Angle | H8 Voltage A-B Angle | 421758 | F32-4321 | R | 257286416
|  | Spectral Components | Voltage A-B Harmonics | H8 Voltage A-B Magnitude | H8 Voltage A-B Magnitude | 421754 | F32-4321 | R | 257286415
|  | Spectral Components | Voltage A-B Harmonics | H8 Voltage A-B Magnitude RMS | H8 Voltage A-B Magnitude RMS | 421756 | F32-4321 | R | 257286534
|  | Spectral Components | Voltage A-B Harmonics | H9 Voltage A-B Angle | H9 Voltage A-B Angle | 421764 | F32-4321 | R | 257286418
|  | Spectral Components | Voltage A-B Harmonics | H9 Voltage A-B Magnitude | H9 Voltage A-B Magnitude | 421760 | F32-4321 | R | 257286417
|  | Spectral Components | Voltage A-B Harmonics | H9 Voltage A-B Magnitude RMS | H9 Voltage A-B Magnitude RMS | 421762 | F32-4321 | R | 257286535
|  | Spectral Components | Voltage A-B Harmonics | H10 Voltage A-B Angle | H10 Voltage A-B Angle | 421770 | F32-4321 | R | 257286420
|  | Spectral Components | Voltage A-B Harmonics | H10 Voltage A-B Magnitude | H10 Voltage A-B Magnitude | 421766 | F32-4321 | R | 257286419
|  | Spectral Components | Voltage A-B Harmonics | H10 Voltage A-B Magnitude RMS | H10 Voltage A-B Magnitude RMS | 421768 | F32-4321 | R | 257286536
|  | Spectral Components | Voltage A-B Harmonics | H11 Voltage A-B Angle | H11 Voltage A-B Angle | 421776 | F32-4321 | R | 257286422
|  | Spectral Components | Voltage A-B Harmonics | H11 Voltage A-B Magnitude | H11 Voltage A-B Magnitude | 421772 | F32-4321 | R | 257286421
|  | Spectral Components | Voltage A-B Harmonics | H11 Voltage A-B Magnitude RMS | H11 Voltage A-B Magnitude RMS | 421774 | F32-4321 | R | 257286537
|  | Spectral Components | Voltage A-B Harmonics | H12 Voltage A-B Angle | H12 Voltage A-B Angle | 421782 | F32-4321 | R | 257286424
|  | Spectral Components | Voltage A-B Harmonics | H12 Voltage A-B Magnitude | H12 Voltage A-B Magnitude | 421778 | F32-4321 | R | 257286423
|  | Spectral Components | Voltage A-B Harmonics | H12 Voltage A-B Magnitude RMS | H12 Voltage A-B Magnitude RMS | 421780 | F32-4321 | R | 257286538
|  | Spectral Components | Voltage A-B Harmonics | H13 Voltage A-B Angle | H13 Voltage A-B Angle | 421788 | F32-4321 | R | 257286426
|  | Spectral Components | Voltage A-B Harmonics | H13 Voltage A-B Magnitude | H13 Voltage A-B Magnitude | 421784 | F32-4321 | R | 257286425
|  | Spectral Components | Voltage A-B Harmonics | H13 Voltage A-B Magnitude RMS | H13 Voltage A-B Magnitude RMS | 421786 | F32-4321 | R | 257286539
|  | Spectral Components | Voltage A-B Harmonics | H14 Voltage A-B Angle | H14 Voltage A-B Angle | 421794 | F32-4321 | R | 257286428
|  | Spectral Components | Voltage A-B Harmonics | H14 Voltage A-B Magnitude | H14 Voltage A-B Magnitude | 421790 | F32-4321 | R | 257286427
|  | Spectral Components | Voltage A-B Harmonics | H14 Voltage A-B Magnitude RMS | H14 Voltage A-B Magnitude RMS | 421792 | F32-4321 | R | 257286540
|  | Spectral Components | Voltage A-B Harmonics | H15 Voltage A-B Angle | H15 Voltage A-B Angle | 421800 | F32-4321 | R | 257286430
|  | Spectral Components | Voltage A-B Harmonics | H15 Voltage A-B Magnitude | H15 Voltage A-B Magnitude | 421796 | F32-4321 | R | 257286429
|  | Spectral Components | Voltage A-B Harmonics | H15 Voltage A-B Magnitude RMS | H15 Voltage A-B Magnitude RMS | 421798 | F32-4321 | R | 257286541
|  | Spectral Components | Voltage A-B Harmonics | H16 Voltage A-B Angle | H16 Voltage A-B Angle | 421806 | F32-4321 | R | 257286432
|  | Spectral Components | Voltage A-B Harmonics | H16 Voltage A-B Magnitude | H16 Voltage A-B Magnitude | 421802 | F32-4321 | R | 257286431
|  | Spectral Components | Voltage A-B Harmonics | H16 Voltage A-B Magnitude RMS | H16 Voltage A-B Magnitude RMS | 421804 | F32-4321 | R | 257286542
|  | Spectral Components | Voltage A-B Harmonics | H17 Voltage A-B Angle | H17 Voltage A-B Angle | 421812 | F32-4321 | R | 257286434
|  | Spectral Components | Voltage A-B Harmonics | H17 Voltage A-B Magnitude | H17 Voltage A-B Magnitude | 421808 | F32-4321 | R | 257286433
|  | Spectral Components | Voltage A-B Harmonics | H17 Voltage A-B Magnitude RMS | H17 Voltage A-B Magnitude RMS | 421810 | F32-4321 | R | 257286543
|  | Spectral Components | Voltage A-B Harmonics | H18 Voltage A-B Angle | H18 Voltage A-B Angle | 421818 | F32-4321 | R | 257286436
|  | Spectral Components | Voltage A-B Harmonics | H18 Voltage A-B Magnitude | H18 Voltage A-B Magnitude | 421814 | F32-4321 | R | 257286435
|  | Spectral Components | Voltage A-B Harmonics | H18 Voltage A-B Magnitude RMS | H18 Voltage A-B Magnitude RMS | 421816 | F32-4321 | R | 257286544
|  | Spectral Components | Voltage A-B Harmonics | H19 Voltage A-B Angle | H19 Voltage A-B Angle | 421824 | F32-4321 | R | 257286438
|  | Spectral Components | Voltage A-B Harmonics | H19 Voltage A-B Magnitude | H19 Voltage A-B Magnitude | 421820 | F32-4321 | R | 257286437
|  | Spectral Components | Voltage A-B Harmonics | H19 Voltage A-B Magnitude RMS | H19 Voltage A-B Magnitude RMS | 421822 | F32-4321 | R | 257286545
|  | Spectral Components | Voltage A-B Harmonics | H20 Voltage A-B Angle | H20 Voltage A-B Angle | 421830 | F32-4321 | R | 257286440
|  | Spectral Components | Voltage A-B Harmonics | H20 Voltage A-B Magnitude | H20 Voltage A-B Magnitude | 421826 | F32-4321 | R | 257286439
|  | Spectral Components | Voltage A-B Harmonics | H20 Voltage A-B Magnitude RMS | H20 Voltage A-B Magnitude RMS | 421828 | F32-4321 | R | 257286546
|  | Spectral Components | Voltage A-B Harmonics | H21 Voltage A-B Angle | H21 Voltage A-B Angle | 421836 | F32-4321 | R | 257286442
|  | Spectral Components | Voltage A-B Harmonics | H21 Voltage A-B Magnitude | H21 Voltage A-B Magnitude | 421832 | F32-4321 | R | 257286441
|  | Spectral Components | Voltage A-B Harmonics | H21 Voltage A-B Magnitude RMS | H21 Voltage A-B Magnitude RMS | 421834 | F32-4321 | R | 257286547
|  | Spectral Components | Voltage A-B Harmonics | H22 Voltage A-B Angle | H22 Voltage A-B Angle | 421842 | F32-4321 | R | 257286444
|  | Spectral Components | Voltage A-B Harmonics | H22 Voltage A-B Magnitude | H22 Voltage A-B Magnitude | 421838 | F32-4321 | R | 257286443
|  | Spectral Components | Voltage A-B Harmonics | H22 Voltage A-B Magnitude RMS | H22 Voltage A-B Magnitude RMS | 421840 | F32-4321 | R | 257286548
|  | Spectral Components | Voltage A-B Harmonics | H23 Voltage A-B Angle | H23 Voltage A-B Angle | 421848 | F32-4321 | R | 257286446
|  | Spectral Components | Voltage A-B Harmonics | H23 Voltage A-B Magnitude | H23 Voltage A-B Magnitude | 421844 | F32-4321 | R | 257286445
|  | Spectral Components | Voltage A-B Harmonics | H23 Voltage A-B Magnitude RMS | H23 Voltage A-B Magnitude RMS | 421846 | F32-4321 | R | 257286549
|  | Spectral Components | Voltage A-B Harmonics | H24 Voltage A-B Angle | H24 Voltage A-B Angle | 421854 | F32-4321 | R | 257286448
|  | Spectral Components | Voltage A-B Harmonics | H24 Voltage A-B Magnitude | H24 Voltage A-B Magnitude | 421850 | F32-4321 | R | 257286447
|  | Spectral Components | Voltage A-B Harmonics | H24 Voltage A-B Magnitude RMS | H24 Voltage A-B Magnitude RMS | 421852 | F32-4321 | R | 257286550
|  | Spectral Components | Voltage A-B Harmonics | H25 Voltage A-B Angle | H25 Voltage A-B Angle | 421860 | F32-4321 | R | 257286450
|  | Spectral Components | Voltage A-B Harmonics | H25 Voltage A-B Magnitude | H25 Voltage A-B Magnitude | 421856 | F32-4321 | R | 257286449
|  | Spectral Components | Voltage A-B Harmonics | H25 Voltage A-B Magnitude RMS | H25 Voltage A-B Magnitude RMS | 421858 | F32-4321 | R | 257286551
|  | Spectral Components | Voltage A-B Harmonics | H26 Voltage A-B Angle | H26 Voltage A-B Angle | 421866 | F32-4321 | R | 257286452
|  | Spectral Components | Voltage A-B Harmonics | H26 Voltage A-B Magnitude | H26 Voltage A-B Magnitude | 421862 | F32-4321 | R | 257286451
|  | Spectral Components | Voltage A-B Harmonics | H26 Voltage A-B Magnitude RMS | H26 Voltage A-B Magnitude RMS | 421864 | F32-4321 | R | 257286552
|  | Spectral Components | Voltage A-B Harmonics | H27 Voltage A-B Angle | H27 Voltage A-B Angle | 421872 | F32-4321 | R | 257286454
|  | Spectral Components | Voltage A-B Harmonics | H27 Voltage A-B Magnitude | H27 Voltage A-B Magnitude | 421868 | F32-4321 | R | 257286453
|  | Spectral Components | Voltage A-B Harmonics | H27 Voltage A-B Magnitude RMS | H27 Voltage A-B Magnitude RMS | 421870 | F32-4321 | R | 257286553
|  | Spectral Components | Voltage A-B Harmonics | H28 Voltage A-B Angle | H28 Voltage A-B Angle | 421878 | F32-4321 | R | 257286456
|  | Spectral Components | Voltage A-B Harmonics | H28 Voltage A-B Magnitude | H28 Voltage A-B Magnitude | 421874 | F32-4321 | R | 257286455
|  | Spectral Components | Voltage A-B Harmonics | H28 Voltage A-B Magnitude RMS | H28 Voltage A-B Magnitude RMS | 421876 | F32-4321 | R | 257286554
|  | Spectral Components | Voltage A-B Harmonics | H29 Voltage A-B Angle | H29 Voltage A-B Angle | 421884 | F32-4321 | R | 257286458
|  | Spectral Components | Voltage A-B Harmonics | H29 Voltage A-B Magnitude | H29 Voltage A-B Magnitude | 421880 | F32-4321 | R | 257286457
|  | Spectral Components | Voltage A-B Harmonics | H29 Voltage A-B Magnitude RMS | H29 Voltage A-B Magnitude RMS | 421882 | F32-4321 | R | 257286555
|  | Spectral Components | Voltage A-B Harmonics | H30 Voltage A-B Angle | H30 Voltage A-B Angle | 421890 | F32-4321 | R | 257286460
|  | Spectral Components | Voltage A-B Harmonics | H30 Voltage A-B Magnitude | H30 Voltage A-B Magnitude | 421886 | F32-4321 | R | 257286459
|  | Spectral Components | Voltage A-B Harmonics | H30 Voltage A-B Magnitude RMS | H30 Voltage A-B Magnitude RMS | 421888 | F32-4321 | R | 257286556
|  | Spectral Components | Voltage A-B Harmonics | H31 Voltage A-B Angle | H31 Voltage A-B Angle | 421896 | F32-4321 | R | 257286462
|  | Spectral Components | Voltage A-B Harmonics | H31 Voltage A-B Magnitude | H31 Voltage A-B Magnitude | 421892 | F32-4321 | R | 257286461
|  | Spectral Components | Voltage A-B Harmonics | H31 Voltage A-B Magnitude RMS | H31 Voltage A-B Magnitude RMS | 421894 | F32-4321 | R | 257286557
|  | Spectral Components | Voltage A-B Harmonics | H32 Voltage A-B Angle | H32 Voltage A-B Angle | 421902 | F32-4321 | R | 257286464
|  | Spectral Components | Voltage A-B Harmonics | H32 Voltage A-B Magnitude | H32 Voltage A-B Magnitude | 421898 | F32-4321 | R | 257286463
|  | Spectral Components | Voltage A-B Harmonics | H32 Voltage A-B Magnitude RMS | H32 Voltage A-B Magnitude RMS | 421900 | F32-4321 | R | 257286558
|  | Spectral Components | Voltage A-B Harmonics | H33 Voltage A-B Angle | H33 Voltage A-B Angle | 421908 | F32-4321 | R | 257286466
|  | Spectral Components | Voltage A-B Harmonics | H33 Voltage A-B Magnitude | H33 Voltage A-B Magnitude | 421904 | F32-4321 | R | 257286465
|  | Spectral Components | Voltage A-B Harmonics | H33 Voltage A-B Magnitude RMS | H33 Voltage A-B Magnitude RMS | 421906 | F32-4321 | R | 257286559
|  | Spectral Components | Voltage A-B Harmonics | H34 Voltage A-B Angle | H34 Voltage A-B Angle | 421914 | F32-4321 | R | 257286468
|  | Spectral Components | Voltage A-B Harmonics | H34 Voltage A-B Magnitude | H34 Voltage A-B Magnitude | 421910 | F32-4321 | R | 257286467
|  | Spectral Components | Voltage A-B Harmonics | H34 Voltage A-B Magnitude RMS | H34 Voltage A-B Magnitude RMS | 421912 | F32-4321 | R | 257286560
|  | Spectral Components | Voltage A-B Harmonics | H35 Voltage A-B Angle | H35 Voltage A-B Angle | 421920 | F32-4321 | R | 257286470
|  | Spectral Components | Voltage A-B Harmonics | H35 Voltage A-B Magnitude | H35 Voltage A-B Magnitude | 421916 | F32-4321 | R | 257286469
|  | Spectral Components | Voltage A-B Harmonics | H35 Voltage A-B Magnitude RMS | H35 Voltage A-B Magnitude RMS | 421918 | F32-4321 | R | 257286561
|  | Spectral Components | Voltage A-B Harmonics | H36 Voltage A-B Angle | H36 Voltage A-B Angle | 421926 | F32-4321 | R | 257286472
|  | Spectral Components | Voltage A-B Harmonics | H36 Voltage A-B Magnitude | H36 Voltage A-B Magnitude | 421922 | F32-4321 | R | 257286471
|  | Spectral Components | Voltage A-B Harmonics | H36 Voltage A-B Magnitude RMS | H36 Voltage A-B Magnitude RMS | 421924 | F32-4321 | R | 257286562
|  | Spectral Components | Voltage A-B Harmonics | H37 Voltage A-B Angle | H37 Voltage A-B Angle | 421932 | F32-4321 | R | 257286474
|  | Spectral Components | Voltage A-B Harmonics | H37 Voltage A-B Magnitude | H37 Voltage A-B Magnitude | 421928 | F32-4321 | R | 257286473
|  | Spectral Components | Voltage A-B Harmonics | H37 Voltage A-B Magnitude RMS | H37 Voltage A-B Magnitude RMS | 421930 | F32-4321 | R | 257286563
|  | Spectral Components | Voltage A-B Harmonics | H38 Voltage A-B Angle | H38 Voltage A-B Angle | 421938 | F32-4321 | R | 257286476
|  | Spectral Components | Voltage A-B Harmonics | H38 Voltage A-B Magnitude | H38 Voltage A-B Magnitude | 421934 | F32-4321 | R | 257286475
|  | Spectral Components | Voltage A-B Harmonics | H38 Voltage A-B Magnitude RMS | H38 Voltage A-B Magnitude RMS | 421936 | F32-4321 | R | 257286564
|  | Spectral Components | Voltage A-B Harmonics | H39 Voltage A-B Angle | H39 Voltage A-B Angle | 421944 | F32-4321 | R | 257286478
|  | Spectral Components | Voltage A-B Harmonics | H39 Voltage A-B Magnitude | H39 Voltage A-B Magnitude | 421940 | F32-4321 | R | 257286477
|  | Spectral Components | Voltage A-B Harmonics | H39 Voltage A-B Magnitude RMS | H39 Voltage A-B Magnitude RMS | 421942 | F32-4321 | R | 257286565
|  | Spectral Components | Voltage A-B Harmonics | H40 Voltage A-B Angle | H40 Voltage A-B Angle | 421950 | F32-4321 | R | 257286480
|  | Spectral Components | Voltage A-B Harmonics | H40 Voltage A-B Magnitude | H40 Voltage A-B Magnitude | 421946 | F32-4321 | R | 257286479
|  | Spectral Components | Voltage A-B Harmonics | H40 Voltage A-B Magnitude RMS | H40 Voltage A-B Magnitude RMS | 421948 | F32-4321 | R | 257286566
|  | Spectral Components | Voltage A-B Harmonics | H41 Voltage A-B Angle | H41 Voltage A-B Angle | 421956 | F32-4321 | R | 257286482
|  | Spectral Components | Voltage A-B Harmonics | H41 Voltage A-B Magnitude | H41 Voltage A-B Magnitude | 421952 | F32-4321 | R | 257286481
|  | Spectral Components | Voltage A-B Harmonics | H41 Voltage A-B Magnitude RMS | H41 Voltage A-B Magnitude RMS | 421954 | F32-4321 | R | 257286567
|  | Spectral Components | Voltage A-B Harmonics | H42 Voltage A-B Angle | H42 Voltage A-B Angle | 421962 | F32-4321 | R | 257286484
|  | Spectral Components | Voltage A-B Harmonics | H42 Voltage A-B Magnitude | H42 Voltage A-B Magnitude | 421958 | F32-4321 | R | 257286483
|  | Spectral Components | Voltage A-B Harmonics | H42 Voltage A-B Magnitude RMS | H42 Voltage A-B Magnitude RMS | 421960 | F32-4321 | R | 257286568
|  | Spectral Components | Voltage A-B Harmonics | H43 Voltage A-B Angle | H43 Voltage A-B Angle | 421968 | F32-4321 | R | 257286486
|  | Spectral Components | Voltage A-B Harmonics | H43 Voltage A-B Magnitude | H43 Voltage A-B Magnitude | 421964 | F32-4321 | R | 257286485
|  | Spectral Components | Voltage A-B Harmonics | H43 Voltage A-B Magnitude RMS | H43 Voltage A-B Magnitude RMS | 421966 | F32-4321 | R | 257286569
|  | Spectral Components | Voltage A-B Harmonics | H44 Voltage A-B Angle | H44 Voltage A-B Angle | 421974 | F32-4321 | R | 257286488
|  | Spectral Components | Voltage A-B Harmonics | H44 Voltage A-B Magnitude | H44 Voltage A-B Magnitude | 421970 | F32-4321 | R | 257286487
|  | Spectral Components | Voltage A-B Harmonics | H44 Voltage A-B Magnitude RMS | H44 Voltage A-B Magnitude RMS | 421972 | F32-4321 | R | 257286570
|  | Spectral Components | Voltage A-B Harmonics | H45 Voltage A-B Angle | H45 Voltage A-B Angle | 421980 | F32-4321 | R | 257286490
|  | Spectral Components | Voltage A-B Harmonics | H45 Voltage A-B Magnitude | H45 Voltage A-B Magnitude | 421976 | F32-4321 | R | 257286489
|  | Spectral Components | Voltage A-B Harmonics | H45 Voltage A-B Magnitude RMS | H45 Voltage A-B Magnitude RMS | 421978 | F32-4321 | R | 257286571
|  | Spectral Components | Voltage A-B Harmonics | H46 Voltage A-B Angle | H46 Voltage A-B Angle | 421986 | F32-4321 | R | 257286492
|  | Spectral Components | Voltage A-B Harmonics | H46 Voltage A-B Magnitude | H46 Voltage A-B Magnitude | 421982 | F32-4321 | R | 257286491
|  | Spectral Components | Voltage A-B Harmonics | H46 Voltage A-B Magnitude RMS | H46 Voltage A-B Magnitude RMS | 421984 | F32-4321 | R | 257286572
|  | Spectral Components | Voltage A-B Harmonics | H47 Voltage A-B Angle | H47 Voltage A-B Angle | 421992 | F32-4321 | R | 257286494
|  | Spectral Components | Voltage A-B Harmonics | H47 Voltage A-B Magnitude | H47 Voltage A-B Magnitude | 421988 | F32-4321 | R | 257286493
|  | Spectral Components | Voltage A-B Harmonics | H47 Voltage A-B Magnitude RMS | H47 Voltage A-B Magnitude RMS | 421990 | F32-4321 | R | 257286573
|  | Spectral Components | Voltage A-B Harmonics | H48 Voltage A-B Angle | H48 Voltage A-B Angle | 421998 | F32-4321 | R | 257286496
|  | Spectral Components | Voltage A-B Harmonics | H48 Voltage A-B Magnitude | H48 Voltage A-B Magnitude | 421994 | F32-4321 | R | 257286495
|  | Spectral Components | Voltage A-B Harmonics | H48 Voltage A-B Magnitude RMS | H48 Voltage A-B Magnitude RMS | 421996 | F32-4321 | R | 257286574
|  | Spectral Components | Voltage A-B Harmonics | H49 Voltage A-B Angle | H49 Voltage A-B Angle | 422004 | F32-4321 | R | 257286498
|  | Spectral Components | Voltage A-B Harmonics | H49 Voltage A-B Magnitude | H49 Voltage A-B Magnitude | 422000 | F32-4321 | R | 257286497
|  | Spectral Components | Voltage A-B Harmonics | H49 Voltage A-B Magnitude RMS | H49 Voltage A-B Magnitude RMS | 422002 | F32-4321 | R | 257286575
|  | Spectral Components | Voltage A-B Harmonics | H50 Voltage A-B Angle | H50 Voltage A-B Angle | 422010 | F32-4321 | R | 257286500
|  | Spectral Components | Voltage A-B Harmonics | H50 Voltage A-B Magnitude | H50 Voltage A-B Magnitude | 422006 | F32-4321 | R | 257286499
|  | Spectral Components | Voltage A-B Harmonics | H50 Voltage A-B Magnitude RMS | H50 Voltage A-B Magnitude RMS | 422008 | F32-4321 | R | 257286576
|  | Spectral Components | Voltage A-B Harmonics | H51 Voltage A-B Angle | H51 Voltage A-B Angle | 422016 | F32-4321 | R | 257286502
|  | Spectral Components | Voltage A-B Harmonics | H51 Voltage A-B Magnitude | H51 Voltage A-B Magnitude | 422012 | F32-4321 | R | 257286501
|  | Spectral Components | Voltage A-B Harmonics | H51 Voltage A-B Magnitude RMS | H51 Voltage A-B Magnitude RMS | 422014 | F32-4321 | R | 257286577
|  | Spectral Components | Voltage A-B Harmonics | H52 Voltage A-B Angle | H52 Voltage A-B Angle | 422022 | F32-4321 | R | 257286504
|  | Spectral Components | Voltage A-B Harmonics | H52 Voltage A-B Magnitude | H52 Voltage A-B Magnitude | 422018 | F32-4321 | R | 257286503
|  | Spectral Components | Voltage A-B Harmonics | H52 Voltage A-B Magnitude RMS | H52 Voltage A-B Magnitude RMS | 422020 | F32-4321 | R | 257286578
|  | Spectral Components | Voltage A-B Harmonics | H53 Voltage A-B Angle | H53 Voltage A-B Angle | 422028 | F32-4321 | R | 257286506
|  | Spectral Components | Voltage A-B Harmonics | H53 Voltage A-B Magnitude | H53 Voltage A-B Magnitude | 422024 | F32-4321 | R | 257286505
|  | Spectral Components | Voltage A-B Harmonics | H53 Voltage A-B Magnitude RMS | H53 Voltage A-B Magnitude RMS | 422026 | F32-4321 | R | 257286579
|  | Spectral Components | Voltage A-B Harmonics | H54 Voltage A-B Angle | H54 Voltage A-B Angle | 422034 | F32-4321 | R | 257286508
|  | Spectral Components | Voltage A-B Harmonics | H54 Voltage A-B Magnitude | H54 Voltage A-B Magnitude | 422030 | F32-4321 | R | 257286507
|  | Spectral Components | Voltage A-B Harmonics | H54 Voltage A-B Magnitude RMS | H54 Voltage A-B Magnitude RMS | 422032 | F32-4321 | R | 257286580
|  | Spectral Components | Voltage A-B Harmonics | H55 Voltage A-B Angle | H55 Voltage A-B Angle | 422040 | F32-4321 | R | 257286510
|  | Spectral Components | Voltage A-B Harmonics | H55 Voltage A-B Magnitude | H55 Voltage A-B Magnitude | 422036 | F32-4321 | R | 257286509
|  | Spectral Components | Voltage A-B Harmonics | H55 Voltage A-B Magnitude RMS | H55 Voltage A-B Magnitude RMS | 422038 | F32-4321 | R | 257286581
|  | Spectral Components | Voltage A-B Harmonics | H56 Voltage A-B Angle | H56 Voltage A-B Angle | 422046 | F32-4321 | R | 257286512
|  | Spectral Components | Voltage A-B Harmonics | H56 Voltage A-B Magnitude | H56 Voltage A-B Magnitude | 422042 | F32-4321 | R | 257286511
|  | Spectral Components | Voltage A-B Harmonics | H56 Voltage A-B Magnitude RMS | H56 Voltage A-B Magnitude RMS | 422044 | F32-4321 | R | 257286582
|  | Spectral Components | Voltage A-B Harmonics | H57 Voltage A-B Angle | H57 Voltage A-B Angle | 422052 | F32-4321 | R | 257286514
|  | Spectral Components | Voltage A-B Harmonics | H57 Voltage A-B Magnitude | H57 Voltage A-B Magnitude | 422048 | F32-4321 | R | 257286513
|  | Spectral Components | Voltage A-B Harmonics | H57 Voltage A-B Magnitude RMS | H57 Voltage A-B Magnitude RMS | 422050 | F32-4321 | R | 257286583
|  | Spectral Components | Voltage A-B Harmonics | H58 Voltage A-B Angle | H58 Voltage A-B Angle | 422058 | F32-4321 | R | 257286516
|  | Spectral Components | Voltage A-B Harmonics | H58 Voltage A-B Magnitude | H58 Voltage A-B Magnitude | 422054 | F32-4321 | R | 257286515
|  | Spectral Components | Voltage A-B Harmonics | H58 Voltage A-B Magnitude RMS | H58 Voltage A-B Magnitude RMS | 422056 | F32-4321 | R | 257286584
|  | Spectral Components | Voltage A-B Harmonics | H59 Voltage A-B Angle | H59 Voltage A-B Angle | 422064 | F32-4321 | R | 257286518
|  | Spectral Components | Voltage A-B Harmonics | H59 Voltage A-B Magnitude | H59 Voltage A-B Magnitude | 422060 | F32-4321 | R | 257286517
|  | Spectral Components | Voltage A-B Harmonics | H59 Voltage A-B Magnitude RMS | H59 Voltage A-B Magnitude RMS | 422062 | F32-4321 | R | 257286585
|  | Spectral Components | Voltage A-B Harmonics | H60 Voltage A-B Angle | H60 Voltage A-B Angle | 422070 | F32-4321 | R | 257286520
|  | Spectral Components | Voltage A-B Harmonics | H60 Voltage A-B Magnitude | H60 Voltage A-B Magnitude | 422066 | F32-4321 | R | 257286519
|  | Spectral Components | Voltage A-B Harmonics | H60 Voltage A-B Magnitude RMS | H60 Voltage A-B Magnitude RMS | 422068 | F32-4321 | R | 257286586
|  | Spectral Components | Voltage A-B Harmonics | H61 Voltage A-B Angle | H61 Voltage A-B Angle | 422076 | F32-4321 | R | 257286522
|  | Spectral Components | Voltage A-B Harmonics | H61 Voltage A-B Magnitude | H61 Voltage A-B Magnitude | 422072 | F32-4321 | R | 257286521
|  | Spectral Components | Voltage A-B Harmonics | H61 Voltage A-B Magnitude RMS | H61 Voltage A-B Magnitude RMS | 422074 | F32-4321 | R | 257286587
|  | Spectral Components | Voltage A-B Harmonics | H62 Voltage A-B Angle | H62 Voltage A-B Angle | 422082 | F32-4321 | R | 257286524
|  | Spectral Components | Voltage A-B Harmonics | H62 Voltage A-B Magnitude | H62 Voltage A-B Magnitude | 422078 | F32-4321 | R | 257286523
|  | Spectral Components | Voltage A-B Harmonics | H62 Voltage A-B Magnitude RMS | H62 Voltage A-B Magnitude RMS | 422080 | F32-4321 | R | 257286588
|  | Spectral Components | Voltage A-B Harmonics | H63 Voltage A-B Angle | H63 Voltage A-B Angle | 422088 | F32-4321 | R | 257286526
|  | Spectral Components | Voltage A-B Harmonics | H63 Voltage A-B Magnitude | H63 Voltage A-B Magnitude | 422084 | F32-4321 | R | 257286525
|  | Spectral Components | Voltage A-B Harmonics | H63 Voltage A-B Magnitude RMS | H63 Voltage A-B Magnitude RMS | 422086 | F32-4321 | R | 257286589
|  | Spectral Components | Voltage A-N Harmonics | H1 Voltage A-N Angle | H1 Voltage A-N Angle | 422880 | F32-4321 | R | 257287170
|  | Spectral Components | Voltage A-N Harmonics | H1 Voltage A-N Magnitude | H1 Voltage A-N Magnitude | 422876 | F32-4321 | R | 257287169
|  | Spectral Components | Voltage A-N Harmonics | H1 Voltage A-N Magnitude RMS | H1 Voltage A-N Magnitude RMS | 422878 | F32-4321 | R | 257287295
|  | Spectral Components | Voltage A-N Harmonics | H2 Voltage A-N Angle | H2 Voltage A-N Angle | 422886 | F32-4321 | R | 257287172
|  | Spectral Components | Voltage A-N Harmonics | H2 Voltage A-N Magnitude | H2 Voltage A-N Magnitude | 422882 | F32-4321 | R | 257287171
|  | Spectral Components | Voltage A-N Harmonics | H2 Voltage A-N Magnitude RMS | H2 Voltage A-N Magnitude RMS | 422884 | F32-4321 | R | 257287296
|  | Spectral Components | Voltage A-N Harmonics | H3 Voltage A-N Angle | H3 Voltage A-N Angle | 422892 | F32-4321 | R | 257287174
|  | Spectral Components | Voltage A-N Harmonics | H3 Voltage A-N Magnitude | H3 Voltage A-N Magnitude | 422888 | F32-4321 | R | 257287173
|  | Spectral Components | Voltage A-N Harmonics | H3 Voltage A-N Magnitude RMS | H3 Voltage A-N Magnitude RMS | 422890 | F32-4321 | R | 257287297
|  | Spectral Components | Voltage A-N Harmonics | H4 Voltage A-N Angle | H4 Voltage A-N Angle | 422898 | F32-4321 | R | 257287176
|  | Spectral Components | Voltage A-N Harmonics | H4 Voltage A-N Magnitude | H4 Voltage A-N Magnitude | 422894 | F32-4321 | R | 257287175
|  | Spectral Components | Voltage A-N Harmonics | H4 Voltage A-N Magnitude RMS | H4 Voltage A-N Magnitude RMS | 422896 | F32-4321 | R | 257287298
|  | Spectral Components | Voltage A-N Harmonics | H5 Voltage A-N Angle | H5 Voltage A-N Angle | 422904 | F32-4321 | R | 257287178
|  | Spectral Components | Voltage A-N Harmonics | H5 Voltage A-N Magnitude | H5 Voltage A-N Magnitude | 422900 | F32-4321 | R | 257287177
|  | Spectral Components | Voltage A-N Harmonics | H5 Voltage A-N Magnitude RMS | H5 Voltage A-N Magnitude RMS | 422902 | F32-4321 | R | 257287299
|  | Spectral Components | Voltage A-N Harmonics | H6 Voltage A-N Angle | H6 Voltage A-N Angle | 422910 | F32-4321 | R | 257287180
|  | Spectral Components | Voltage A-N Harmonics | H6 Voltage A-N Magnitude | H6 Voltage A-N Magnitude | 422906 | F32-4321 | R | 257287179
|  | Spectral Components | Voltage A-N Harmonics | H6 Voltage A-N Magnitude RMS | H6 Voltage A-N Magnitude RMS | 422908 | F32-4321 | R | 257287300
|  | Spectral Components | Voltage A-N Harmonics | H7 Voltage A-N Angle | H7 Voltage A-N Angle | 422916 | F32-4321 | R | 257287182
|  | Spectral Components | Voltage A-N Harmonics | H7 Voltage A-N Magnitude | H7 Voltage A-N Magnitude | 422912 | F32-4321 | R | 257287181
|  | Spectral Components | Voltage A-N Harmonics | H7 Voltage A-N Magnitude RMS | H7 Voltage A-N Magnitude RMS | 422914 | F32-4321 | R | 257287301
|  | Spectral Components | Voltage A-N Harmonics | H8 Voltage A-N Angle | H8 Voltage A-N Angle | 422922 | F32-4321 | R | 257287184
|  | Spectral Components | Voltage A-N Harmonics | H8 Voltage A-N Magnitude | H8 Voltage A-N Magnitude | 422918 | F32-4321 | R | 257287183
|  | Spectral Components | Voltage A-N Harmonics | H8 Voltage A-N Magnitude RMS | H8 Voltage A-N Magnitude RMS | 422920 | F32-4321 | R | 257287302
|  | Spectral Components | Voltage A-N Harmonics | H9 Voltage A-N Angle | H9 Voltage A-N Angle | 422928 | F32-4321 | R | 257287186
|  | Spectral Components | Voltage A-N Harmonics | H9 Voltage A-N Magnitude | H9 Voltage A-N Magnitude | 422924 | F32-4321 | R | 257287185
|  | Spectral Components | Voltage A-N Harmonics | H9 Voltage A-N Magnitude RMS | H9 Voltage A-N Magnitude RMS | 422926 | F32-4321 | R | 257287303
|  | Spectral Components | Voltage A-N Harmonics | H10 Voltage A-N Angle | H10 Voltage A-N Angle | 422934 | F32-4321 | R | 257287188
|  | Spectral Components | Voltage A-N Harmonics | H10 Voltage A-N Magnitude | H10 Voltage A-N Magnitude | 422930 | F32-4321 | R | 257287187
|  | Spectral Components | Voltage A-N Harmonics | H10 Voltage A-N Magnitude RMS | H10 Voltage A-N Magnitude RMS | 422932 | F32-4321 | R | 257287304
|  | Spectral Components | Voltage A-N Harmonics | H11 Voltage A-N Angle | H11 Voltage A-N Angle | 422940 | F32-4321 | R | 257287190
|  | Spectral Components | Voltage A-N Harmonics | H11 Voltage A-N Magnitude | H11 Voltage A-N Magnitude | 422936 | F32-4321 | R | 257287189
|  | Spectral Components | Voltage A-N Harmonics | H11 Voltage A-N Magnitude RMS | H11 Voltage A-N Magnitude RMS | 422938 | F32-4321 | R | 257287305
|  | Spectral Components | Voltage A-N Harmonics | H12 Voltage A-N Angle | H12 Voltage A-N Angle | 422946 | F32-4321 | R | 257287192
|  | Spectral Components | Voltage A-N Harmonics | H12 Voltage A-N Magnitude | H12 Voltage A-N Magnitude | 422942 | F32-4321 | R | 257287191
|  | Spectral Components | Voltage A-N Harmonics | H12 Voltage A-N Magnitude RMS | H12 Voltage A-N Magnitude RMS | 422944 | F32-4321 | R | 257287306
|  | Spectral Components | Voltage A-N Harmonics | H13 Voltage A-N Angle | H13 Voltage A-N Angle | 422952 | F32-4321 | R | 257287194
|  | Spectral Components | Voltage A-N Harmonics | H13 Voltage A-N Magnitude | H13 Voltage A-N Magnitude | 422948 | F32-4321 | R | 257287193
|  | Spectral Components | Voltage A-N Harmonics | H13 Voltage A-N Magnitude RMS | H13 Voltage A-N Magnitude RMS | 422950 | F32-4321 | R | 257287307
|  | Spectral Components | Voltage A-N Harmonics | H14 Voltage A-N Angle | H14 Voltage A-N Angle | 422958 | F32-4321 | R | 257287196
|  | Spectral Components | Voltage A-N Harmonics | H14 Voltage A-N Magnitude | H14 Voltage A-N Magnitude | 422954 | F32-4321 | R | 257287195
|  | Spectral Components | Voltage A-N Harmonics | H14 Voltage A-N Magnitude RMS | H14 Voltage A-N Magnitude RMS | 422956 | F32-4321 | R | 257287308
|  | Spectral Components | Voltage A-N Harmonics | H15 Voltage A-N Angle | H15 Voltage A-N Angle | 422964 | F32-4321 | R | 257287198
|  | Spectral Components | Voltage A-N Harmonics | H15 Voltage A-N Magnitude | H15 Voltage A-N Magnitude | 422960 | F32-4321 | R | 257287197
|  | Spectral Components | Voltage A-N Harmonics | H15 Voltage A-N Magnitude RMS | H15 Voltage A-N Magnitude RMS | 422962 | F32-4321 | R | 257287309
|  | Spectral Components | Voltage A-N Harmonics | H16 Voltage A-N Angle | H16 Voltage A-N Angle | 422970 | F32-4321 | R | 257287200
|  | Spectral Components | Voltage A-N Harmonics | H16 Voltage A-N Magnitude | H16 Voltage A-N Magnitude | 422966 | F32-4321 | R | 257287199
|  | Spectral Components | Voltage A-N Harmonics | H16 Voltage A-N Magnitude RMS | H16 Voltage A-N Magnitude RMS | 422968 | F32-4321 | R | 257287310
|  | Spectral Components | Voltage A-N Harmonics | H17 Voltage A-N Angle | H17 Voltage A-N Angle | 422976 | F32-4321 | R | 257287202
|  | Spectral Components | Voltage A-N Harmonics | H17 Voltage A-N Magnitude | H17 Voltage A-N Magnitude | 422972 | F32-4321 | R | 257287201
|  | Spectral Components | Voltage A-N Harmonics | H17 Voltage A-N Magnitude RMS | H17 Voltage A-N Magnitude RMS | 422974 | F32-4321 | R | 257287311
|  | Spectral Components | Voltage A-N Harmonics | H18 Voltage A-N Angle | H18 Voltage A-N Angle | 422982 | F32-4321 | R | 257287204
|  | Spectral Components | Voltage A-N Harmonics | H18 Voltage A-N Magnitude | H18 Voltage A-N Magnitude | 422978 | F32-4321 | R | 257287203
|  | Spectral Components | Voltage A-N Harmonics | H18 Voltage A-N Magnitude RMS | H18 Voltage A-N Magnitude RMS | 422980 | F32-4321 | R | 257287312
|  | Spectral Components | Voltage A-N Harmonics | H19 Voltage A-N Angle | H19 Voltage A-N Angle | 422988 | F32-4321 | R | 257287206
|  | Spectral Components | Voltage A-N Harmonics | H19 Voltage A-N Magnitude | H19 Voltage A-N Magnitude | 422984 | F32-4321 | R | 257287205
|  | Spectral Components | Voltage A-N Harmonics | H19 Voltage A-N Magnitude RMS | H19 Voltage A-N Magnitude RMS | 422986 | F32-4321 | R | 257287313
|  | Spectral Components | Voltage A-N Harmonics | H20 Voltage A-N Angle | H20 Voltage A-N Angle | 422994 | F32-4321 | R | 257287208
|  | Spectral Components | Voltage A-N Harmonics | H20 Voltage A-N Magnitude | H20 Voltage A-N Magnitude | 422990 | F32-4321 | R | 257287207
|  | Spectral Components | Voltage A-N Harmonics | H20 Voltage A-N Magnitude RMS | H20 Voltage A-N Magnitude RMS | 422992 | F32-4321 | R | 257287314
|  | Spectral Components | Voltage A-N Harmonics | H21 Voltage A-N Angle | H21 Voltage A-N Angle | 423000 | F32-4321 | R | 257287210
|  | Spectral Components | Voltage A-N Harmonics | H21 Voltage A-N Magnitude | H21 Voltage A-N Magnitude | 422996 | F32-4321 | R | 257287209
|  | Spectral Components | Voltage A-N Harmonics | H21 Voltage A-N Magnitude RMS | H21 Voltage A-N Magnitude RMS | 422998 | F32-4321 | R | 257287315
|  | Spectral Components | Voltage A-N Harmonics | H22 Voltage A-N Angle | H22 Voltage A-N Angle | 423006 | F32-4321 | R | 257287212
|  | Spectral Components | Voltage A-N Harmonics | H22 Voltage A-N Magnitude | H22 Voltage A-N Magnitude | 423002 | F32-4321 | R | 257287211
|  | Spectral Components | Voltage A-N Harmonics | H22 Voltage A-N Magnitude RMS | H22 Voltage A-N Magnitude RMS | 423004 | F32-4321 | R | 257287316
|  | Spectral Components | Voltage A-N Harmonics | H23 Voltage A-N Angle | H23 Voltage A-N Angle | 423012 | F32-4321 | R | 257287214
|  | Spectral Components | Voltage A-N Harmonics | H23 Voltage A-N Magnitude | H23 Voltage A-N Magnitude | 423008 | F32-4321 | R | 257287213
|  | Spectral Components | Voltage A-N Harmonics | H23 Voltage A-N Magnitude RMS | H23 Voltage A-N Magnitude RMS | 423010 | F32-4321 | R | 257287317
|  | Spectral Components | Voltage A-N Harmonics | H24 Voltage A-N Angle | H24 Voltage A-N Angle | 423018 | F32-4321 | R | 257287216
|  | Spectral Components | Voltage A-N Harmonics | H24 Voltage A-N Magnitude | H24 Voltage A-N Magnitude | 423014 | F32-4321 | R | 257287215
|  | Spectral Components | Voltage A-N Harmonics | H24 Voltage A-N Magnitude RMS | H24 Voltage A-N Magnitude RMS | 423016 | F32-4321 | R | 257287318
|  | Spectral Components | Voltage A-N Harmonics | H25 Voltage A-N Angle | H25 Voltage A-N Angle | 423024 | F32-4321 | R | 257287218
|  | Spectral Components | Voltage A-N Harmonics | H25 Voltage A-N Magnitude | H25 Voltage A-N Magnitude | 423020 | F32-4321 | R | 257287217
|  | Spectral Components | Voltage A-N Harmonics | H25 Voltage A-N Magnitude RMS | H25 Voltage A-N Magnitude RMS | 423022 | F32-4321 | R | 257287319
|  | Spectral Components | Voltage A-N Harmonics | H26 Voltage A-N Angle | H26 Voltage A-N Angle | 423030 | F32-4321 | R | 257287220
|  | Spectral Components | Voltage A-N Harmonics | H26 Voltage A-N Magnitude | H26 Voltage A-N Magnitude | 423026 | F32-4321 | R | 257287219
|  | Spectral Components | Voltage A-N Harmonics | H26 Voltage A-N Magnitude RMS | H26 Voltage A-N Magnitude RMS | 423028 | F32-4321 | R | 257287320
|  | Spectral Components | Voltage A-N Harmonics | H27 Voltage A-N Angle | H27 Voltage A-N Angle | 423036 | F32-4321 | R | 257287222
|  | Spectral Components | Voltage A-N Harmonics | H27 Voltage A-N Magnitude | H27 Voltage A-N Magnitude | 423032 | F32-4321 | R | 257287221
|  | Spectral Components | Voltage A-N Harmonics | H27 Voltage A-N Magnitude RMS | H27 Voltage A-N Magnitude RMS | 423034 | F32-4321 | R | 257287321
|  | Spectral Components | Voltage A-N Harmonics | H28 Voltage A-N Angle | H28 Voltage A-N Angle | 423042 | F32-4321 | R | 257287224
|  | Spectral Components | Voltage A-N Harmonics | H28 Voltage A-N Magnitude | H28 Voltage A-N Magnitude | 423038 | F32-4321 | R | 257287223
|  | Spectral Components | Voltage A-N Harmonics | H28 Voltage A-N Magnitude RMS | H28 Voltage A-N Magnitude RMS | 423040 | F32-4321 | R | 257287322
|  | Spectral Components | Voltage A-N Harmonics | H29 Voltage A-N Angle | H29 Voltage A-N Angle | 423048 | F32-4321 | R | 257287226
|  | Spectral Components | Voltage A-N Harmonics | H29 Voltage A-N Magnitude | H29 Voltage A-N Magnitude | 423044 | F32-4321 | R | 257287225
|  | Spectral Components | Voltage A-N Harmonics | H29 Voltage A-N Magnitude RMS | H29 Voltage A-N Magnitude RMS | 423046 | F32-4321 | R | 257287323
|  | Spectral Components | Voltage A-N Harmonics | H30 Voltage A-N Angle | H30 Voltage A-N Angle | 423054 | F32-4321 | R | 257287228
|  | Spectral Components | Voltage A-N Harmonics | H30 Voltage A-N Magnitude | H30 Voltage A-N Magnitude | 423050 | F32-4321 | R | 257287227
|  | Spectral Components | Voltage A-N Harmonics | H30 Voltage A-N Magnitude RMS | H30 Voltage A-N Magnitude RMS | 423052 | F32-4321 | R | 257287324
|  | Spectral Components | Voltage A-N Harmonics | H31 Voltage A-N Angle | H31 Voltage A-N Angle | 423060 | F32-4321 | R | 257287230
|  | Spectral Components | Voltage A-N Harmonics | H31 Voltage A-N Magnitude | H31 Voltage A-N Magnitude | 423056 | F32-4321 | R | 257287229
|  | Spectral Components | Voltage A-N Harmonics | H31 Voltage A-N Magnitude RMS | H31 Voltage A-N Magnitude RMS | 423058 | F32-4321 | R | 257287325
|  | Spectral Components | Voltage A-N Harmonics | H32 Voltage A-N Angle | H32 Voltage A-N Angle | 423066 | F32-4321 | R | 257287232
|  | Spectral Components | Voltage A-N Harmonics | H32 Voltage A-N Magnitude | H32 Voltage A-N Magnitude | 423062 | F32-4321 | R | 257287231
|  | Spectral Components | Voltage A-N Harmonics | H32 Voltage A-N Magnitude RMS | H32 Voltage A-N Magnitude RMS | 423064 | F32-4321 | R | 257287326
|  | Spectral Components | Voltage A-N Harmonics | H33 Voltage A-N Angle | H33 Voltage A-N Angle | 423072 | F32-4321 | R | 257287234
|  | Spectral Components | Voltage A-N Harmonics | H33 Voltage A-N Magnitude | H33 Voltage A-N Magnitude | 423068 | F32-4321 | R | 257287233
|  | Spectral Components | Voltage A-N Harmonics | H33 Voltage A-N Magnitude RMS | H33 Voltage A-N Magnitude RMS | 423070 | F32-4321 | R | 257287327
|  | Spectral Components | Voltage A-N Harmonics | H34 Voltage A-N Angle | H34 Voltage A-N Angle | 423078 | F32-4321 | R | 257287236
|  | Spectral Components | Voltage A-N Harmonics | H34 Voltage A-N Magnitude | H34 Voltage A-N Magnitude | 423074 | F32-4321 | R | 257287235
|  | Spectral Components | Voltage A-N Harmonics | H34 Voltage A-N Magnitude RMS | H34 Voltage A-N Magnitude RMS | 423076 | F32-4321 | R | 257287328
|  | Spectral Components | Voltage A-N Harmonics | H35 Voltage A-N Angle | H35 Voltage A-N Angle | 423084 | F32-4321 | R | 257287238
|  | Spectral Components | Voltage A-N Harmonics | H35 Voltage A-N Magnitude | H35 Voltage A-N Magnitude | 423080 | F32-4321 | R | 257287237
|  | Spectral Components | Voltage A-N Harmonics | H35 Voltage A-N Magnitude RMS | H35 Voltage A-N Magnitude RMS | 423082 | F32-4321 | R | 257287329
|  | Spectral Components | Voltage A-N Harmonics | H36 Voltage A-N Angle | H36 Voltage A-N Angle | 423090 | F32-4321 | R | 257287240
|  | Spectral Components | Voltage A-N Harmonics | H36 Voltage A-N Magnitude | H36 Voltage A-N Magnitude | 423086 | F32-4321 | R | 257287239
|  | Spectral Components | Voltage A-N Harmonics | H36 Voltage A-N Magnitude RMS | H36 Voltage A-N Magnitude RMS | 423088 | F32-4321 | R | 257287330
|  | Spectral Components | Voltage A-N Harmonics | H37 Voltage A-N Angle | H37 Voltage A-N Angle | 423096 | F32-4321 | R | 257287242
|  | Spectral Components | Voltage A-N Harmonics | H37 Voltage A-N Magnitude | H37 Voltage A-N Magnitude | 423092 | F32-4321 | R | 257287241
|  | Spectral Components | Voltage A-N Harmonics | H37 Voltage A-N Magnitude RMS | H37 Voltage A-N Magnitude RMS | 423094 | F32-4321 | R | 257287331
|  | Spectral Components | Voltage A-N Harmonics | H38 Voltage A-N Angle | H38 Voltage A-N Angle | 423102 | F32-4321 | R | 257287244
|  | Spectral Components | Voltage A-N Harmonics | H38 Voltage A-N Magnitude | H38 Voltage A-N Magnitude | 423098 | F32-4321 | R | 257287243
|  | Spectral Components | Voltage A-N Harmonics | H38 Voltage A-N Magnitude RMS | H38 Voltage A-N Magnitude RMS | 423100 | F32-4321 | R | 257287332
|  | Spectral Components | Voltage A-N Harmonics | H39 Voltage A-N Angle | H39 Voltage A-N Angle | 423108 | F32-4321 | R | 257287246
|  | Spectral Components | Voltage A-N Harmonics | H39 Voltage A-N Magnitude | H39 Voltage A-N Magnitude | 423104 | F32-4321 | R | 257287245
|  | Spectral Components | Voltage A-N Harmonics | H39 Voltage A-N Magnitude RMS | H39 Voltage A-N Magnitude RMS | 423106 | F32-4321 | R | 257287333
|  | Spectral Components | Voltage A-N Harmonics | H40 Voltage A-N Angle | H40 Voltage A-N Angle | 423114 | F32-4321 | R | 257287248
|  | Spectral Components | Voltage A-N Harmonics | H40 Voltage A-N Magnitude | H40 Voltage A-N Magnitude | 423110 | F32-4321 | R | 257287247
|  | Spectral Components | Voltage A-N Harmonics | H40 Voltage A-N Magnitude RMS | H40 Voltage A-N Magnitude RMS | 423112 | F32-4321 | R | 257287334
|  | Spectral Components | Voltage A-N Harmonics | H41 Voltage A-N Angle | H41 Voltage A-N Angle | 423120 | F32-4321 | R | 257287250
|  | Spectral Components | Voltage A-N Harmonics | H41 Voltage A-N Magnitude | H41 Voltage A-N Magnitude | 423116 | F32-4321 | R | 257287249
|  | Spectral Components | Voltage A-N Harmonics | H41 Voltage A-N Magnitude RMS | H41 Voltage A-N Magnitude RMS | 423118 | F32-4321 | R | 257287335
|  | Spectral Components | Voltage A-N Harmonics | H42 Voltage A-N Angle | H42 Voltage A-N Angle | 423126 | F32-4321 | R | 257287252
|  | Spectral Components | Voltage A-N Harmonics | H42 Voltage A-N Magnitude | H42 Voltage A-N Magnitude | 423122 | F32-4321 | R | 257287251
|  | Spectral Components | Voltage A-N Harmonics | H42 Voltage A-N Magnitude RMS | H42 Voltage A-N Magnitude RMS | 423124 | F32-4321 | R | 257287336
|  | Spectral Components | Voltage A-N Harmonics | H43 Voltage A-N Angle | H43 Voltage A-N Angle | 423132 | F32-4321 | R | 257287254
|  | Spectral Components | Voltage A-N Harmonics | H43 Voltage A-N Magnitude | H43 Voltage A-N Magnitude | 423128 | F32-4321 | R | 257287253
|  | Spectral Components | Voltage A-N Harmonics | H43 Voltage A-N Magnitude RMS | H43 Voltage A-N Magnitude RMS | 423130 | F32-4321 | R | 257287337
|  | Spectral Components | Voltage A-N Harmonics | H44 Voltage A-N Angle | H44 Voltage A-N Angle | 423138 | F32-4321 | R | 257287256
|  | Spectral Components | Voltage A-N Harmonics | H44 Voltage A-N Magnitude | H44 Voltage A-N Magnitude | 423134 | F32-4321 | R | 257287255
|  | Spectral Components | Voltage A-N Harmonics | H44 Voltage A-N Magnitude RMS | H44 Voltage A-N Magnitude RMS | 423136 | F32-4321 | R | 257287338
|  | Spectral Components | Voltage A-N Harmonics | H45 Voltage A-N Angle | H45 Voltage A-N Angle | 423144 | F32-4321 | R | 257287258
|  | Spectral Components | Voltage A-N Harmonics | H45 Voltage A-N Magnitude | H45 Voltage A-N Magnitude | 423140 | F32-4321 | R | 257287257
|  | Spectral Components | Voltage A-N Harmonics | H45 Voltage A-N Magnitude RMS | H45 Voltage A-N Magnitude RMS | 423142 | F32-4321 | R | 257287339
|  | Spectral Components | Voltage A-N Harmonics | H46 Voltage A-N Angle | H46 Voltage A-N Angle | 423150 | F32-4321 | R | 257287260
|  | Spectral Components | Voltage A-N Harmonics | H46 Voltage A-N Magnitude | H46 Voltage A-N Magnitude | 423146 | F32-4321 | R | 257287259
|  | Spectral Components | Voltage A-N Harmonics | H46 Voltage A-N Magnitude RMS | H46 Voltage A-N Magnitude RMS | 423148 | F32-4321 | R | 257287340
|  | Spectral Components | Voltage A-N Harmonics | H47 Voltage A-N Angle | H47 Voltage A-N Angle | 423156 | F32-4321 | R | 257287262
|  | Spectral Components | Voltage A-N Harmonics | H47 Voltage A-N Magnitude | H47 Voltage A-N Magnitude | 423152 | F32-4321 | R | 257287261
|  | Spectral Components | Voltage A-N Harmonics | H47 Voltage A-N Magnitude RMS | H47 Voltage A-N Magnitude RMS | 423154 | F32-4321 | R | 257287341
|  | Spectral Components | Voltage A-N Harmonics | H48 Voltage A-N Angle | H48 Voltage A-N Angle | 423162 | F32-4321 | R | 257287264
|  | Spectral Components | Voltage A-N Harmonics | H48 Voltage A-N Magnitude | H48 Voltage A-N Magnitude | 423158 | F32-4321 | R | 257287263
|  | Spectral Components | Voltage A-N Harmonics | H48 Voltage A-N Magnitude RMS | H48 Voltage A-N Magnitude RMS | 423160 | F32-4321 | R | 257287342
|  | Spectral Components | Voltage A-N Harmonics | H49 Voltage A-N Angle | H49 Voltage A-N Angle | 423168 | F32-4321 | R | 257287266
|  | Spectral Components | Voltage A-N Harmonics | H49 Voltage A-N Magnitude | H49 Voltage A-N Magnitude | 423164 | F32-4321 | R | 257287265
|  | Spectral Components | Voltage A-N Harmonics | H49 Voltage A-N Magnitude RMS | H49 Voltage A-N Magnitude RMS | 423166 | F32-4321 | R | 257287343
|  | Spectral Components | Voltage A-N Harmonics | H50 Voltage A-N Angle | H50 Voltage A-N Angle | 423174 | F32-4321 | R | 257287268
|  | Spectral Components | Voltage A-N Harmonics | H50 Voltage A-N Magnitude | H50 Voltage A-N Magnitude | 423170 | F32-4321 | R | 257287267
|  | Spectral Components | Voltage A-N Harmonics | H50 Voltage A-N Magnitude RMS | H50 Voltage A-N Magnitude RMS | 423172 | F32-4321 | R | 257287344
|  | Spectral Components | Voltage A-N Harmonics | H51 Voltage A-N Angle | H51 Voltage A-N Angle | 423180 | F32-4321 | R | 257287270
|  | Spectral Components | Voltage A-N Harmonics | H51 Voltage A-N Magnitude | H51 Voltage A-N Magnitude | 423176 | F32-4321 | R | 257287269
|  | Spectral Components | Voltage A-N Harmonics | H51 Voltage A-N Magnitude RMS | H51 Voltage A-N Magnitude RMS | 423178 | F32-4321 | R | 257287345
|  | Spectral Components | Voltage A-N Harmonics | H52 Voltage A-N Angle | H52 Voltage A-N Angle | 423186 | F32-4321 | R | 257287272
|  | Spectral Components | Voltage A-N Harmonics | H52 Voltage A-N Magnitude | H52 Voltage A-N Magnitude | 423182 | F32-4321 | R | 257287271
|  | Spectral Components | Voltage A-N Harmonics | H52 Voltage A-N Magnitude RMS | H52 Voltage A-N Magnitude RMS | 423184 | F32-4321 | R | 257287346
|  | Spectral Components | Voltage A-N Harmonics | H53 Voltage A-N Angle | H53 Voltage A-N Angle | 423192 | F32-4321 | R | 257287274
|  | Spectral Components | Voltage A-N Harmonics | H53 Voltage A-N Magnitude | H53 Voltage A-N Magnitude | 423188 | F32-4321 | R | 257287273
|  | Spectral Components | Voltage A-N Harmonics | H53 Voltage A-N Magnitude RMS | H53 Voltage A-N Magnitude RMS | 423190 | F32-4321 | R | 257287347
|  | Spectral Components | Voltage A-N Harmonics | H54 Voltage A-N Angle | H54 Voltage A-N Angle | 423198 | F32-4321 | R | 257287276
|  | Spectral Components | Voltage A-N Harmonics | H54 Voltage A-N Magnitude | H54 Voltage A-N Magnitude | 423194 | F32-4321 | R | 257287275
|  | Spectral Components | Voltage A-N Harmonics | H54 Voltage A-N Magnitude RMS | H54 Voltage A-N Magnitude RMS | 423196 | F32-4321 | R | 257287348
|  | Spectral Components | Voltage A-N Harmonics | H55 Voltage A-N Angle | H55 Voltage A-N Angle | 423204 | F32-4321 | R | 257287278
|  | Spectral Components | Voltage A-N Harmonics | H55 Voltage A-N Magnitude | H55 Voltage A-N Magnitude | 423200 | F32-4321 | R | 257287277
|  | Spectral Components | Voltage A-N Harmonics | H55 Voltage A-N Magnitude RMS | H55 Voltage A-N Magnitude RMS | 423202 | F32-4321 | R | 257287349
|  | Spectral Components | Voltage A-N Harmonics | H56 Voltage A-N Angle | H56 Voltage A-N Angle | 423210 | F32-4321 | R | 257287280
|  | Spectral Components | Voltage A-N Harmonics | H56 Voltage A-N Magnitude | H56 Voltage A-N Magnitude | 423206 | F32-4321 | R | 257287279
|  | Spectral Components | Voltage A-N Harmonics | H56 Voltage A-N Magnitude RMS | H56 Voltage A-N Magnitude RMS | 423208 | F32-4321 | R | 257287350
|  | Spectral Components | Voltage A-N Harmonics | H57 Voltage A-N Angle | H57 Voltage A-N Angle | 423216 | F32-4321 | R | 257287282
|  | Spectral Components | Voltage A-N Harmonics | H57 Voltage A-N Magnitude | H57 Voltage A-N Magnitude | 423212 | F32-4321 | R | 257287281
|  | Spectral Components | Voltage A-N Harmonics | H57 Voltage A-N Magnitude RMS | H57 Voltage A-N Magnitude RMS | 423214 | F32-4321 | R | 257287351
|  | Spectral Components | Voltage A-N Harmonics | H58 Voltage A-N Angle | H58 Voltage A-N Angle | 423222 | F32-4321 | R | 257287284
|  | Spectral Components | Voltage A-N Harmonics | H58 Voltage A-N Magnitude | H58 Voltage A-N Magnitude | 423218 | F32-4321 | R | 257287283
|  | Spectral Components | Voltage A-N Harmonics | H58 Voltage A-N Magnitude RMS | H58 Voltage A-N Magnitude RMS | 423220 | F32-4321 | R | 257287352
|  | Spectral Components | Voltage A-N Harmonics | H59 Voltage A-N Angle | H59 Voltage A-N Angle | 423228 | F32-4321 | R | 257287286
|  | Spectral Components | Voltage A-N Harmonics | H59 Voltage A-N Magnitude | H59 Voltage A-N Magnitude | 423224 | F32-4321 | R | 257287285
|  | Spectral Components | Voltage A-N Harmonics | H59 Voltage A-N Magnitude RMS | H59 Voltage A-N Magnitude RMS | 423226 | F32-4321 | R | 257287353
|  | Spectral Components | Voltage A-N Harmonics | H60 Voltage A-N Angle | H60 Voltage A-N Angle | 423234 | F32-4321 | R | 257287288
|  | Spectral Components | Voltage A-N Harmonics | H60 Voltage A-N Magnitude | H60 Voltage A-N Magnitude | 423230 | F32-4321 | R | 257287287
|  | Spectral Components | Voltage A-N Harmonics | H60 Voltage A-N Magnitude RMS | H60 Voltage A-N Magnitude RMS | 423232 | F32-4321 | R | 257287354
|  | Spectral Components | Voltage A-N Harmonics | H61 Voltage A-N Angle | H61 Voltage A-N Angle | 423240 | F32-4321 | R | 257287290
|  | Spectral Components | Voltage A-N Harmonics | H61 Voltage A-N Magnitude | H61 Voltage A-N Magnitude | 423236 | F32-4321 | R | 257287289
|  | Spectral Components | Voltage A-N Harmonics | H61 Voltage A-N Magnitude RMS | H61 Voltage A-N Magnitude RMS | 423238 | F32-4321 | R | 257287355
|  | Spectral Components | Voltage A-N Harmonics | H62 Voltage A-N Angle | H62 Voltage A-N Angle | 423246 | F32-4321 | R | 257287292
|  | Spectral Components | Voltage A-N Harmonics | H62 Voltage A-N Magnitude | H62 Voltage A-N Magnitude | 423242 | F32-4321 | R | 257287291
|  | Spectral Components | Voltage A-N Harmonics | H62 Voltage A-N Magnitude RMS | H62 Voltage A-N Magnitude RMS | 423244 | F32-4321 | R | 257287356
|  | Spectral Components | Voltage A-N Harmonics | H63 Voltage A-N Angle | H63 Voltage A-N Angle | 423252 | F32-4321 | R | 257287294
|  | Spectral Components | Voltage A-N Harmonics | H63 Voltage A-N Magnitude | H63 Voltage A-N Magnitude | 423248 | F32-4321 | R | 257287293
|  | Spectral Components | Voltage A-N Harmonics | H63 Voltage A-N Magnitude RMS | H63 Voltage A-N Magnitude RMS | 423250 | F32-4321 | R | 257287357
|  | Spectral Components | Voltage B-C Harmonics | H1 Voltage B-C Angle | H1 Voltage B-C Angle | 422104 | F32-4321 | R | 257286658
|  | Spectral Components | Voltage B-C Harmonics | H1 Voltage B-C Magnitude | H1 Voltage B-C Magnitude | 422100 | F32-4321 | R | 257286657
|  | Spectral Components | Voltage B-C Harmonics | H1 Voltage B-C Magnitude RMS | H1 Voltage B-C Magnitude RMS | 422102 | F32-4321 | R | 257286783
|  | Spectral Components | Voltage B-C Harmonics | H2 Voltage B-C Angle | H2 Voltage B-C Angle | 422110 | F32-4321 | R | 257286660
|  | Spectral Components | Voltage B-C Harmonics | H2 Voltage B-C Magnitude | H2 Voltage B-C Magnitude | 422106 | F32-4321 | R | 257286659
|  | Spectral Components | Voltage B-C Harmonics | H2 Voltage B-C Magnitude RMS | H2 Voltage B-C Magnitude RMS | 422108 | F32-4321 | R | 257286784
|  | Spectral Components | Voltage B-C Harmonics | H3 Voltage B-C Angle | H3 Voltage B-C Angle | 422116 | F32-4321 | R | 257286662
|  | Spectral Components | Voltage B-C Harmonics | H3 Voltage B-C Magnitude | H3 Voltage B-C Magnitude | 422112 | F32-4321 | R | 257286661
|  | Spectral Components | Voltage B-C Harmonics | H3 Voltage B-C Magnitude RMS | H3 Voltage B-C Magnitude RMS | 422114 | F32-4321 | R | 257286785
|  | Spectral Components | Voltage B-C Harmonics | H4 Voltage B-C Angle | H4 Voltage B-C Angle | 422122 | F32-4321 | R | 257286664
|  | Spectral Components | Voltage B-C Harmonics | H4 Voltage B-C Magnitude | H4 Voltage B-C Magnitude | 422118 | F32-4321 | R | 257286663
|  | Spectral Components | Voltage B-C Harmonics | H4 Voltage B-C Magnitude RMS | H4 Voltage B-C Magnitude RMS | 422120 | F32-4321 | R | 257286786
|  | Spectral Components | Voltage B-C Harmonics | H5 Voltage B-C Angle | H5 Voltage B-C Angle | 422128 | F32-4321 | R | 257286666
|  | Spectral Components | Voltage B-C Harmonics | H5 Voltage B-C Magnitude | H5 Voltage B-C Magnitude | 422124 | F32-4321 | R | 257286665
|  | Spectral Components | Voltage B-C Harmonics | H5 Voltage B-C Magnitude RMS | H5 Voltage B-C Magnitude RMS | 422126 | F32-4321 | R | 257286787
|  | Spectral Components | Voltage B-C Harmonics | H6 Voltage B-C Angle | H6 Voltage B-C Angle | 422134 | F32-4321 | R | 257286668
|  | Spectral Components | Voltage B-C Harmonics | H6 Voltage B-C Magnitude | H6 Voltage B-C Magnitude | 422130 | F32-4321 | R | 257286667
|  | Spectral Components | Voltage B-C Harmonics | H6 Voltage B-C Magnitude RMS | H6 Voltage B-C Magnitude RMS | 422132 | F32-4321 | R | 257286788
|  | Spectral Components | Voltage B-C Harmonics | H7 Voltage B-C Angle | H7 Voltage B-C Angle | 422140 | F32-4321 | R | 257286670
|  | Spectral Components | Voltage B-C Harmonics | H7 Voltage B-C Magnitude | H7 Voltage B-C Magnitude | 422136 | F32-4321 | R | 257286669
|  | Spectral Components | Voltage B-C Harmonics | H7 Voltage B-C Magnitude RMS | H7 Voltage B-C Magnitude RMS | 422138 | F32-4321 | R | 257286789
|  | Spectral Components | Voltage B-C Harmonics | H8 Voltage B-C Angle | H8 Voltage B-C Angle | 422146 | F32-4321 | R | 257286672
|  | Spectral Components | Voltage B-C Harmonics | H8 Voltage B-C Magnitude | H8 Voltage B-C Magnitude | 422142 | F32-4321 | R | 257286671
|  | Spectral Components | Voltage B-C Harmonics | H8 Voltage B-C Magnitude RMS | H8 Voltage B-C Magnitude RMS | 422144 | F32-4321 | R | 257286790
|  | Spectral Components | Voltage B-C Harmonics | H9 Voltage B-C Angle | H9 Voltage B-C Angle | 422152 | F32-4321 | R | 257286674
|  | Spectral Components | Voltage B-C Harmonics | H9 Voltage B-C Magnitude | H9 Voltage B-C Magnitude | 422148 | F32-4321 | R | 257286673
|  | Spectral Components | Voltage B-C Harmonics | H9 Voltage B-C Magnitude RMS | H9 Voltage B-C Magnitude RMS | 422150 | F32-4321 | R | 257286791
|  | Spectral Components | Voltage B-C Harmonics | H10 Voltage B-C Angle | H10 Voltage B-C Angle | 422158 | F32-4321 | R | 257286676
|  | Spectral Components | Voltage B-C Harmonics | H10 Voltage B-C Magnitude | H10 Voltage B-C Magnitude | 422154 | F32-4321 | R | 257286675
|  | Spectral Components | Voltage B-C Harmonics | H10 Voltage B-C Magnitude RMS | H10 Voltage B-C Magnitude RMS | 422156 | F32-4321 | R | 257286792
|  | Spectral Components | Voltage B-C Harmonics | H11 Voltage B-C Angle | H11 Voltage B-C Angle | 422164 | F32-4321 | R | 257286678
|  | Spectral Components | Voltage B-C Harmonics | H11 Voltage B-C Magnitude | H11 Voltage B-C Magnitude | 422160 | F32-4321 | R | 257286677
|  | Spectral Components | Voltage B-C Harmonics | H11 Voltage B-C Magnitude RMS | H11 Voltage B-C Magnitude RMS | 422162 | F32-4321 | R | 257286793
|  | Spectral Components | Voltage B-C Harmonics | H12 Voltage B-C Angle | H12 Voltage B-C Angle | 422170 | F32-4321 | R | 257286680
|  | Spectral Components | Voltage B-C Harmonics | H12 Voltage B-C Magnitude | H12 Voltage B-C Magnitude | 422166 | F32-4321 | R | 257286679
|  | Spectral Components | Voltage B-C Harmonics | H12 Voltage B-C Magnitude RMS | H12 Voltage B-C Magnitude RMS | 422168 | F32-4321 | R | 257286794
|  | Spectral Components | Voltage B-C Harmonics | H13 Voltage B-C Angle | H13 Voltage B-C Angle | 422176 | F32-4321 | R | 257286682
|  | Spectral Components | Voltage B-C Harmonics | H13 Voltage B-C Magnitude | H13 Voltage B-C Magnitude | 422172 | F32-4321 | R | 257286681
|  | Spectral Components | Voltage B-C Harmonics | H13 Voltage B-C Magnitude RMS | H13 Voltage B-C Magnitude RMS | 422174 | F32-4321 | R | 257286795
|  | Spectral Components | Voltage B-C Harmonics | H14 Voltage B-C Angle | H14 Voltage B-C Angle | 422182 | F32-4321 | R | 257286684
|  | Spectral Components | Voltage B-C Harmonics | H14 Voltage B-C Magnitude | H14 Voltage B-C Magnitude | 422178 | F32-4321 | R | 257286683
|  | Spectral Components | Voltage B-C Harmonics | H14 Voltage B-C Magnitude RMS | H14 Voltage B-C Magnitude RMS | 422180 | F32-4321 | R | 257286796
|  | Spectral Components | Voltage B-C Harmonics | H15 Voltage B-C Angle | H15 Voltage B-C Angle | 422188 | F32-4321 | R | 257286686
|  | Spectral Components | Voltage B-C Harmonics | H15 Voltage B-C Magnitude | H15 Voltage B-C Magnitude | 422184 | F32-4321 | R | 257286685
|  | Spectral Components | Voltage B-C Harmonics | H15 Voltage B-C Magnitude RMS | H15 Voltage B-C Magnitude RMS | 422186 | F32-4321 | R | 257286797
|  | Spectral Components | Voltage B-C Harmonics | H16 Voltage B-C Angle | H16 Voltage B-C Angle | 422194 | F32-4321 | R | 257286688
|  | Spectral Components | Voltage B-C Harmonics | H16 Voltage B-C Magnitude | H16 Voltage B-C Magnitude | 422190 | F32-4321 | R | 257286687
|  | Spectral Components | Voltage B-C Harmonics | H16 Voltage B-C Magnitude RMS | H16 Voltage B-C Magnitude RMS | 422192 | F32-4321 | R | 257286798
|  | Spectral Components | Voltage B-C Harmonics | H17 Voltage B-C Angle | H17 Voltage B-C Angle | 422200 | F32-4321 | R | 257286690
|  | Spectral Components | Voltage B-C Harmonics | H17 Voltage B-C Magnitude | H17 Voltage B-C Magnitude | 422196 | F32-4321 | R | 257286689
|  | Spectral Components | Voltage B-C Harmonics | H17 Voltage B-C Magnitude RMS | H17 Voltage B-C Magnitude RMS | 422198 | F32-4321 | R | 257286799
|  | Spectral Components | Voltage B-C Harmonics | H18 Voltage B-C Angle | H18 Voltage B-C Angle | 422206 | F32-4321 | R | 257286692
|  | Spectral Components | Voltage B-C Harmonics | H18 Voltage B-C Magnitude | H18 Voltage B-C Magnitude | 422202 | F32-4321 | R | 257286691
|  | Spectral Components | Voltage B-C Harmonics | H18 Voltage B-C Magnitude RMS | H18 Voltage B-C Magnitude RMS | 422204 | F32-4321 | R | 257286800
|  | Spectral Components | Voltage B-C Harmonics | H19 Voltage B-C Angle | H19 Voltage B-C Angle | 422212 | F32-4321 | R | 257286694
|  | Spectral Components | Voltage B-C Harmonics | H19 Voltage B-C Magnitude | H19 Voltage B-C Magnitude | 422208 | F32-4321 | R | 257286693
|  | Spectral Components | Voltage B-C Harmonics | H19 Voltage B-C Magnitude RMS | H19 Voltage B-C Magnitude RMS | 422210 | F32-4321 | R | 257286801
|  | Spectral Components | Voltage B-C Harmonics | H20 Voltage B-C Angle | H20 Voltage B-C Angle | 422218 | F32-4321 | R | 257286696
|  | Spectral Components | Voltage B-C Harmonics | H20 Voltage B-C Magnitude | H20 Voltage B-C Magnitude | 422214 | F32-4321 | R | 257286695
|  | Spectral Components | Voltage B-C Harmonics | H20 Voltage B-C Magnitude RMS | H20 Voltage B-C Magnitude RMS | 422216 | F32-4321 | R | 257286802
|  | Spectral Components | Voltage B-C Harmonics | H21 Voltage B-C Angle | H21 Voltage B-C Angle | 422224 | F32-4321 | R | 257286698
|  | Spectral Components | Voltage B-C Harmonics | H21 Voltage B-C Magnitude | H21 Voltage B-C Magnitude | 422220 | F32-4321 | R | 257286697
|  | Spectral Components | Voltage B-C Harmonics | H21 Voltage B-C Magnitude RMS | H21 Voltage B-C Magnitude RMS | 422222 | F32-4321 | R | 257286803
|  | Spectral Components | Voltage B-C Harmonics | H22 Voltage B-C Angle | H22 Voltage B-C Angle | 422230 | F32-4321 | R | 257286700
|  | Spectral Components | Voltage B-C Harmonics | H22 Voltage B-C Magnitude | H22 Voltage B-C Magnitude | 422226 | F32-4321 | R | 257286699
|  | Spectral Components | Voltage B-C Harmonics | H22 Voltage B-C Magnitude RMS | H22 Voltage B-C Magnitude RMS | 422228 | F32-4321 | R | 257286804
|  | Spectral Components | Voltage B-C Harmonics | H23 Voltage B-C Angle | H23 Voltage B-C Angle | 422236 | F32-4321 | R | 257286702
|  | Spectral Components | Voltage B-C Harmonics | H23 Voltage B-C Magnitude | H23 Voltage B-C Magnitude | 422232 | F32-4321 | R | 257286701
|  | Spectral Components | Voltage B-C Harmonics | H23 Voltage B-C Magnitude RMS | H23 Voltage B-C Magnitude RMS | 422234 | F32-4321 | R | 257286805
|  | Spectral Components | Voltage B-C Harmonics | H24 Voltage B-C Angle | H24 Voltage B-C Angle | 422242 | F32-4321 | R | 257286704
|  | Spectral Components | Voltage B-C Harmonics | H24 Voltage B-C Magnitude | H24 Voltage B-C Magnitude | 422238 | F32-4321 | R | 257286703
|  | Spectral Components | Voltage B-C Harmonics | H24 Voltage B-C Magnitude RMS | H24 Voltage B-C Magnitude RMS | 422240 | F32-4321 | R | 257286806
|  | Spectral Components | Voltage B-C Harmonics | H25 Voltage B-C Angle | H25 Voltage B-C Angle | 422248 | F32-4321 | R | 257286706
|  | Spectral Components | Voltage B-C Harmonics | H25 Voltage B-C Magnitude | H25 Voltage B-C Magnitude | 422244 | F32-4321 | R | 257286705
|  | Spectral Components | Voltage B-C Harmonics | H25 Voltage B-C Magnitude RMS | H25 Voltage B-C Magnitude RMS | 422246 | F32-4321 | R | 257286807
|  | Spectral Components | Voltage B-C Harmonics | H26 Voltage B-C Angle | H26 Voltage B-C Angle | 422254 | F32-4321 | R | 257286708
|  | Spectral Components | Voltage B-C Harmonics | H26 Voltage B-C Magnitude | H26 Voltage B-C Magnitude | 422250 | F32-4321 | R | 257286707
|  | Spectral Components | Voltage B-C Harmonics | H26 Voltage B-C Magnitude RMS | H26 Voltage B-C Magnitude RMS | 422252 | F32-4321 | R | 257286808
|  | Spectral Components | Voltage B-C Harmonics | H27 Voltage B-C Angle | H27 Voltage B-C Angle | 422260 | F32-4321 | R | 257286710
|  | Spectral Components | Voltage B-C Harmonics | H27 Voltage B-C Magnitude | H27 Voltage B-C Magnitude | 422256 | F32-4321 | R | 257286709
|  | Spectral Components | Voltage B-C Harmonics | H27 Voltage B-C Magnitude RMS | H27 Voltage B-C Magnitude RMS | 422258 | F32-4321 | R | 257286809
|  | Spectral Components | Voltage B-C Harmonics | H28 Voltage B-C Angle | H28 Voltage B-C Angle | 422266 | F32-4321 | R | 257286712
|  | Spectral Components | Voltage B-C Harmonics | H28 Voltage B-C Magnitude | H28 Voltage B-C Magnitude | 422262 | F32-4321 | R | 257286711
|  | Spectral Components | Voltage B-C Harmonics | H28 Voltage B-C Magnitude RMS | H28 Voltage B-C Magnitude RMS | 422264 | F32-4321 | R | 257286810
|  | Spectral Components | Voltage B-C Harmonics | H29 Voltage B-C Angle | H29 Voltage B-C Angle | 422272 | F32-4321 | R | 257286714
|  | Spectral Components | Voltage B-C Harmonics | H29 Voltage B-C Magnitude | H29 Voltage B-C Magnitude | 422268 | F32-4321 | R | 257286713
|  | Spectral Components | Voltage B-C Harmonics | H29 Voltage B-C Magnitude RMS | H29 Voltage B-C Magnitude RMS | 422270 | F32-4321 | R | 257286811
|  | Spectral Components | Voltage B-C Harmonics | H30 Voltage B-C Angle | H30 Voltage B-C Angle | 422278 | F32-4321 | R | 257286716
|  | Spectral Components | Voltage B-C Harmonics | H30 Voltage B-C Magnitude | H30 Voltage B-C Magnitude | 422274 | F32-4321 | R | 257286715
|  | Spectral Components | Voltage B-C Harmonics | H30 Voltage B-C Magnitude RMS | H30 Voltage B-C Magnitude RMS | 422276 | F32-4321 | R | 257286812
|  | Spectral Components | Voltage B-C Harmonics | H31 Voltage B-C Angle | H31 Voltage B-C Angle | 422284 | F32-4321 | R | 257286718
|  | Spectral Components | Voltage B-C Harmonics | H31 Voltage B-C Magnitude | H31 Voltage B-C Magnitude | 422280 | F32-4321 | R | 257286717
|  | Spectral Components | Voltage B-C Harmonics | H31 Voltage B-C Magnitude RMS | H31 Voltage B-C Magnitude RMS | 422282 | F32-4321 | R | 257286813
|  | Spectral Components | Voltage B-C Harmonics | H32 Voltage B-C Angle | H32 Voltage B-C Angle | 422290 | F32-4321 | R | 257286720
|  | Spectral Components | Voltage B-C Harmonics | H32 Voltage B-C Magnitude | H32 Voltage B-C Magnitude | 422286 | F32-4321 | R | 257286719
|  | Spectral Components | Voltage B-C Harmonics | H32 Voltage B-C Magnitude RMS | H32 Voltage B-C Magnitude RMS | 422288 | F32-4321 | R | 257286814
|  | Spectral Components | Voltage B-C Harmonics | H33 Voltage B-C Angle | H33 Voltage B-C Angle | 422296 | F32-4321 | R | 257286722
|  | Spectral Components | Voltage B-C Harmonics | H33 Voltage B-C Magnitude | H33 Voltage B-C Magnitude | 422292 | F32-4321 | R | 257286721
|  | Spectral Components | Voltage B-C Harmonics | H33 Voltage B-C Magnitude RMS | H33 Voltage B-C Magnitude RMS | 422294 | F32-4321 | R | 257286815
|  | Spectral Components | Voltage B-C Harmonics | H34 Voltage B-C Angle | H34 Voltage B-C Angle | 422302 | F32-4321 | R | 257286724
|  | Spectral Components | Voltage B-C Harmonics | H34 Voltage B-C Magnitude | H34 Voltage B-C Magnitude | 422298 | F32-4321 | R | 257286723
|  | Spectral Components | Voltage B-C Harmonics | H34 Voltage B-C Magnitude RMS | H34 Voltage B-C Magnitude RMS | 422300 | F32-4321 | R | 257286816
|  | Spectral Components | Voltage B-C Harmonics | H35 Voltage B-C Angle | H35 Voltage B-C Angle | 422308 | F32-4321 | R | 257286726
|  | Spectral Components | Voltage B-C Harmonics | H35 Voltage B-C Magnitude | H35 Voltage B-C Magnitude | 422304 | F32-4321 | R | 257286725
|  | Spectral Components | Voltage B-C Harmonics | H35 Voltage B-C Magnitude RMS | H35 Voltage B-C Magnitude RMS | 422306 | F32-4321 | R | 257286817
|  | Spectral Components | Voltage B-C Harmonics | H36 Voltage B-C Angle | H36 Voltage B-C Angle | 422314 | F32-4321 | R | 257286728
|  | Spectral Components | Voltage B-C Harmonics | H36 Voltage B-C Magnitude | H36 Voltage B-C Magnitude | 422310 | F32-4321 | R | 257286727
|  | Spectral Components | Voltage B-C Harmonics | H36 Voltage B-C Magnitude RMS | H36 Voltage B-C Magnitude RMS | 422312 | F32-4321 | R | 257286818
|  | Spectral Components | Voltage B-C Harmonics | H37 Voltage B-C Angle | H37 Voltage B-C Angle | 422320 | F32-4321 | R | 257286730
|  | Spectral Components | Voltage B-C Harmonics | H37 Voltage B-C Magnitude | H37 Voltage B-C Magnitude | 422316 | F32-4321 | R | 257286729
|  | Spectral Components | Voltage B-C Harmonics | H37 Voltage B-C Magnitude RMS | H37 Voltage B-C Magnitude RMS | 422318 | F32-4321 | R | 257286819
|  | Spectral Components | Voltage B-C Harmonics | H38 Voltage B-C Angle | H38 Voltage B-C Angle | 422326 | F32-4321 | R | 257286732
|  | Spectral Components | Voltage B-C Harmonics | H38 Voltage B-C Magnitude | H38 Voltage B-C Magnitude | 422322 | F32-4321 | R | 257286731
|  | Spectral Components | Voltage B-C Harmonics | H38 Voltage B-C Magnitude RMS | H38 Voltage B-C Magnitude RMS | 422324 | F32-4321 | R | 257286820
|  | Spectral Components | Voltage B-C Harmonics | H39 Voltage B-C Angle | H39 Voltage B-C Angle | 422332 | F32-4321 | R | 257286734
|  | Spectral Components | Voltage B-C Harmonics | H39 Voltage B-C Magnitude | H39 Voltage B-C Magnitude | 422328 | F32-4321 | R | 257286733
|  | Spectral Components | Voltage B-C Harmonics | H39 Voltage B-C Magnitude RMS | H39 Voltage B-C Magnitude RMS | 422330 | F32-4321 | R | 257286821
|  | Spectral Components | Voltage B-C Harmonics | H40 Voltage B-C Angle | H40 Voltage B-C Angle | 422338 | F32-4321 | R | 257286736
|  | Spectral Components | Voltage B-C Harmonics | H40 Voltage B-C Magnitude | H40 Voltage B-C Magnitude | 422334 | F32-4321 | R | 257286735
|  | Spectral Components | Voltage B-C Harmonics | H40 Voltage B-C Magnitude RMS | H40 Voltage B-C Magnitude RMS | 422336 | F32-4321 | R | 257286822
|  | Spectral Components | Voltage B-C Harmonics | H41 Voltage B-C Angle | H41 Voltage B-C Angle | 422344 | F32-4321 | R | 257286738
|  | Spectral Components | Voltage B-C Harmonics | H41 Voltage B-C Magnitude | H41 Voltage B-C Magnitude | 422340 | F32-4321 | R | 257286737
|  | Spectral Components | Voltage B-C Harmonics | H41 Voltage B-C Magnitude RMS | H41 Voltage B-C Magnitude RMS | 422342 | F32-4321 | R | 257286823
|  | Spectral Components | Voltage B-C Harmonics | H42 Voltage B-C Angle | H42 Voltage B-C Angle | 422350 | F32-4321 | R | 257286740
|  | Spectral Components | Voltage B-C Harmonics | H42 Voltage B-C Magnitude | H42 Voltage B-C Magnitude | 422346 | F32-4321 | R | 257286739
|  | Spectral Components | Voltage B-C Harmonics | H42 Voltage B-C Magnitude RMS | H42 Voltage B-C Magnitude RMS | 422348 | F32-4321 | R | 257286824
|  | Spectral Components | Voltage B-C Harmonics | H43 Voltage B-C Angle | H43 Voltage B-C Angle | 422356 | F32-4321 | R | 257286742
|  | Spectral Components | Voltage B-C Harmonics | H43 Voltage B-C Magnitude | H43 Voltage B-C Magnitude | 422352 | F32-4321 | R | 257286741
|  | Spectral Components | Voltage B-C Harmonics | H43 Voltage B-C Magnitude RMS | H43 Voltage B-C Magnitude RMS | 422354 | F32-4321 | R | 257286825
|  | Spectral Components | Voltage B-C Harmonics | H44 Voltage B-C Angle | H44 Voltage B-C Angle | 422362 | F32-4321 | R | 257286744
|  | Spectral Components | Voltage B-C Harmonics | H44 Voltage B-C Magnitude | H44 Voltage B-C Magnitude | 422358 | F32-4321 | R | 257286743
|  | Spectral Components | Voltage B-C Harmonics | H44 Voltage B-C Magnitude RMS | H44 Voltage B-C Magnitude RMS | 422360 | F32-4321 | R | 257286826
|  | Spectral Components | Voltage B-C Harmonics | H45 Voltage B-C Angle | H45 Voltage B-C Angle | 422368 | F32-4321 | R | 257286746
|  | Spectral Components | Voltage B-C Harmonics | H45 Voltage B-C Magnitude | H45 Voltage B-C Magnitude | 422364 | F32-4321 | R | 257286745
|  | Spectral Components | Voltage B-C Harmonics | H45 Voltage B-C Magnitude RMS | H45 Voltage B-C Magnitude RMS | 422366 | F32-4321 | R | 257286827
|  | Spectral Components | Voltage B-C Harmonics | H46 Voltage B-C Angle | H46 Voltage B-C Angle | 422374 | F32-4321 | R | 257286748
|  | Spectral Components | Voltage B-C Harmonics | H46 Voltage B-C Magnitude | H46 Voltage B-C Magnitude | 422370 | F32-4321 | R | 257286747
|  | Spectral Components | Voltage B-C Harmonics | H46 Voltage B-C Magnitude RMS | H46 Voltage B-C Magnitude RMS | 422372 | F32-4321 | R | 257286828
|  | Spectral Components | Voltage B-C Harmonics | H47 Voltage B-C Angle | H47 Voltage B-C Angle | 422380 | F32-4321 | R | 257286750
|  | Spectral Components | Voltage B-C Harmonics | H47 Voltage B-C Magnitude | H47 Voltage B-C Magnitude | 422376 | F32-4321 | R | 257286749
|  | Spectral Components | Voltage B-C Harmonics | H47 Voltage B-C Magnitude RMS | H47 Voltage B-C Magnitude RMS | 422378 | F32-4321 | R | 257286829
|  | Spectral Components | Voltage B-C Harmonics | H48 Voltage B-C Angle | H48 Voltage B-C Angle | 422386 | F32-4321 | R | 257286752
|  | Spectral Components | Voltage B-C Harmonics | H48 Voltage B-C Magnitude | H48 Voltage B-C Magnitude | 422382 | F32-4321 | R | 257286751
|  | Spectral Components | Voltage B-C Harmonics | H48 Voltage B-C Magnitude RMS | H48 Voltage B-C Magnitude RMS | 422384 | F32-4321 | R | 257286830
|  | Spectral Components | Voltage B-C Harmonics | H49 Voltage B-C Angle | H49 Voltage B-C Angle | 422392 | F32-4321 | R | 257286754
|  | Spectral Components | Voltage B-C Harmonics | H49 Voltage B-C Magnitude | H49 Voltage B-C Magnitude | 422388 | F32-4321 | R | 257286753
|  | Spectral Components | Voltage B-C Harmonics | H49 Voltage B-C Magnitude RMS | H49 Voltage B-C Magnitude RMS | 422390 | F32-4321 | R | 257286831
|  | Spectral Components | Voltage B-C Harmonics | H50 Voltage B-C Angle | H50 Voltage B-C Angle | 422398 | F32-4321 | R | 257286756
|  | Spectral Components | Voltage B-C Harmonics | H50 Voltage B-C Magnitude | H50 Voltage B-C Magnitude | 422394 | F32-4321 | R | 257286755
|  | Spectral Components | Voltage B-C Harmonics | H50 Voltage B-C Magnitude RMS | H50 Voltage B-C Magnitude RMS | 422396 | F32-4321 | R | 257286832
|  | Spectral Components | Voltage B-C Harmonics | H51 Voltage B-C Angle | H51 Voltage B-C Angle | 422404 | F32-4321 | R | 257286758
|  | Spectral Components | Voltage B-C Harmonics | H51 Voltage B-C Magnitude | H51 Voltage B-C Magnitude | 422400 | F32-4321 | R | 257286757
|  | Spectral Components | Voltage B-C Harmonics | H51 Voltage B-C Magnitude RMS | H51 Voltage B-C Magnitude RMS | 422402 | F32-4321 | R | 257286833
|  | Spectral Components | Voltage B-C Harmonics | H52 Voltage B-C Angle | H52 Voltage B-C Angle | 422410 | F32-4321 | R | 257286760
|  | Spectral Components | Voltage B-C Harmonics | H52 Voltage B-C Magnitude | H52 Voltage B-C Magnitude | 422406 | F32-4321 | R | 257286759
|  | Spectral Components | Voltage B-C Harmonics | H52 Voltage B-C Magnitude RMS | H52 Voltage B-C Magnitude RMS | 422408 | F32-4321 | R | 257286834
|  | Spectral Components | Voltage B-C Harmonics | H53 Voltage B-C Angle | H53 Voltage B-C Angle | 422416 | F32-4321 | R | 257286762
|  | Spectral Components | Voltage B-C Harmonics | H53 Voltage B-C Magnitude | H53 Voltage B-C Magnitude | 422412 | F32-4321 | R | 257286761
|  | Spectral Components | Voltage B-C Harmonics | H53 Voltage B-C Magnitude RMS | H53 Voltage B-C Magnitude RMS | 422414 | F32-4321 | R | 257286835
|  | Spectral Components | Voltage B-C Harmonics | H54 Voltage B-C Angle | H54 Voltage B-C Angle | 422422 | F32-4321 | R | 257286764
|  | Spectral Components | Voltage B-C Harmonics | H54 Voltage B-C Magnitude | H54 Voltage B-C Magnitude | 422418 | F32-4321 | R | 257286763
|  | Spectral Components | Voltage B-C Harmonics | H54 Voltage B-C Magnitude RMS | H54 Voltage B-C Magnitude RMS | 422420 | F32-4321 | R | 257286836
|  | Spectral Components | Voltage B-C Harmonics | H55 Voltage B-C Angle | H55 Voltage B-C Angle | 422428 | F32-4321 | R | 257286766
|  | Spectral Components | Voltage B-C Harmonics | H55 Voltage B-C Magnitude | H55 Voltage B-C Magnitude | 422424 | F32-4321 | R | 257286765
|  | Spectral Components | Voltage B-C Harmonics | H55 Voltage B-C Magnitude RMS | H55 Voltage B-C Magnitude RMS | 422426 | F32-4321 | R | 257286837
|  | Spectral Components | Voltage B-C Harmonics | H56 Voltage B-C Angle | H56 Voltage B-C Angle | 422434 | F32-4321 | R | 257286768
|  | Spectral Components | Voltage B-C Harmonics | H56 Voltage B-C Magnitude | H56 Voltage B-C Magnitude | 422430 | F32-4321 | R | 257286767
|  | Spectral Components | Voltage B-C Harmonics | H56 Voltage B-C Magnitude RMS | H56 Voltage B-C Magnitude RMS | 422432 | F32-4321 | R | 257286838
|  | Spectral Components | Voltage B-C Harmonics | H57 Voltage B-C Angle | H57 Voltage B-C Angle | 422440 | F32-4321 | R | 257286770
|  | Spectral Components | Voltage B-C Harmonics | H57 Voltage B-C Magnitude | H57 Voltage B-C Magnitude | 422436 | F32-4321 | R | 257286769
|  | Spectral Components | Voltage B-C Harmonics | H57 Voltage B-C Magnitude RMS | H57 Voltage B-C Magnitude RMS | 422438 | F32-4321 | R | 257286839
|  | Spectral Components | Voltage B-C Harmonics | H58 Voltage B-C Angle | H58 Voltage B-C Angle | 422446 | F32-4321 | R | 257286772
|  | Spectral Components | Voltage B-C Harmonics | H58 Voltage B-C Magnitude | H58 Voltage B-C Magnitude | 422442 | F32-4321 | R | 257286771
|  | Spectral Components | Voltage B-C Harmonics | H58 Voltage B-C Magnitude RMS | H58 Voltage B-C Magnitude RMS | 422444 | F32-4321 | R | 257286840
|  | Spectral Components | Voltage B-C Harmonics | H59 Voltage B-C Angle | H59 Voltage B-C Angle | 422452 | F32-4321 | R | 257286774
|  | Spectral Components | Voltage B-C Harmonics | H59 Voltage B-C Magnitude | H59 Voltage B-C Magnitude | 422448 | F32-4321 | R | 257286773
|  | Spectral Components | Voltage B-C Harmonics | H59 Voltage B-C Magnitude RMS | H59 Voltage B-C Magnitude RMS | 422450 | F32-4321 | R | 257286841
|  | Spectral Components | Voltage B-C Harmonics | H60 Voltage B-C Angle | H60 Voltage B-C Angle | 422458 | F32-4321 | R | 257286776
|  | Spectral Components | Voltage B-C Harmonics | H60 Voltage B-C Magnitude | H60 Voltage B-C Magnitude | 422454 | F32-4321 | R | 257286775
|  | Spectral Components | Voltage B-C Harmonics | H60 Voltage B-C Magnitude RMS | H60 Voltage B-C Magnitude RMS | 422456 | F32-4321 | R | 257286842
|  | Spectral Components | Voltage B-C Harmonics | H61 Voltage B-C Angle | H61 Voltage B-C Angle | 422464 | F32-4321 | R | 257286778
|  | Spectral Components | Voltage B-C Harmonics | H61 Voltage B-C Magnitude | H61 Voltage B-C Magnitude | 422460 | F32-4321 | R | 257286777
|  | Spectral Components | Voltage B-C Harmonics | H61 Voltage B-C Magnitude RMS | H61 Voltage B-C Magnitude RMS | 422462 | F32-4321 | R | 257286843
|  | Spectral Components | Voltage B-C Harmonics | H62 Voltage B-C Angle | H62 Voltage B-C Angle | 422470 | F32-4321 | R | 257286780
|  | Spectral Components | Voltage B-C Harmonics | H62 Voltage B-C Magnitude | H62 Voltage B-C Magnitude | 422466 | F32-4321 | R | 257286779
|  | Spectral Components | Voltage B-C Harmonics | H62 Voltage B-C Magnitude RMS | H62 Voltage B-C Magnitude RMS | 422468 | F32-4321 | R | 257286844
|  | Spectral Components | Voltage B-C Harmonics | H63 Voltage B-C Angle | H63 Voltage B-C Angle | 422476 | F32-4321 | R | 257286782
|  | Spectral Components | Voltage B-C Harmonics | H63 Voltage B-C Magnitude | H63 Voltage B-C Magnitude | 422472 | F32-4321 | R | 257286781
|  | Spectral Components | Voltage B-C Harmonics | H63 Voltage B-C Magnitude RMS | H63 Voltage B-C Magnitude RMS | 422474 | F32-4321 | R | 257286845
|  | Spectral Components | Voltage B-N Harmonics | H1 Voltage B-N Angle | H1 Voltage B-N Angle | 423268 | F32-4321 | R | 257287426
|  | Spectral Components | Voltage B-N Harmonics | H1 Voltage B-N Magnitude | H1 Voltage B-N Magnitude | 423264 | F32-4321 | R | 257287425
|  | Spectral Components | Voltage B-N Harmonics | H1 Voltage B-N Magnitude RMS | H1 Voltage B-N Magnitude RMS | 423266 | F32-4321 | R | 257287551
|  | Spectral Components | Voltage B-N Harmonics | H2 Voltage B-N Angle | H2 Voltage B-N Angle | 423274 | F32-4321 | R | 257287428
|  | Spectral Components | Voltage B-N Harmonics | H2 Voltage B-N Magnitude | H2 Voltage B-N Magnitude | 423270 | F32-4321 | R | 257287427
|  | Spectral Components | Voltage B-N Harmonics | H2 Voltage B-N Magnitude RMS | H2 Voltage B-N Magnitude RMS | 423272 | F32-4321 | R | 257287552
|  | Spectral Components | Voltage B-N Harmonics | H3 Voltage B-N Angle | H3 Voltage B-N Angle | 423280 | F32-4321 | R | 257287430
|  | Spectral Components | Voltage B-N Harmonics | H3 Voltage B-N Magnitude | H3 Voltage B-N Magnitude | 423276 | F32-4321 | R | 257287429
|  | Spectral Components | Voltage B-N Harmonics | H3 Voltage B-N Magnitude RMS | H3 Voltage B-N Magnitude RMS | 423278 | F32-4321 | R | 257287553
|  | Spectral Components | Voltage B-N Harmonics | H4 Voltage B-N Angle | H4 Voltage B-N Angle | 423286 | F32-4321 | R | 257287432
|  | Spectral Components | Voltage B-N Harmonics | H4 Voltage B-N Magnitude | H4 Voltage B-N Magnitude | 423282 | F32-4321 | R | 257287431
|  | Spectral Components | Voltage B-N Harmonics | H4 Voltage B-N Magnitude RMS | H4 Voltage B-N Magnitude RMS | 423284 | F32-4321 | R | 257287554
|  | Spectral Components | Voltage B-N Harmonics | H5 Voltage B-N Angle | H5 Voltage B-N Angle | 423292 | F32-4321 | R | 257287434
|  | Spectral Components | Voltage B-N Harmonics | H5 Voltage B-N Magnitude | H5 Voltage B-N Magnitude | 423288 | F32-4321 | R | 257287433
|  | Spectral Components | Voltage B-N Harmonics | H5 Voltage B-N Magnitude RMS | H5 Voltage B-N Magnitude RMS | 423290 | F32-4321 | R | 257287555
|  | Spectral Components | Voltage B-N Harmonics | H6 Voltage B-N Angle | H6 Voltage B-N Angle | 423298 | F32-4321 | R | 257287436
|  | Spectral Components | Voltage B-N Harmonics | H6 Voltage B-N Magnitude | H6 Voltage B-N Magnitude | 423294 | F32-4321 | R | 257287435
|  | Spectral Components | Voltage B-N Harmonics | H6 Voltage B-N Magnitude RMS | H6 Voltage B-N Magnitude RMS | 423296 | F32-4321 | R | 257287556
|  | Spectral Components | Voltage B-N Harmonics | H7 Voltage B-N Angle | H7 Voltage B-N Angle | 423304 | F32-4321 | R | 257287438
|  | Spectral Components | Voltage B-N Harmonics | H7 Voltage B-N Magnitude | H7 Voltage B-N Magnitude | 423300 | F32-4321 | R | 257287437
|  | Spectral Components | Voltage B-N Harmonics | H7 Voltage B-N Magnitude RMS | H7 Voltage B-N Magnitude RMS | 423302 | F32-4321 | R | 257287557
|  | Spectral Components | Voltage B-N Harmonics | H8 Voltage B-N Angle | H8 Voltage B-N Angle | 423310 | F32-4321 | R | 257287440
|  | Spectral Components | Voltage B-N Harmonics | H8 Voltage B-N Magnitude | H8 Voltage B-N Magnitude | 423306 | F32-4321 | R | 257287439
|  | Spectral Components | Voltage B-N Harmonics | H8 Voltage B-N Magnitude RMS | H8 Voltage B-N Magnitude RMS | 423308 | F32-4321 | R | 257287558
|  | Spectral Components | Voltage B-N Harmonics | H9 Voltage B-N Angle | H9 Voltage B-N Angle | 423316 | F32-4321 | R | 257287442
|  | Spectral Components | Voltage B-N Harmonics | H9 Voltage B-N Magnitude | H9 Voltage B-N Magnitude | 423312 | F32-4321 | R | 257287441
|  | Spectral Components | Voltage B-N Harmonics | H9 Voltage B-N Magnitude RMS | H9 Voltage B-N Magnitude RMS | 423314 | F32-4321 | R | 257287559
|  | Spectral Components | Voltage B-N Harmonics | H10 Voltage B-N Angle | H10 Voltage B-N Angle | 423322 | F32-4321 | R | 257287444
|  | Spectral Components | Voltage B-N Harmonics | H10 Voltage B-N Magnitude | H10 Voltage B-N Magnitude | 423318 | F32-4321 | R | 257287443
|  | Spectral Components | Voltage B-N Harmonics | H10 Voltage B-N Magnitude RMS | H10 Voltage B-N Magnitude RMS | 423320 | F32-4321 | R | 257287560
|  | Spectral Components | Voltage B-N Harmonics | H11 Voltage B-N Angle | H11 Voltage B-N Angle | 423328 | F32-4321 | R | 257287446
|  | Spectral Components | Voltage B-N Harmonics | H11 Voltage B-N Magnitude | H11 Voltage B-N Magnitude | 423324 | F32-4321 | R | 257287445
|  | Spectral Components | Voltage B-N Harmonics | H11 Voltage B-N Magnitude RMS | H11 Voltage B-N Magnitude RMS | 423326 | F32-4321 | R | 257287561
|  | Spectral Components | Voltage B-N Harmonics | H12 Voltage B-N Angle | H12 Voltage B-N Angle | 423334 | F32-4321 | R | 257287448
|  | Spectral Components | Voltage B-N Harmonics | H12 Voltage B-N Magnitude | H12 Voltage B-N Magnitude | 423330 | F32-4321 | R | 257287447
|  | Spectral Components | Voltage B-N Harmonics | H12 Voltage B-N Magnitude RMS | H12 Voltage B-N Magnitude RMS | 423332 | F32-4321 | R | 257287562
|  | Spectral Components | Voltage B-N Harmonics | H13 Voltage B-N Angle | H13 Voltage B-N Angle | 423340 | F32-4321 | R | 257287450
|  | Spectral Components | Voltage B-N Harmonics | H13 Voltage B-N Magnitude | H13 Voltage B-N Magnitude | 423336 | F32-4321 | R | 257287449
|  | Spectral Components | Voltage B-N Harmonics | H13 Voltage B-N Magnitude RMS | H13 Voltage B-N Magnitude RMS | 423338 | F32-4321 | R | 257287563
|  | Spectral Components | Voltage B-N Harmonics | H14 Voltage B-N Angle | H14 Voltage B-N Angle | 423346 | F32-4321 | R | 257287452
|  | Spectral Components | Voltage B-N Harmonics | H14 Voltage B-N Magnitude | H14 Voltage B-N Magnitude | 423342 | F32-4321 | R | 257287451
|  | Spectral Components | Voltage B-N Harmonics | H14 Voltage B-N Magnitude RMS | H14 Voltage B-N Magnitude RMS | 423344 | F32-4321 | R | 257287564
|  | Spectral Components | Voltage B-N Harmonics | H15 Voltage B-N Angle | H15 Voltage B-N Angle | 423352 | F32-4321 | R | 257287454
|  | Spectral Components | Voltage B-N Harmonics | H15 Voltage B-N Magnitude | H15 Voltage B-N Magnitude | 423348 | F32-4321 | R | 257287453
|  | Spectral Components | Voltage B-N Harmonics | H15 Voltage B-N Magnitude RMS | H15 Voltage B-N Magnitude RMS | 423350 | F32-4321 | R | 257287565
|  | Spectral Components | Voltage B-N Harmonics | H16 Voltage B-N Angle | H16 Voltage B-N Angle | 423358 | F32-4321 | R | 257287456
|  | Spectral Components | Voltage B-N Harmonics | H16 Voltage B-N Magnitude | H16 Voltage B-N Magnitude | 423354 | F32-4321 | R | 257287455
|  | Spectral Components | Voltage B-N Harmonics | H16 Voltage B-N Magnitude RMS | H16 Voltage B-N Magnitude RMS | 423356 | F32-4321 | R | 257287566
|  | Spectral Components | Voltage B-N Harmonics | H17 Voltage B-N Angle | H17 Voltage B-N Angle | 423364 | F32-4321 | R | 257287458
|  | Spectral Components | Voltage B-N Harmonics | H17 Voltage B-N Magnitude | H17 Voltage B-N Magnitude | 423360 | F32-4321 | R | 257287457
|  | Spectral Components | Voltage B-N Harmonics | H17 Voltage B-N Magnitude RMS | H17 Voltage B-N Magnitude RMS | 423362 | F32-4321 | R | 257287567
|  | Spectral Components | Voltage B-N Harmonics | H18 Voltage B-N Angle | H18 Voltage B-N Angle | 423370 | F32-4321 | R | 257287460
|  | Spectral Components | Voltage B-N Harmonics | H18 Voltage B-N Magnitude | H18 Voltage B-N Magnitude | 423366 | F32-4321 | R | 257287459
|  | Spectral Components | Voltage B-N Harmonics | H18 Voltage B-N Magnitude RMS | H18 Voltage B-N Magnitude RMS | 423368 | F32-4321 | R | 257287568
|  | Spectral Components | Voltage B-N Harmonics | H19 Voltage B-N Angle | H19 Voltage B-N Angle | 423376 | F32-4321 | R | 257287462
|  | Spectral Components | Voltage B-N Harmonics | H19 Voltage B-N Magnitude | H19 Voltage B-N Magnitude | 423372 | F32-4321 | R | 257287461
|  | Spectral Components | Voltage B-N Harmonics | H19 Voltage B-N Magnitude RMS | H19 Voltage B-N Magnitude RMS | 423374 | F32-4321 | R | 257287569
|  | Spectral Components | Voltage B-N Harmonics | H20 Voltage B-N Angle | H20 Voltage B-N Angle | 423382 | F32-4321 | R | 257287464
|  | Spectral Components | Voltage B-N Harmonics | H20 Voltage B-N Magnitude | H20 Voltage B-N Magnitude | 423378 | F32-4321 | R | 257287463
|  | Spectral Components | Voltage B-N Harmonics | H20 Voltage B-N Magnitude RMS | H20 Voltage B-N Magnitude RMS | 423380 | F32-4321 | R | 257287570
|  | Spectral Components | Voltage B-N Harmonics | H21 Voltage B-N Angle | H21 Voltage B-N Angle | 423388 | F32-4321 | R | 257287466
|  | Spectral Components | Voltage B-N Harmonics | H21 Voltage B-N Magnitude | H21 Voltage B-N Magnitude | 423384 | F32-4321 | R | 257287465
|  | Spectral Components | Voltage B-N Harmonics | H21 Voltage B-N Magnitude RMS | H21 Voltage B-N Magnitude RMS | 423386 | F32-4321 | R | 257287571
|  | Spectral Components | Voltage B-N Harmonics | H22 Voltage B-N Angle | H22 Voltage B-N Angle | 423394 | F32-4321 | R | 257287468
|  | Spectral Components | Voltage B-N Harmonics | H22 Voltage B-N Magnitude | H22 Voltage B-N Magnitude | 423390 | F32-4321 | R | 257287467
|  | Spectral Components | Voltage B-N Harmonics | H22 Voltage B-N Magnitude RMS | H22 Voltage B-N Magnitude RMS | 423392 | F32-4321 | R | 257287572
|  | Spectral Components | Voltage B-N Harmonics | H23 Voltage B-N Angle | H23 Voltage B-N Angle | 423400 | F32-4321 | R | 257287470
|  | Spectral Components | Voltage B-N Harmonics | H23 Voltage B-N Magnitude | H23 Voltage B-N Magnitude | 423396 | F32-4321 | R | 257287469
|  | Spectral Components | Voltage B-N Harmonics | H23 Voltage B-N Magnitude RMS | H23 Voltage B-N Magnitude RMS | 423398 | F32-4321 | R | 257287573
|  | Spectral Components | Voltage B-N Harmonics | H24 Voltage B-N Angle | H24 Voltage B-N Angle | 423406 | F32-4321 | R | 257287472
|  | Spectral Components | Voltage B-N Harmonics | H24 Voltage B-N Magnitude | H24 Voltage B-N Magnitude | 423402 | F32-4321 | R | 257287471
|  | Spectral Components | Voltage B-N Harmonics | H24 Voltage B-N Magnitude RMS | H24 Voltage B-N Magnitude RMS | 423404 | F32-4321 | R | 257287574
|  | Spectral Components | Voltage B-N Harmonics | H25 Voltage B-N Angle | H25 Voltage B-N Angle | 423412 | F32-4321 | R | 257287474
|  | Spectral Components | Voltage B-N Harmonics | H25 Voltage B-N Magnitude | H25 Voltage B-N Magnitude | 423408 | F32-4321 | R | 257287473
|  | Spectral Components | Voltage B-N Harmonics | H25 Voltage B-N Magnitude RMS | H25 Voltage B-N Magnitude RMS | 423410 | F32-4321 | R | 257287575
|  | Spectral Components | Voltage B-N Harmonics | H26 Voltage B-N Angle | H26 Voltage B-N Angle | 423418 | F32-4321 | R | 257287476
|  | Spectral Components | Voltage B-N Harmonics | H26 Voltage B-N Magnitude | H26 Voltage B-N Magnitude | 423414 | F32-4321 | R | 257287475
|  | Spectral Components | Voltage B-N Harmonics | H26 Voltage B-N Magnitude RMS | H26 Voltage B-N Magnitude RMS | 423416 | F32-4321 | R | 257287576
|  | Spectral Components | Voltage B-N Harmonics | H27 Voltage B-N Angle | H27 Voltage B-N Angle | 423424 | F32-4321 | R | 257287478
|  | Spectral Components | Voltage B-N Harmonics | H27 Voltage B-N Magnitude | H27 Voltage B-N Magnitude | 423420 | F32-4321 | R | 257287477
|  | Spectral Components | Voltage B-N Harmonics | H27 Voltage B-N Magnitude RMS | H27 Voltage B-N Magnitude RMS | 423422 | F32-4321 | R | 257287577
|  | Spectral Components | Voltage B-N Harmonics | H28 Voltage B-N Angle | H28 Voltage B-N Angle | 423430 | F32-4321 | R | 257287480
|  | Spectral Components | Voltage B-N Harmonics | H28 Voltage B-N Magnitude | H28 Voltage B-N Magnitude | 423426 | F32-4321 | R | 257287479
|  | Spectral Components | Voltage B-N Harmonics | H28 Voltage B-N Magnitude RMS | H28 Voltage B-N Magnitude RMS | 423428 | F32-4321 | R | 257287578
|  | Spectral Components | Voltage B-N Harmonics | H29 Voltage B-N Angle | H29 Voltage B-N Angle | 423436 | F32-4321 | R | 257287482
|  | Spectral Components | Voltage B-N Harmonics | H29 Voltage B-N Magnitude | H29 Voltage B-N Magnitude | 423432 | F32-4321 | R | 257287481
|  | Spectral Components | Voltage B-N Harmonics | H29 Voltage B-N Magnitude RMS | H29 Voltage B-N Magnitude RMS | 423434 | F32-4321 | R | 257287579
|  | Spectral Components | Voltage B-N Harmonics | H30 Voltage B-N Angle | H30 Voltage B-N Angle | 423442 | F32-4321 | R | 257287484
|  | Spectral Components | Voltage B-N Harmonics | H30 Voltage B-N Magnitude | H30 Voltage B-N Magnitude | 423438 | F32-4321 | R | 257287483
|  | Spectral Components | Voltage B-N Harmonics | H30 Voltage B-N Magnitude RMS | H30 Voltage B-N Magnitude RMS | 423440 | F32-4321 | R | 257287580
|  | Spectral Components | Voltage B-N Harmonics | H31 Voltage B-N Angle | H31 Voltage B-N Angle | 423448 | F32-4321 | R | 257287486
|  | Spectral Components | Voltage B-N Harmonics | H31 Voltage B-N Magnitude | H31 Voltage B-N Magnitude | 423444 | F32-4321 | R | 257287485
|  | Spectral Components | Voltage B-N Harmonics | H31 Voltage B-N Magnitude RMS | H31 Voltage B-N Magnitude RMS | 423446 | F32-4321 | R | 257287581
|  | Spectral Components | Voltage B-N Harmonics | H32 Voltage B-N Angle | H32 Voltage B-N Angle | 423454 | F32-4321 | R | 257287488
|  | Spectral Components | Voltage B-N Harmonics | H32 Voltage B-N Magnitude | H32 Voltage B-N Magnitude | 423450 | F32-4321 | R | 257287487
|  | Spectral Components | Voltage B-N Harmonics | H32 Voltage B-N Magnitude RMS | H32 Voltage B-N Magnitude RMS | 423452 | F32-4321 | R | 257287582
|  | Spectral Components | Voltage B-N Harmonics | H33 Voltage B-N Angle | H33 Voltage B-N Angle | 423460 | F32-4321 | R | 257287490
|  | Spectral Components | Voltage B-N Harmonics | H33 Voltage B-N Magnitude | H33 Voltage B-N Magnitude | 423456 | F32-4321 | R | 257287489
|  | Spectral Components | Voltage B-N Harmonics | H33 Voltage B-N Magnitude RMS | H33 Voltage B-N Magnitude RMS | 423458 | F32-4321 | R | 257287583
|  | Spectral Components | Voltage B-N Harmonics | H34 Voltage B-N Angle | H34 Voltage B-N Angle | 423466 | F32-4321 | R | 257287492
|  | Spectral Components | Voltage B-N Harmonics | H34 Voltage B-N Magnitude | H34 Voltage B-N Magnitude | 423462 | F32-4321 | R | 257287491
|  | Spectral Components | Voltage B-N Harmonics | H34 Voltage B-N Magnitude RMS | H34 Voltage B-N Magnitude RMS | 423464 | F32-4321 | R | 257287584
|  | Spectral Components | Voltage B-N Harmonics | H35 Voltage B-N Angle | H35 Voltage B-N Angle | 423472 | F32-4321 | R | 257287494
|  | Spectral Components | Voltage B-N Harmonics | H35 Voltage B-N Magnitude | H35 Voltage B-N Magnitude | 423468 | F32-4321 | R | 257287493
|  | Spectral Components | Voltage B-N Harmonics | H35 Voltage B-N Magnitude RMS | H35 Voltage B-N Magnitude RMS | 423470 | F32-4321 | R | 257287585
|  | Spectral Components | Voltage B-N Harmonics | H36 Voltage B-N Angle | H36 Voltage B-N Angle | 423478 | F32-4321 | R | 257287496
|  | Spectral Components | Voltage B-N Harmonics | H36 Voltage B-N Magnitude | H36 Voltage B-N Magnitude | 423474 | F32-4321 | R | 257287495
|  | Spectral Components | Voltage B-N Harmonics | H36 Voltage B-N Magnitude RMS | H36 Voltage B-N Magnitude RMS | 423476 | F32-4321 | R | 257287586
|  | Spectral Components | Voltage B-N Harmonics | H37 Voltage B-N Angle | H37 Voltage B-N Angle | 423484 | F32-4321 | R | 257287498
|  | Spectral Components | Voltage B-N Harmonics | H37 Voltage B-N Magnitude | H37 Voltage B-N Magnitude | 423480 | F32-4321 | R | 257287497
|  | Spectral Components | Voltage B-N Harmonics | H37 Voltage B-N Magnitude RMS | H37 Voltage B-N Magnitude RMS | 423482 | F32-4321 | R | 257287587
|  | Spectral Components | Voltage B-N Harmonics | H38 Voltage B-N Angle | H38 Voltage B-N Angle | 423490 | F32-4321 | R | 257287500
|  | Spectral Components | Voltage B-N Harmonics | H38 Voltage B-N Magnitude | H38 Voltage B-N Magnitude | 423486 | F32-4321 | R | 257287499
|  | Spectral Components | Voltage B-N Harmonics | H38 Voltage B-N Magnitude RMS | H38 Voltage B-N Magnitude RMS | 423488 | F32-4321 | R | 257287588
|  | Spectral Components | Voltage B-N Harmonics | H39 Voltage B-N Angle | H39 Voltage B-N Angle | 423496 | F32-4321 | R | 257287502
|  | Spectral Components | Voltage B-N Harmonics | H39 Voltage B-N Magnitude | H39 Voltage B-N Magnitude | 423492 | F32-4321 | R | 257287501
|  | Spectral Components | Voltage B-N Harmonics | H39 Voltage B-N Magnitude RMS | H39 Voltage B-N Magnitude RMS | 423494 | F32-4321 | R | 257287589
|  | Spectral Components | Voltage B-N Harmonics | H40 Voltage B-N Angle | H40 Voltage B-N Angle | 423502 | F32-4321 | R | 257287504
|  | Spectral Components | Voltage B-N Harmonics | H40 Voltage B-N Magnitude | H40 Voltage B-N Magnitude | 423498 | F32-4321 | R | 257287503
|  | Spectral Components | Voltage B-N Harmonics | H40 Voltage B-N Magnitude RMS | H40 Voltage B-N Magnitude RMS | 423500 | F32-4321 | R | 257287590
|  | Spectral Components | Voltage B-N Harmonics | H41 Voltage B-N Angle | H41 Voltage B-N Angle | 423508 | F32-4321 | R | 257287506
|  | Spectral Components | Voltage B-N Harmonics | H41 Voltage B-N Magnitude | H41 Voltage B-N Magnitude | 423504 | F32-4321 | R | 257287505
|  | Spectral Components | Voltage B-N Harmonics | H41 Voltage B-N Magnitude RMS | H41 Voltage B-N Magnitude RMS | 423506 | F32-4321 | R | 257287591
|  | Spectral Components | Voltage B-N Harmonics | H42 Voltage B-N Angle | H42 Voltage B-N Angle | 423514 | F32-4321 | R | 257287508
|  | Spectral Components | Voltage B-N Harmonics | H42 Voltage B-N Magnitude | H42 Voltage B-N Magnitude | 423510 | F32-4321 | R | 257287507
|  | Spectral Components | Voltage B-N Harmonics | H42 Voltage B-N Magnitude RMS | H42 Voltage B-N Magnitude RMS | 423512 | F32-4321 | R | 257287592
|  | Spectral Components | Voltage B-N Harmonics | H43 Voltage B-N Angle | H43 Voltage B-N Angle | 423520 | F32-4321 | R | 257287510
|  | Spectral Components | Voltage B-N Harmonics | H43 Voltage B-N Magnitude | H43 Voltage B-N Magnitude | 423516 | F32-4321 | R | 257287509
|  | Spectral Components | Voltage B-N Harmonics | H43 Voltage B-N Magnitude RMS | H43 Voltage B-N Magnitude RMS | 423518 | F32-4321 | R | 257287593
|  | Spectral Components | Voltage B-N Harmonics | H44 Voltage B-N Angle | H44 Voltage B-N Angle | 423526 | F32-4321 | R | 257287512
|  | Spectral Components | Voltage B-N Harmonics | H44 Voltage B-N Magnitude | H44 Voltage B-N Magnitude | 423522 | F32-4321 | R | 257287511
|  | Spectral Components | Voltage B-N Harmonics | H44 Voltage B-N Magnitude RMS | H44 Voltage B-N Magnitude RMS | 423524 | F32-4321 | R | 257287594
|  | Spectral Components | Voltage B-N Harmonics | H45 Voltage B-N Angle | H45 Voltage B-N Angle | 423532 | F32-4321 | R | 257287514
|  | Spectral Components | Voltage B-N Harmonics | H45 Voltage B-N Magnitude | H45 Voltage B-N Magnitude | 423528 | F32-4321 | R | 257287513
|  | Spectral Components | Voltage B-N Harmonics | H45 Voltage B-N Magnitude RMS | H45 Voltage B-N Magnitude RMS | 423530 | F32-4321 | R | 257287595
|  | Spectral Components | Voltage B-N Harmonics | H46 Voltage B-N Angle | H46 Voltage B-N Angle | 423538 | F32-4321 | R | 257287516
|  | Spectral Components | Voltage B-N Harmonics | H46 Voltage B-N Magnitude | H46 Voltage B-N Magnitude | 423534 | F32-4321 | R | 257287515
|  | Spectral Components | Voltage B-N Harmonics | H46 Voltage B-N Magnitude RMS | H46 Voltage B-N Magnitude RMS | 423536 | F32-4321 | R | 257287596
|  | Spectral Components | Voltage B-N Harmonics | H47 Voltage B-N Angle | H47 Voltage B-N Angle | 423544 | F32-4321 | R | 257287518
|  | Spectral Components | Voltage B-N Harmonics | H47 Voltage B-N Magnitude | H47 Voltage B-N Magnitude | 423540 | F32-4321 | R | 257287517
|  | Spectral Components | Voltage B-N Harmonics | H47 Voltage B-N Magnitude RMS | H47 Voltage B-N Magnitude RMS | 423542 | F32-4321 | R | 257287597
|  | Spectral Components | Voltage B-N Harmonics | H48 Voltage B-N Angle | H48 Voltage B-N Angle | 423550 | F32-4321 | R | 257287520
|  | Spectral Components | Voltage B-N Harmonics | H48 Voltage B-N Magnitude | H48 Voltage B-N Magnitude | 423546 | F32-4321 | R | 257287519
|  | Spectral Components | Voltage B-N Harmonics | H48 Voltage B-N Magnitude RMS | H48 Voltage B-N Magnitude RMS | 423548 | F32-4321 | R | 257287598
|  | Spectral Components | Voltage B-N Harmonics | H49 Voltage B-N Angle | H49 Voltage B-N Angle | 423556 | F32-4321 | R | 257287522
|  | Spectral Components | Voltage B-N Harmonics | H49 Voltage B-N Magnitude | H49 Voltage B-N Magnitude | 423552 | F32-4321 | R | 257287521
|  | Spectral Components | Voltage B-N Harmonics | H49 Voltage B-N Magnitude RMS | H49 Voltage B-N Magnitude RMS | 423554 | F32-4321 | R | 257287599
|  | Spectral Components | Voltage B-N Harmonics | H50 Voltage B-N Angle | H50 Voltage B-N Angle | 423562 | F32-4321 | R | 257287524
|  | Spectral Components | Voltage B-N Harmonics | H50 Voltage B-N Magnitude | H50 Voltage B-N Magnitude | 423558 | F32-4321 | R | 257287523
|  | Spectral Components | Voltage B-N Harmonics | H50 Voltage B-N Magnitude RMS | H50 Voltage B-N Magnitude RMS | 423560 | F32-4321 | R | 257287600
|  | Spectral Components | Voltage B-N Harmonics | H51 Voltage B-N Angle | H51 Voltage B-N Angle | 423568 | F32-4321 | R | 257287526
|  | Spectral Components | Voltage B-N Harmonics | H51 Voltage B-N Magnitude | H51 Voltage B-N Magnitude | 423564 | F32-4321 | R | 257287525
|  | Spectral Components | Voltage B-N Harmonics | H51 Voltage B-N Magnitude RMS | H51 Voltage B-N Magnitude RMS | 423566 | F32-4321 | R | 257287601
|  | Spectral Components | Voltage B-N Harmonics | H52 Voltage B-N Angle | H52 Voltage B-N Angle | 423574 | F32-4321 | R | 257287528
|  | Spectral Components | Voltage B-N Harmonics | H52 Voltage B-N Magnitude | H52 Voltage B-N Magnitude | 423570 | F32-4321 | R | 257287527
|  | Spectral Components | Voltage B-N Harmonics | H52 Voltage B-N Magnitude RMS | H52 Voltage B-N Magnitude RMS | 423572 | F32-4321 | R | 257287602
|  | Spectral Components | Voltage B-N Harmonics | H53 Voltage B-N Angle | H53 Voltage B-N Angle | 423580 | F32-4321 | R | 257287530
|  | Spectral Components | Voltage B-N Harmonics | H53 Voltage B-N Magnitude | H53 Voltage B-N Magnitude | 423576 | F32-4321 | R | 257287529
|  | Spectral Components | Voltage B-N Harmonics | H53 Voltage B-N Magnitude RMS | H53 Voltage B-N Magnitude RMS | 423578 | F32-4321 | R | 257287603
|  | Spectral Components | Voltage B-N Harmonics | H54 Voltage B-N Angle | H54 Voltage B-N Angle | 423586 | F32-4321 | R | 257287532
|  | Spectral Components | Voltage B-N Harmonics | H54 Voltage B-N Magnitude | H54 Voltage B-N Magnitude | 423582 | F32-4321 | R | 257287531
|  | Spectral Components | Voltage B-N Harmonics | H54 Voltage B-N Magnitude RMS | H54 Voltage B-N Magnitude RMS | 423584 | F32-4321 | R | 257287604
|  | Spectral Components | Voltage B-N Harmonics | H55 Voltage B-N Angle | H55 Voltage B-N Angle | 423592 | F32-4321 | R | 257287534
|  | Spectral Components | Voltage B-N Harmonics | H55 Voltage B-N Magnitude | H55 Voltage B-N Magnitude | 423588 | F32-4321 | R | 257287533
|  | Spectral Components | Voltage B-N Harmonics | H55 Voltage B-N Magnitude RMS | H55 Voltage B-N Magnitude RMS | 423590 | F32-4321 | R | 257287605
|  | Spectral Components | Voltage B-N Harmonics | H56 Voltage B-N Angle | H56 Voltage B-N Angle | 423598 | F32-4321 | R | 257287536
|  | Spectral Components | Voltage B-N Harmonics | H56 Voltage B-N Magnitude | H56 Voltage B-N Magnitude | 423594 | F32-4321 | R | 257287535
|  | Spectral Components | Voltage B-N Harmonics | H56 Voltage B-N Magnitude RMS | H56 Voltage B-N Magnitude RMS | 423596 | F32-4321 | R | 257287606
|  | Spectral Components | Voltage B-N Harmonics | H57 Voltage B-N Angle | H57 Voltage B-N Angle | 423604 | F32-4321 | R | 257287538
|  | Spectral Components | Voltage B-N Harmonics | H57 Voltage B-N Magnitude | H57 Voltage B-N Magnitude | 423600 | F32-4321 | R | 257287537
|  | Spectral Components | Voltage B-N Harmonics | H57 Voltage B-N Magnitude RMS | H57 Voltage B-N Magnitude RMS | 423602 | F32-4321 | R | 257287607
|  | Spectral Components | Voltage B-N Harmonics | H58 Voltage B-N Angle | H58 Voltage B-N Angle | 423610 | F32-4321 | R | 257287540
|  | Spectral Components | Voltage B-N Harmonics | H58 Voltage B-N Magnitude | H58 Voltage B-N Magnitude | 423606 | F32-4321 | R | 257287539
|  | Spectral Components | Voltage B-N Harmonics | H58 Voltage B-N Magnitude RMS | H58 Voltage B-N Magnitude RMS | 423608 | F32-4321 | R | 257287608
|  | Spectral Components | Voltage B-N Harmonics | H59 Voltage B-N Angle | H59 Voltage B-N Angle | 423616 | F32-4321 | R | 257287542
|  | Spectral Components | Voltage B-N Harmonics | H59 Voltage B-N Magnitude | H59 Voltage B-N Magnitude | 423612 | F32-4321 | R | 257287541
|  | Spectral Components | Voltage B-N Harmonics | H59 Voltage B-N Magnitude RMS | H59 Voltage B-N Magnitude RMS | 423614 | F32-4321 | R | 257287609
|  | Spectral Components | Voltage B-N Harmonics | H60 Voltage B-N Angle | H60 Voltage B-N Angle | 423622 | F32-4321 | R | 257287544
|  | Spectral Components | Voltage B-N Harmonics | H60 Voltage B-N Magnitude | H60 Voltage B-N Magnitude | 423618 | F32-4321 | R | 257287543
|  | Spectral Components | Voltage B-N Harmonics | H60 Voltage B-N Magnitude RMS | H60 Voltage B-N Magnitude RMS | 423620 | F32-4321 | R | 257287610
|  | Spectral Components | Voltage B-N Harmonics | H61 Voltage B-N Angle | H61 Voltage B-N Angle | 423628 | F32-4321 | R | 257287546
|  | Spectral Components | Voltage B-N Harmonics | H61 Voltage B-N Magnitude | H61 Voltage B-N Magnitude | 423624 | F32-4321 | R | 257287545
|  | Spectral Components | Voltage B-N Harmonics | H61 Voltage B-N Magnitude RMS | H61 Voltage B-N Magnitude RMS | 423626 | F32-4321 | R | 257287611
|  | Spectral Components | Voltage B-N Harmonics | H62 Voltage B-N Angle | H62 Voltage B-N Angle | 423634 | F32-4321 | R | 257287548
|  | Spectral Components | Voltage B-N Harmonics | H62 Voltage B-N Magnitude | H62 Voltage B-N Magnitude | 423630 | F32-4321 | R | 257287547
|  | Spectral Components | Voltage B-N Harmonics | H62 Voltage B-N Magnitude RMS | H62 Voltage B-N Magnitude RMS | 423632 | F32-4321 | R | 257287612
|  | Spectral Components | Voltage B-N Harmonics | H63 Voltage B-N Angle | H63 Voltage B-N Angle | 423640 | F32-4321 | R | 257287550
|  | Spectral Components | Voltage B-N Harmonics | H63 Voltage B-N Magnitude | H63 Voltage B-N Magnitude | 423636 | F32-4321 | R | 257287549
|  | Spectral Components | Voltage B-N Harmonics | H63 Voltage B-N Magnitude RMS | H63 Voltage B-N Magnitude RMS | 423638 | F32-4321 | R | 257287613
|  | Spectral Components | Voltage C-A Harmonics | H1 Voltage C-A Angle | H1 Voltage C-A Angle | 422492 | F32-4321 | R | 257286914
|  | Spectral Components | Voltage C-A Harmonics | H1 Voltage C-A Magnitude | H1 Voltage C-A Magnitude | 422488 | F32-4321 | R | 257286913
|  | Spectral Components | Voltage C-A Harmonics | H1 Voltage C-A Magnitude RMS | H1 Voltage C-A Magnitude RMS | 422490 | F32-4321 | R | 257287039
|  | Spectral Components | Voltage C-A Harmonics | H2 Voltage C-A Angle | H2 Voltage C-A Angle | 422498 | F32-4321 | R | 257286916
|  | Spectral Components | Voltage C-A Harmonics | H2 Voltage C-A Magnitude | H2 Voltage C-A Magnitude | 422494 | F32-4321 | R | 257286915
|  | Spectral Components | Voltage C-A Harmonics | H2 Voltage C-A Magnitude RMS | H2 Voltage C-A Magnitude RMS | 422496 | F32-4321 | R | 257287040
|  | Spectral Components | Voltage C-A Harmonics | H3 Voltage C-A Angle | H3 Voltage C-A Angle | 422504 | F32-4321 | R | 257286918
|  | Spectral Components | Voltage C-A Harmonics | H3 Voltage C-A Magnitude | H3 Voltage C-A Magnitude | 422500 | F32-4321 | R | 257286917
|  | Spectral Components | Voltage C-A Harmonics | H3 Voltage C-A Magnitude RMS | H3 Voltage C-A Magnitude RMS | 422502 | F32-4321 | R | 257287041
|  | Spectral Components | Voltage C-A Harmonics | H4 Voltage C-A Angle | H4 Voltage C-A Angle | 422510 | F32-4321 | R | 257286920
|  | Spectral Components | Voltage C-A Harmonics | H4 Voltage C-A Magnitude | H4 Voltage C-A Magnitude | 422506 | F32-4321 | R | 257286919
|  | Spectral Components | Voltage C-A Harmonics | H4 Voltage C-A Magnitude RMS | H4 Voltage C-A Magnitude RMS | 422508 | F32-4321 | R | 257287042
|  | Spectral Components | Voltage C-A Harmonics | H5 Voltage C-A Angle | H5 Voltage C-A Angle | 422516 | F32-4321 | R | 257286922
|  | Spectral Components | Voltage C-A Harmonics | H5 Voltage C-A Magnitude | H5 Voltage C-A Magnitude | 422512 | F32-4321 | R | 257286921
|  | Spectral Components | Voltage C-A Harmonics | H5 Voltage C-A Magnitude RMS | H5 Voltage C-A Magnitude RMS | 422514 | F32-4321 | R | 257287043
|  | Spectral Components | Voltage C-A Harmonics | H6 Voltage C-A Angle | H6 Voltage C-A Angle | 422522 | F32-4321 | R | 257286924
|  | Spectral Components | Voltage C-A Harmonics | H6 Voltage C-A Magnitude | H6 Voltage C-A Magnitude | 422518 | F32-4321 | R | 257286923
|  | Spectral Components | Voltage C-A Harmonics | H6 Voltage C-A Magnitude RMS | H6 Voltage C-A Magnitude RMS | 422520 | F32-4321 | R | 257287044
|  | Spectral Components | Voltage C-A Harmonics | H7 Voltage C-A Angle | H7 Voltage C-A Angle | 422528 | F32-4321 | R | 257286926
|  | Spectral Components | Voltage C-A Harmonics | H7 Voltage C-A Magnitude | H7 Voltage C-A Magnitude | 422524 | F32-4321 | R | 257286925
|  | Spectral Components | Voltage C-A Harmonics | H7 Voltage C-A Magnitude RMS | H7 Voltage C-A Magnitude RMS | 422526 | F32-4321 | R | 257287045
|  | Spectral Components | Voltage C-A Harmonics | H8 Voltage C-A Angle | H8 Voltage C-A Angle | 422534 | F32-4321 | R | 257286928
|  | Spectral Components | Voltage C-A Harmonics | H8 Voltage C-A Magnitude | H8 Voltage C-A Magnitude | 422530 | F32-4321 | R | 257286927
|  | Spectral Components | Voltage C-A Harmonics | H8 Voltage C-A Magnitude RMS | H8 Voltage C-A Magnitude RMS | 422532 | F32-4321 | R | 257287046
|  | Spectral Components | Voltage C-A Harmonics | H9 Voltage C-A Angle | H9 Voltage C-A Angle | 422540 | F32-4321 | R | 257286930
|  | Spectral Components | Voltage C-A Harmonics | H9 Voltage C-A Magnitude | H9 Voltage C-A Magnitude | 422536 | F32-4321 | R | 257286929
|  | Spectral Components | Voltage C-A Harmonics | H9 Voltage C-A Magnitude RMS | H9 Voltage C-A Magnitude RMS | 422538 | F32-4321 | R | 257287047
|  | Spectral Components | Voltage C-A Harmonics | H10 Voltage C-A Angle | H10 Voltage C-A Angle | 422546 | F32-4321 | R | 257286932
|  | Spectral Components | Voltage C-A Harmonics | H10 Voltage C-A Magnitude | H10 Voltage C-A Magnitude | 422542 | F32-4321 | R | 257286931
|  | Spectral Components | Voltage C-A Harmonics | H10 Voltage C-A Magnitude RMS | H10 Voltage C-A Magnitude RMS | 422544 | F32-4321 | R | 257287048
|  | Spectral Components | Voltage C-A Harmonics | H11 Voltage C-A Angle | H11 Voltage C-A Angle | 422552 | F32-4321 | R | 257286934
|  | Spectral Components | Voltage C-A Harmonics | H11 Voltage C-A Magnitude | H11 Voltage C-A Magnitude | 422548 | F32-4321 | R | 257286933
|  | Spectral Components | Voltage C-A Harmonics | H11 Voltage C-A Magnitude RMS | H11 Voltage C-A Magnitude RMS | 422550 | F32-4321 | R | 257287049
|  | Spectral Components | Voltage C-A Harmonics | H12 Voltage C-A Angle | H12 Voltage C-A Angle | 422558 | F32-4321 | R | 257286936
|  | Spectral Components | Voltage C-A Harmonics | H12 Voltage C-A Magnitude | H12 Voltage C-A Magnitude | 422554 | F32-4321 | R | 257286935
|  | Spectral Components | Voltage C-A Harmonics | H12 Voltage C-A Magnitude RMS | H12 Voltage C-A Magnitude RMS | 422556 | F32-4321 | R | 257287050
|  | Spectral Components | Voltage C-A Harmonics | H13 Voltage C-A Angle | H13 Voltage C-A Angle | 422564 | F32-4321 | R | 257286938
|  | Spectral Components | Voltage C-A Harmonics | H13 Voltage C-A Magnitude | H13 Voltage C-A Magnitude | 422560 | F32-4321 | R | 257286937
|  | Spectral Components | Voltage C-A Harmonics | H13 Voltage C-A Magnitude RMS | H13 Voltage C-A Magnitude RMS | 422562 | F32-4321 | R | 257287051
|  | Spectral Components | Voltage C-A Harmonics | H14 Voltage C-A Angle | H14 Voltage C-A Angle | 422570 | F32-4321 | R | 257286940
|  | Spectral Components | Voltage C-A Harmonics | H14 Voltage C-A Magnitude | H14 Voltage C-A Magnitude | 422566 | F32-4321 | R | 257286939
|  | Spectral Components | Voltage C-A Harmonics | H14 Voltage C-A Magnitude RMS | H14 Voltage C-A Magnitude RMS | 422568 | F32-4321 | R | 257287052
|  | Spectral Components | Voltage C-A Harmonics | H15 Voltage C-A Angle | H15 Voltage C-A Angle | 422576 | F32-4321 | R | 257286942
|  | Spectral Components | Voltage C-A Harmonics | H15 Voltage C-A Magnitude | H15 Voltage C-A Magnitude | 422572 | F32-4321 | R | 257286941
|  | Spectral Components | Voltage C-A Harmonics | H15 Voltage C-A Magnitude RMS | H15 Voltage C-A Magnitude RMS | 422574 | F32-4321 | R | 257287053
|  | Spectral Components | Voltage C-A Harmonics | H16 Voltage C-A Angle | H16 Voltage C-A Angle | 422582 | F32-4321 | R | 257286944
|  | Spectral Components | Voltage C-A Harmonics | H16 Voltage C-A Magnitude | H16 Voltage C-A Magnitude | 422578 | F32-4321 | R | 257286943
|  | Spectral Components | Voltage C-A Harmonics | H16 Voltage C-A Magnitude RMS | H16 Voltage C-A Magnitude RMS | 422580 | F32-4321 | R | 257287054
|  | Spectral Components | Voltage C-A Harmonics | H17 Voltage C-A Angle | H17 Voltage C-A Angle | 422588 | F32-4321 | R | 257286946
|  | Spectral Components | Voltage C-A Harmonics | H17 Voltage C-A Magnitude | H17 Voltage C-A Magnitude | 422584 | F32-4321 | R | 257286945
|  | Spectral Components | Voltage C-A Harmonics | H17 Voltage C-A Magnitude RMS | H17 Voltage C-A Magnitude RMS | 422586 | F32-4321 | R | 257287055
|  | Spectral Components | Voltage C-A Harmonics | H18 Voltage C-A Angle | H18 Voltage C-A Angle | 422594 | F32-4321 | R | 257286948
|  | Spectral Components | Voltage C-A Harmonics | H18 Voltage C-A Magnitude | H18 Voltage C-A Magnitude | 422590 | F32-4321 | R | 257286947
|  | Spectral Components | Voltage C-A Harmonics | H18 Voltage C-A Magnitude RMS | H18 Voltage C-A Magnitude RMS | 422592 | F32-4321 | R | 257287056
|  | Spectral Components | Voltage C-A Harmonics | H19 Voltage C-A Angle | H19 Voltage C-A Angle | 422600 | F32-4321 | R | 257286950
|  | Spectral Components | Voltage C-A Harmonics | H19 Voltage C-A Magnitude | H19 Voltage C-A Magnitude | 422596 | F32-4321 | R | 257286949
|  | Spectral Components | Voltage C-A Harmonics | H19 Voltage C-A Magnitude RMS | H19 Voltage C-A Magnitude RMS | 422598 | F32-4321 | R | 257287057
|  | Spectral Components | Voltage C-A Harmonics | H20 Voltage C-A Angle | H20 Voltage C-A Angle | 422606 | F32-4321 | R | 257286952
|  | Spectral Components | Voltage C-A Harmonics | H20 Voltage C-A Magnitude | H20 Voltage C-A Magnitude | 422602 | F32-4321 | R | 257286951
|  | Spectral Components | Voltage C-A Harmonics | H20 Voltage C-A Magnitude RMS | H20 Voltage C-A Magnitude RMS | 422604 | F32-4321 | R | 257287058
|  | Spectral Components | Voltage C-A Harmonics | H21 Voltage C-A Angle | H21 Voltage C-A Angle | 422612 | F32-4321 | R | 257286954
|  | Spectral Components | Voltage C-A Harmonics | H21 Voltage C-A Magnitude | H21 Voltage C-A Magnitude | 422608 | F32-4321 | R | 257286953
|  | Spectral Components | Voltage C-A Harmonics | H21 Voltage C-A Magnitude RMS | H21 Voltage C-A Magnitude RMS | 422610 | F32-4321 | R | 257287059
|  | Spectral Components | Voltage C-A Harmonics | H22 Voltage C-A Angle | H22 Voltage C-A Angle | 422618 | F32-4321 | R | 257286956
|  | Spectral Components | Voltage C-A Harmonics | H22 Voltage C-A Magnitude | H22 Voltage C-A Magnitude | 422614 | F32-4321 | R | 257286955
|  | Spectral Components | Voltage C-A Harmonics | H22 Voltage C-A Magnitude RMS | H22 Voltage C-A Magnitude RMS | 422616 | F32-4321 | R | 257287060
|  | Spectral Components | Voltage C-A Harmonics | H23 Voltage C-A Angle | H23 Voltage C-A Angle | 422624 | F32-4321 | R | 257286958
|  | Spectral Components | Voltage C-A Harmonics | H23 Voltage C-A Magnitude | H23 Voltage C-A Magnitude | 422620 | F32-4321 | R | 257286957
|  | Spectral Components | Voltage C-A Harmonics | H23 Voltage C-A Magnitude RMS | H23 Voltage C-A Magnitude RMS | 422622 | F32-4321 | R | 257287061
|  | Spectral Components | Voltage C-A Harmonics | H24 Voltage C-A Angle | H24 Voltage C-A Angle | 422630 | F32-4321 | R | 257286960
|  | Spectral Components | Voltage C-A Harmonics | H24 Voltage C-A Magnitude | H24 Voltage C-A Magnitude | 422626 | F32-4321 | R | 257286959
|  | Spectral Components | Voltage C-A Harmonics | H24 Voltage C-A Magnitude RMS | H24 Voltage C-A Magnitude RMS | 422628 | F32-4321 | R | 257287062
|  | Spectral Components | Voltage C-A Harmonics | H25 Voltage C-A Angle | H25 Voltage C-A Angle | 422636 | F32-4321 | R | 257286962
|  | Spectral Components | Voltage C-A Harmonics | H25 Voltage C-A Magnitude | H25 Voltage C-A Magnitude | 422632 | F32-4321 | R | 257286961
|  | Spectral Components | Voltage C-A Harmonics | H25 Voltage C-A Magnitude RMS | H25 Voltage C-A Magnitude RMS | 422634 | F32-4321 | R | 257287063
|  | Spectral Components | Voltage C-A Harmonics | H26 Voltage C-A Angle | H26 Voltage C-A Angle | 422642 | F32-4321 | R | 257286964
|  | Spectral Components | Voltage C-A Harmonics | H26 Voltage C-A Magnitude | H26 Voltage C-A Magnitude | 422638 | F32-4321 | R | 257286963
|  | Spectral Components | Voltage C-A Harmonics | H26 Voltage C-A Magnitude RMS | H26 Voltage C-A Magnitude RMS | 422640 | F32-4321 | R | 257287064
|  | Spectral Components | Voltage C-A Harmonics | H27 Voltage C-A Angle | H27 Voltage C-A Angle | 422648 | F32-4321 | R | 257286966
|  | Spectral Components | Voltage C-A Harmonics | H27 Voltage C-A Magnitude | H27 Voltage C-A Magnitude | 422644 | F32-4321 | R | 257286965
|  | Spectral Components | Voltage C-A Harmonics | H27 Voltage C-A Magnitude RMS | H27 Voltage C-A Magnitude RMS | 422646 | F32-4321 | R | 257287065
|  | Spectral Components | Voltage C-A Harmonics | H28 Voltage C-A Angle | H28 Voltage C-A Angle | 422654 | F32-4321 | R | 257286968
|  | Spectral Components | Voltage C-A Harmonics | H28 Voltage C-A Magnitude | H28 Voltage C-A Magnitude | 422650 | F32-4321 | R | 257286967
|  | Spectral Components | Voltage C-A Harmonics | H28 Voltage C-A Magnitude RMS | H28 Voltage C-A Magnitude RMS | 422652 | F32-4321 | R | 257287066
|  | Spectral Components | Voltage C-A Harmonics | H29 Voltage C-A Angle | H29 Voltage C-A Angle | 422660 | F32-4321 | R | 257286970
|  | Spectral Components | Voltage C-A Harmonics | H29 Voltage C-A Magnitude | H29 Voltage C-A Magnitude | 422656 | F32-4321 | R | 257286969
|  | Spectral Components | Voltage C-A Harmonics | H29 Voltage C-A Magnitude RMS | H29 Voltage C-A Magnitude RMS | 422658 | F32-4321 | R | 257287067
|  | Spectral Components | Voltage C-A Harmonics | H30 Voltage C-A Angle | H30 Voltage C-A Angle | 422666 | F32-4321 | R | 257286972
|  | Spectral Components | Voltage C-A Harmonics | H30 Voltage C-A Magnitude | H30 Voltage C-A Magnitude | 422662 | F32-4321 | R | 257286971
|  | Spectral Components | Voltage C-A Harmonics | H30 Voltage C-A Magnitude RMS | H30 Voltage C-A Magnitude RMS | 422664 | F32-4321 | R | 257287068
|  | Spectral Components | Voltage C-A Harmonics | H31 Voltage C-A Angle | H31 Voltage C-A Angle | 422672 | F32-4321 | R | 257286974
|  | Spectral Components | Voltage C-A Harmonics | H31 Voltage C-A Magnitude | H31 Voltage C-A Magnitude | 422668 | F32-4321 | R | 257286973
|  | Spectral Components | Voltage C-A Harmonics | H31 Voltage C-A Magnitude RMS | H31 Voltage C-A Magnitude RMS | 422670 | F32-4321 | R | 257287069
|  | Spectral Components | Voltage C-A Harmonics | H32 Voltage C-A Angle | H32 Voltage C-A Angle | 422678 | F32-4321 | R | 257286976
|  | Spectral Components | Voltage C-A Harmonics | H32 Voltage C-A Magnitude | H32 Voltage C-A Magnitude | 422674 | F32-4321 | R | 257286975
|  | Spectral Components | Voltage C-A Harmonics | H32 Voltage C-A Magnitude RMS | H32 Voltage C-A Magnitude RMS | 422676 | F32-4321 | R | 257287070
|  | Spectral Components | Voltage C-A Harmonics | H33 Voltage C-A Angle | H33 Voltage C-A Angle | 422684 | F32-4321 | R | 257286978
|  | Spectral Components | Voltage C-A Harmonics | H33 Voltage C-A Magnitude | H33 Voltage C-A Magnitude | 422680 | F32-4321 | R | 257286977
|  | Spectral Components | Voltage C-A Harmonics | H33 Voltage C-A Magnitude RMS | H33 Voltage C-A Magnitude RMS | 422682 | F32-4321 | R | 257287071
|  | Spectral Components | Voltage C-A Harmonics | H34 Voltage C-A Angle | H34 Voltage C-A Angle | 422690 | F32-4321 | R | 257286980
|  | Spectral Components | Voltage C-A Harmonics | H34 Voltage C-A Magnitude | H34 Voltage C-A Magnitude | 422686 | F32-4321 | R | 257286979
|  | Spectral Components | Voltage C-A Harmonics | H34 Voltage C-A Magnitude RMS | H34 Voltage C-A Magnitude RMS | 422688 | F32-4321 | R | 257287072
|  | Spectral Components | Voltage C-A Harmonics | H35 Voltage C-A Angle | H35 Voltage C-A Angle | 422696 | F32-4321 | R | 257286982
|  | Spectral Components | Voltage C-A Harmonics | H35 Voltage C-A Magnitude | H35 Voltage C-A Magnitude | 422692 | F32-4321 | R | 257286981
|  | Spectral Components | Voltage C-A Harmonics | H35 Voltage C-A Magnitude RMS | H35 Voltage C-A Magnitude RMS | 422694 | F32-4321 | R | 257287073
|  | Spectral Components | Voltage C-A Harmonics | H36 Voltage C-A Angle | H36 Voltage C-A Angle | 422702 | F32-4321 | R | 257286984
|  | Spectral Components | Voltage C-A Harmonics | H36 Voltage C-A Magnitude | H36 Voltage C-A Magnitude | 422698 | F32-4321 | R | 257286983
|  | Spectral Components | Voltage C-A Harmonics | H36 Voltage C-A Magnitude RMS | H36 Voltage C-A Magnitude RMS | 422700 | F32-4321 | R | 257287074
|  | Spectral Components | Voltage C-A Harmonics | H37 Voltage C-A Angle | H37 Voltage C-A Angle | 422708 | F32-4321 | R | 257286986
|  | Spectral Components | Voltage C-A Harmonics | H37 Voltage C-A Magnitude | H37 Voltage C-A Magnitude | 422704 | F32-4321 | R | 257286985
|  | Spectral Components | Voltage C-A Harmonics | H37 Voltage C-A Magnitude RMS | H37 Voltage C-A Magnitude RMS | 422706 | F32-4321 | R | 257287075
|  | Spectral Components | Voltage C-A Harmonics | H38 Voltage C-A Angle | H38 Voltage C-A Angle | 422714 | F32-4321 | R | 257286988
|  | Spectral Components | Voltage C-A Harmonics | H38 Voltage C-A Magnitude | H38 Voltage C-A Magnitude | 422710 | F32-4321 | R | 257286987
|  | Spectral Components | Voltage C-A Harmonics | H38 Voltage C-A Magnitude RMS | H38 Voltage C-A Magnitude RMS | 422712 | F32-4321 | R | 257287076
|  | Spectral Components | Voltage C-A Harmonics | H39 Voltage C-A Angle | H39 Voltage C-A Angle | 422720 | F32-4321 | R | 257286990
|  | Spectral Components | Voltage C-A Harmonics | H39 Voltage C-A Magnitude | H39 Voltage C-A Magnitude | 422716 | F32-4321 | R | 257286989
|  | Spectral Components | Voltage C-A Harmonics | H39 Voltage C-A Magnitude RMS | H39 Voltage C-A Magnitude RMS | 422718 | F32-4321 | R | 257287077
|  | Spectral Components | Voltage C-A Harmonics | H40 Voltage C-A Angle | H40 Voltage C-A Angle | 422726 | F32-4321 | R | 257286992
|  | Spectral Components | Voltage C-A Harmonics | H40 Voltage C-A Magnitude | H40 Voltage C-A Magnitude | 422722 | F32-4321 | R | 257286991
|  | Spectral Components | Voltage C-A Harmonics | H40 Voltage C-A Magnitude RMS | H40 Voltage C-A Magnitude RMS | 422724 | F32-4321 | R | 257287078
|  | Spectral Components | Voltage C-A Harmonics | H41 Voltage C-A Angle | H41 Voltage C-A Angle | 422732 | F32-4321 | R | 257286994
|  | Spectral Components | Voltage C-A Harmonics | H41 Voltage C-A Magnitude | H41 Voltage C-A Magnitude | 422728 | F32-4321 | R | 257286993
|  | Spectral Components | Voltage C-A Harmonics | H41 Voltage C-A Magnitude RMS | H41 Voltage C-A Magnitude RMS | 422730 | F32-4321 | R | 257287079
|  | Spectral Components | Voltage C-A Harmonics | H42 Voltage C-A Angle | H42 Voltage C-A Angle | 422738 | F32-4321 | R | 257286996
|  | Spectral Components | Voltage C-A Harmonics | H42 Voltage C-A Magnitude | H42 Voltage C-A Magnitude | 422734 | F32-4321 | R | 257286995
|  | Spectral Components | Voltage C-A Harmonics | H42 Voltage C-A Magnitude RMS | H42 Voltage C-A Magnitude RMS | 422736 | F32-4321 | R | 257287080
|  | Spectral Components | Voltage C-A Harmonics | H43 Voltage C-A Angle | H43 Voltage C-A Angle | 422744 | F32-4321 | R | 257286998
|  | Spectral Components | Voltage C-A Harmonics | H43 Voltage C-A Magnitude | H43 Voltage C-A Magnitude | 422740 | F32-4321 | R | 257286997
|  | Spectral Components | Voltage C-A Harmonics | H43 Voltage C-A Magnitude RMS | H43 Voltage C-A Magnitude RMS | 422742 | F32-4321 | R | 257287081
|  | Spectral Components | Voltage C-A Harmonics | H44 Voltage C-A Angle | H44 Voltage C-A Angle | 422750 | F32-4321 | R | 257287000
|  | Spectral Components | Voltage C-A Harmonics | H44 Voltage C-A Magnitude | H44 Voltage C-A Magnitude | 422746 | F32-4321 | R | 257286999
|  | Spectral Components | Voltage C-A Harmonics | H44 Voltage C-A Magnitude RMS | H44 Voltage C-A Magnitude RMS | 422748 | F32-4321 | R | 257287082
|  | Spectral Components | Voltage C-A Harmonics | H45 Voltage C-A Angle | H45 Voltage C-A Angle | 422756 | F32-4321 | R | 257287002
|  | Spectral Components | Voltage C-A Harmonics | H45 Voltage C-A Magnitude | H45 Voltage C-A Magnitude | 422752 | F32-4321 | R | 257287001
|  | Spectral Components | Voltage C-A Harmonics | H45 Voltage C-A Magnitude RMS | H45 Voltage C-A Magnitude RMS | 422754 | F32-4321 | R | 257287083
|  | Spectral Components | Voltage C-A Harmonics | H46 Voltage C-A Angle | H46 Voltage C-A Angle | 422762 | F32-4321 | R | 257287004
|  | Spectral Components | Voltage C-A Harmonics | H46 Voltage C-A Magnitude | H46 Voltage C-A Magnitude | 422758 | F32-4321 | R | 257287003
|  | Spectral Components | Voltage C-A Harmonics | H46 Voltage C-A Magnitude RMS | H46 Voltage C-A Magnitude RMS | 422760 | F32-4321 | R | 257287084
|  | Spectral Components | Voltage C-A Harmonics | H47 Voltage C-A Angle | H47 Voltage C-A Angle | 422768 | F32-4321 | R | 257287006
|  | Spectral Components | Voltage C-A Harmonics | H47 Voltage C-A Magnitude | H47 Voltage C-A Magnitude | 422764 | F32-4321 | R | 257287005
|  | Spectral Components | Voltage C-A Harmonics | H47 Voltage C-A Magnitude RMS | H47 Voltage C-A Magnitude RMS | 422766 | F32-4321 | R | 257287085
|  | Spectral Components | Voltage C-A Harmonics | H48 Voltage C-A Angle | H48 Voltage C-A Angle | 422774 | F32-4321 | R | 257287008
|  | Spectral Components | Voltage C-A Harmonics | H48 Voltage C-A Magnitude | H48 Voltage C-A Magnitude | 422770 | F32-4321 | R | 257287007
|  | Spectral Components | Voltage C-A Harmonics | H48 Voltage C-A Magnitude RMS | H48 Voltage C-A Magnitude RMS | 422772 | F32-4321 | R | 257287086
|  | Spectral Components | Voltage C-A Harmonics | H49 Voltage C-A Angle | H49 Voltage C-A Angle | 422780 | F32-4321 | R | 257287010
|  | Spectral Components | Voltage C-A Harmonics | H49 Voltage C-A Magnitude | H49 Voltage C-A Magnitude | 422776 | F32-4321 | R | 257287009
|  | Spectral Components | Voltage C-A Harmonics | H49 Voltage C-A Magnitude RMS | H49 Voltage C-A Magnitude RMS | 422778 | F32-4321 | R | 257287087
|  | Spectral Components | Voltage C-A Harmonics | H50 Voltage C-A Angle | H50 Voltage C-A Angle | 422786 | F32-4321 | R | 257287012
|  | Spectral Components | Voltage C-A Harmonics | H50 Voltage C-A Magnitude | H50 Voltage C-A Magnitude | 422782 | F32-4321 | R | 257287011
|  | Spectral Components | Voltage C-A Harmonics | H50 Voltage C-A Magnitude RMS | H50 Voltage C-A Magnitude RMS | 422784 | F32-4321 | R | 257287088
|  | Spectral Components | Voltage C-A Harmonics | H51 Voltage C-A Angle | H51 Voltage C-A Angle | 422792 | F32-4321 | R | 257287014
|  | Spectral Components | Voltage C-A Harmonics | H51 Voltage C-A Magnitude | H51 Voltage C-A Magnitude | 422788 | F32-4321 | R | 257287013
|  | Spectral Components | Voltage C-A Harmonics | H51 Voltage C-A Magnitude RMS | H51 Voltage C-A Magnitude RMS | 422790 | F32-4321 | R | 257287089
|  | Spectral Components | Voltage C-A Harmonics | H52 Voltage C-A Angle | H52 Voltage C-A Angle | 422798 | F32-4321 | R | 257287016
|  | Spectral Components | Voltage C-A Harmonics | H52 Voltage C-A Magnitude | H52 Voltage C-A Magnitude | 422794 | F32-4321 | R | 257287015
|  | Spectral Components | Voltage C-A Harmonics | H52 Voltage C-A Magnitude RMS | H52 Voltage C-A Magnitude RMS | 422796 | F32-4321 | R | 257287090
|  | Spectral Components | Voltage C-A Harmonics | H53 Voltage C-A Angle | H53 Voltage C-A Angle | 422804 | F32-4321 | R | 257287018
|  | Spectral Components | Voltage C-A Harmonics | H53 Voltage C-A Magnitude | H53 Voltage C-A Magnitude | 422800 | F32-4321 | R | 257287017
|  | Spectral Components | Voltage C-A Harmonics | H53 Voltage C-A Magnitude RMS | H53 Voltage C-A Magnitude RMS | 422802 | F32-4321 | R | 257287091
|  | Spectral Components | Voltage C-A Harmonics | H54 Voltage C-A Angle | H54 Voltage C-A Angle | 422810 | F32-4321 | R | 257287020
|  | Spectral Components | Voltage C-A Harmonics | H54 Voltage C-A Magnitude | H54 Voltage C-A Magnitude | 422806 | F32-4321 | R | 257287019
|  | Spectral Components | Voltage C-A Harmonics | H54 Voltage C-A Magnitude RMS | H54 Voltage C-A Magnitude RMS | 422808 | F32-4321 | R | 257287092
|  | Spectral Components | Voltage C-A Harmonics | H55 Voltage C-A Angle | H55 Voltage C-A Angle | 422816 | F32-4321 | R | 257287022
|  | Spectral Components | Voltage C-A Harmonics | H55 Voltage C-A Magnitude | H55 Voltage C-A Magnitude | 422812 | F32-4321 | R | 257287021
|  | Spectral Components | Voltage C-A Harmonics | H55 Voltage C-A Magnitude RMS | H55 Voltage C-A Magnitude RMS | 422814 | F32-4321 | R | 257287093
|  | Spectral Components | Voltage C-A Harmonics | H56 Voltage C-A Angle | H56 Voltage C-A Angle | 422822 | F32-4321 | R | 257287024
|  | Spectral Components | Voltage C-A Harmonics | H56 Voltage C-A Magnitude | H56 Voltage C-A Magnitude | 422818 | F32-4321 | R | 257287023
|  | Spectral Components | Voltage C-A Harmonics | H56 Voltage C-A Magnitude RMS | H56 Voltage C-A Magnitude RMS | 422820 | F32-4321 | R | 257287094
|  | Spectral Components | Voltage C-A Harmonics | H57 Voltage C-A Angle | H57 Voltage C-A Angle | 422828 | F32-4321 | R | 257287026
|  | Spectral Components | Voltage C-A Harmonics | H57 Voltage C-A Magnitude | H57 Voltage C-A Magnitude | 422824 | F32-4321 | R | 257287025
|  | Spectral Components | Voltage C-A Harmonics | H57 Voltage C-A Magnitude RMS | H57 Voltage C-A Magnitude RMS | 422826 | F32-4321 | R | 257287095
|  | Spectral Components | Voltage C-A Harmonics | H58 Voltage C-A Angle | H58 Voltage C-A Angle | 422834 | F32-4321 | R | 257287028
|  | Spectral Components | Voltage C-A Harmonics | H58 Voltage C-A Magnitude | H58 Voltage C-A Magnitude | 422830 | F32-4321 | R | 257287027
|  | Spectral Components | Voltage C-A Harmonics | H58 Voltage C-A Magnitude RMS | H58 Voltage C-A Magnitude RMS | 422832 | F32-4321 | R | 257287096
|  | Spectral Components | Voltage C-A Harmonics | H59 Voltage C-A Angle | H59 Voltage C-A Angle | 422840 | F32-4321 | R | 257287030
|  | Spectral Components | Voltage C-A Harmonics | H59 Voltage C-A Magnitude | H59 Voltage C-A Magnitude | 422836 | F32-4321 | R | 257287029
|  | Spectral Components | Voltage C-A Harmonics | H59 Voltage C-A Magnitude RMS | H59 Voltage C-A Magnitude RMS | 422838 | F32-4321 | R | 257287097
|  | Spectral Components | Voltage C-A Harmonics | H60 Voltage C-A Angle | H60 Voltage C-A Angle | 422846 | F32-4321 | R | 257287032
|  | Spectral Components | Voltage C-A Harmonics | H60 Voltage C-A Magnitude | H60 Voltage C-A Magnitude | 422842 | F32-4321 | R | 257287031
|  | Spectral Components | Voltage C-A Harmonics | H60 Voltage C-A Magnitude RMS | H60 Voltage C-A Magnitude RMS | 422844 | F32-4321 | R | 257287098
|  | Spectral Components | Voltage C-A Harmonics | H61 Voltage C-A Angle | H61 Voltage C-A Angle | 422852 | F32-4321 | R | 257287034
|  | Spectral Components | Voltage C-A Harmonics | H61 Voltage C-A Magnitude | H61 Voltage C-A Magnitude | 422848 | F32-4321 | R | 257287033
|  | Spectral Components | Voltage C-A Harmonics | H61 Voltage C-A Magnitude RMS | H61 Voltage C-A Magnitude RMS | 422850 | F32-4321 | R | 257287099
|  | Spectral Components | Voltage C-A Harmonics | H62 Voltage C-A Angle | H62 Voltage C-A Angle | 422858 | F32-4321 | R | 257287036
|  | Spectral Components | Voltage C-A Harmonics | H62 Voltage C-A Magnitude | H62 Voltage C-A Magnitude | 422854 | F32-4321 | R | 257287035
|  | Spectral Components | Voltage C-A Harmonics | H62 Voltage C-A Magnitude RMS | H62 Voltage C-A Magnitude RMS | 422856 | F32-4321 | R | 257287100
|  | Spectral Components | Voltage C-A Harmonics | H63 Voltage C-A Angle | H63 Voltage C-A Angle | 422864 | F32-4321 | R | 257287038
|  | Spectral Components | Voltage C-A Harmonics | H63 Voltage C-A Magnitude | H63 Voltage C-A Magnitude | 422860 | F32-4321 | R | 257287037
|  | Spectral Components | Voltage C-A Harmonics | H63 Voltage C-A Magnitude RMS | H63 Voltage C-A Magnitude RMS | 422862 | F32-4321 | R | 257287101
|  | Spectral Components | Voltage C-N Harmonics | H1 Voltage C-N Angle | H1 Voltage C-N Angle | 423656 | F32-4321 | R | 257287682
|  | Spectral Components | Voltage C-N Harmonics | H1 Voltage C-N Magnitude | H1 Voltage C-N Magnitude | 423652 | F32-4321 | R | 257287681
|  | Spectral Components | Voltage C-N Harmonics | H1 Voltage C-N Magnitude RMS | H1 Voltage C-N Magnitude RMS | 423654 | F32-4321 | R | 257287807
|  | Spectral Components | Voltage C-N Harmonics | H2 Voltage C-N Angle | H2 Voltage C-N Angle | 423662 | F32-4321 | R | 257287684
|  | Spectral Components | Voltage C-N Harmonics | H2 Voltage C-N Magnitude | H2 Voltage C-N Magnitude | 423658 | F32-4321 | R | 257287683
|  | Spectral Components | Voltage C-N Harmonics | H2 Voltage C-N Magnitude RMS | H2 Voltage C-N Magnitude RMS | 423660 | F32-4321 | R | 257287808
|  | Spectral Components | Voltage C-N Harmonics | H3 Voltage C-N Angle | H3 Voltage C-N Angle | 423668 | F32-4321 | R | 257287686
|  | Spectral Components | Voltage C-N Harmonics | H3 Voltage C-N Magnitude | H3 Voltage C-N Magnitude | 423664 | F32-4321 | R | 257287685
|  | Spectral Components | Voltage C-N Harmonics | H3 Voltage C-N Magnitude RMS | H3 Voltage C-N Magnitude RMS | 423666 | F32-4321 | R | 257287809
|  | Spectral Components | Voltage C-N Harmonics | H4 Voltage C-N Angle | H4 Voltage C-N Angle | 423674 | F32-4321 | R | 257287688
|  | Spectral Components | Voltage C-N Harmonics | H4 Voltage C-N Magnitude | H4 Voltage C-N Magnitude | 423670 | F32-4321 | R | 257287687
|  | Spectral Components | Voltage C-N Harmonics | H4 Voltage C-N Magnitude RMS | H4 Voltage C-N Magnitude RMS | 423672 | F32-4321 | R | 257287810
|  | Spectral Components | Voltage C-N Harmonics | H5 Voltage C-N Angle | H5 Voltage C-N Angle | 423680 | F32-4321 | R | 257287690
|  | Spectral Components | Voltage C-N Harmonics | H5 Voltage C-N Magnitude | H5 Voltage C-N Magnitude | 423676 | F32-4321 | R | 257287689
|  | Spectral Components | Voltage C-N Harmonics | H5 Voltage C-N Magnitude RMS | H5 Voltage C-N Magnitude RMS | 423678 | F32-4321 | R | 257287811
|  | Spectral Components | Voltage C-N Harmonics | H6 Voltage C-N Angle | H6 Voltage C-N Angle | 423686 | F32-4321 | R | 257287692
|  | Spectral Components | Voltage C-N Harmonics | H6 Voltage C-N Magnitude | H6 Voltage C-N Magnitude | 423682 | F32-4321 | R | 257287691
|  | Spectral Components | Voltage C-N Harmonics | H6 Voltage C-N Magnitude RMS | H6 Voltage C-N Magnitude RMS | 423684 | F32-4321 | R | 257287812
|  | Spectral Components | Voltage C-N Harmonics | H7 Voltage C-N Angle | H7 Voltage C-N Angle | 423692 | F32-4321 | R | 257287694
|  | Spectral Components | Voltage C-N Harmonics | H7 Voltage C-N Magnitude | H7 Voltage C-N Magnitude | 423688 | F32-4321 | R | 257287693
|  | Spectral Components | Voltage C-N Harmonics | H7 Voltage C-N Magnitude RMS | H7 Voltage C-N Magnitude RMS | 423690 | F32-4321 | R | 257287813
|  | Spectral Components | Voltage C-N Harmonics | H8 Voltage C-N Angle | H8 Voltage C-N Angle | 423698 | F32-4321 | R | 257287696
|  | Spectral Components | Voltage C-N Harmonics | H8 Voltage C-N Magnitude | H8 Voltage C-N Magnitude | 423694 | F32-4321 | R | 257287695
|  | Spectral Components | Voltage C-N Harmonics | H8 Voltage C-N Magnitude RMS | H8 Voltage C-N Magnitude RMS | 423696 | F32-4321 | R | 257287814
|  | Spectral Components | Voltage C-N Harmonics | H9 Voltage C-N Angle | H9 Voltage C-N Angle | 423704 | F32-4321 | R | 257287698
|  | Spectral Components | Voltage C-N Harmonics | H9 Voltage C-N Magnitude | H9 Voltage C-N Magnitude | 423700 | F32-4321 | R | 257287697
|  | Spectral Components | Voltage C-N Harmonics | H9 Voltage C-N Magnitude RMS | H9 Voltage C-N Magnitude RMS | 423702 | F32-4321 | R | 257287815
|  | Spectral Components | Voltage C-N Harmonics | H10 Voltage C-N Angle | H10 Voltage C-N Angle | 423710 | F32-4321 | R | 257287700
|  | Spectral Components | Voltage C-N Harmonics | H10 Voltage C-N Magnitude | H10 Voltage C-N Magnitude | 423706 | F32-4321 | R | 257287699
|  | Spectral Components | Voltage C-N Harmonics | H10 Voltage C-N Magnitude RMS | H10 Voltage C-N Magnitude RMS | 423708 | F32-4321 | R | 257287816
|  | Spectral Components | Voltage C-N Harmonics | H11 Voltage C-N Angle | H11 Voltage C-N Angle | 423716 | F32-4321 | R | 257287702
|  | Spectral Components | Voltage C-N Harmonics | H11 Voltage C-N Magnitude | H11 Voltage C-N Magnitude | 423712 | F32-4321 | R | 257287701
|  | Spectral Components | Voltage C-N Harmonics | H11 Voltage C-N Magnitude RMS | H11 Voltage C-N Magnitude RMS | 423714 | F32-4321 | R | 257287817
|  | Spectral Components | Voltage C-N Harmonics | H12 Voltage C-N Angle | H12 Voltage C-N Angle | 423722 | F32-4321 | R | 257287704
|  | Spectral Components | Voltage C-N Harmonics | H12 Voltage C-N Magnitude | H12 Voltage C-N Magnitude | 423718 | F32-4321 | R | 257287703
|  | Spectral Components | Voltage C-N Harmonics | H12 Voltage C-N Magnitude RMS | H12 Voltage C-N Magnitude RMS | 423720 | F32-4321 | R | 257287818
|  | Spectral Components | Voltage C-N Harmonics | H13 Voltage C-N Angle | H13 Voltage C-N Angle | 423728 | F32-4321 | R | 257287706
|  | Spectral Components | Voltage C-N Harmonics | H13 Voltage C-N Magnitude | H13 Voltage C-N Magnitude | 423724 | F32-4321 | R | 257287705
|  | Spectral Components | Voltage C-N Harmonics | H13 Voltage C-N Magnitude RMS | H13 Voltage C-N Magnitude RMS | 423726 | F32-4321 | R | 257287819
|  | Spectral Components | Voltage C-N Harmonics | H14 Voltage C-N Angle | H14 Voltage C-N Angle | 423734 | F32-4321 | R | 257287708
|  | Spectral Components | Voltage C-N Harmonics | H14 Voltage C-N Magnitude | H14 Voltage C-N Magnitude | 423730 | F32-4321 | R | 257287707
|  | Spectral Components | Voltage C-N Harmonics | H14 Voltage C-N Magnitude RMS | H14 Voltage C-N Magnitude RMS | 423732 | F32-4321 | R | 257287820
|  | Spectral Components | Voltage C-N Harmonics | H15 Voltage C-N Angle | H15 Voltage C-N Angle | 423740 | F32-4321 | R | 257287710
|  | Spectral Components | Voltage C-N Harmonics | H15 Voltage C-N Magnitude | H15 Voltage C-N Magnitude | 423736 | F32-4321 | R | 257287709
|  | Spectral Components | Voltage C-N Harmonics | H15 Voltage C-N Magnitude RMS | H15 Voltage C-N Magnitude RMS | 423738 | F32-4321 | R | 257287821
|  | Spectral Components | Voltage C-N Harmonics | H16 Voltage C-N Angle | H16 Voltage C-N Angle | 423746 | F32-4321 | R | 257287712
|  | Spectral Components | Voltage C-N Harmonics | H16 Voltage C-N Magnitude | H16 Voltage C-N Magnitude | 423742 | F32-4321 | R | 257287711
|  | Spectral Components | Voltage C-N Harmonics | H16 Voltage C-N Magnitude RMS | H16 Voltage C-N Magnitude RMS | 423744 | F32-4321 | R | 257287822
|  | Spectral Components | Voltage C-N Harmonics | H17 Voltage C-N Angle | H17 Voltage C-N Angle | 423752 | F32-4321 | R | 257287714
|  | Spectral Components | Voltage C-N Harmonics | H17 Voltage C-N Magnitude | H17 Voltage C-N Magnitude | 423748 | F32-4321 | R | 257287713
|  | Spectral Components | Voltage C-N Harmonics | H17 Voltage C-N Magnitude RMS | H17 Voltage C-N Magnitude RMS | 423750 | F32-4321 | R | 257287823
|  | Spectral Components | Voltage C-N Harmonics | H18 Voltage C-N Angle | H18 Voltage C-N Angle | 423758 | F32-4321 | R | 257287716
|  | Spectral Components | Voltage C-N Harmonics | H18 Voltage C-N Magnitude | H18 Voltage C-N Magnitude | 423754 | F32-4321 | R | 257287715
|  | Spectral Components | Voltage C-N Harmonics | H18 Voltage C-N Magnitude RMS | H18 Voltage C-N Magnitude RMS | 423756 | F32-4321 | R | 257287824
|  | Spectral Components | Voltage C-N Harmonics | H19 Voltage C-N Angle | H19 Voltage C-N Angle | 423764 | F32-4321 | R | 257287718
|  | Spectral Components | Voltage C-N Harmonics | H19 Voltage C-N Magnitude | H19 Voltage C-N Magnitude | 423760 | F32-4321 | R | 257287717
|  | Spectral Components | Voltage C-N Harmonics | H19 Voltage C-N Magnitude RMS | H19 Voltage C-N Magnitude RMS | 423762 | F32-4321 | R | 257287825
|  | Spectral Components | Voltage C-N Harmonics | H20 Voltage C-N Angle | H20 Voltage C-N Angle | 423770 | F32-4321 | R | 257287720
|  | Spectral Components | Voltage C-N Harmonics | H20 Voltage C-N Magnitude | H20 Voltage C-N Magnitude | 423766 | F32-4321 | R | 257287719
|  | Spectral Components | Voltage C-N Harmonics | H20 Voltage C-N Magnitude RMS | H20 Voltage C-N Magnitude RMS | 423768 | F32-4321 | R | 257287826
|  | Spectral Components | Voltage C-N Harmonics | H21 Voltage C-N Angle | H21 Voltage C-N Angle | 423776 | F32-4321 | R | 257287722
|  | Spectral Components | Voltage C-N Harmonics | H21 Voltage C-N Magnitude | H21 Voltage C-N Magnitude | 423772 | F32-4321 | R | 257287721
|  | Spectral Components | Voltage C-N Harmonics | H21 Voltage C-N Magnitude RMS | H21 Voltage C-N Magnitude RMS | 423774 | F32-4321 | R | 257287827
|  | Spectral Components | Voltage C-N Harmonics | H22 Voltage C-N Angle | H22 Voltage C-N Angle | 423782 | F32-4321 | R | 257287724
|  | Spectral Components | Voltage C-N Harmonics | H22 Voltage C-N Magnitude | H22 Voltage C-N Magnitude | 423778 | F32-4321 | R | 257287723
|  | Spectral Components | Voltage C-N Harmonics | H22 Voltage C-N Magnitude RMS | H22 Voltage C-N Magnitude RMS | 423780 | F32-4321 | R | 257287828
|  | Spectral Components | Voltage C-N Harmonics | H23 Voltage C-N Angle | H23 Voltage C-N Angle | 423788 | F32-4321 | R | 257287726
|  | Spectral Components | Voltage C-N Harmonics | H23 Voltage C-N Magnitude | H23 Voltage C-N Magnitude | 423784 | F32-4321 | R | 257287725
|  | Spectral Components | Voltage C-N Harmonics | H23 Voltage C-N Magnitude RMS | H23 Voltage C-N Magnitude RMS | 423786 | F32-4321 | R | 257287829
|  | Spectral Components | Voltage C-N Harmonics | H24 Voltage C-N Angle | H24 Voltage C-N Angle | 423794 | F32-4321 | R | 257287728
|  | Spectral Components | Voltage C-N Harmonics | H24 Voltage C-N Magnitude | H24 Voltage C-N Magnitude | 423790 | F32-4321 | R | 257287727
|  | Spectral Components | Voltage C-N Harmonics | H24 Voltage C-N Magnitude RMS | H24 Voltage C-N Magnitude RMS | 423792 | F32-4321 | R | 257287830
|  | Spectral Components | Voltage C-N Harmonics | H25 Voltage C-N Angle | H25 Voltage C-N Angle | 423800 | F32-4321 | R | 257287730
|  | Spectral Components | Voltage C-N Harmonics | H25 Voltage C-N Magnitude | H25 Voltage C-N Magnitude | 423796 | F32-4321 | R | 257287729
|  | Spectral Components | Voltage C-N Harmonics | H25 Voltage C-N Magnitude RMS | H25 Voltage C-N Magnitude RMS | 423798 | F32-4321 | R | 257287831
|  | Spectral Components | Voltage C-N Harmonics | H26 Voltage C-N Angle | H26 Voltage C-N Angle | 423806 | F32-4321 | R | 257287732
|  | Spectral Components | Voltage C-N Harmonics | H26 Voltage C-N Magnitude | H26 Voltage C-N Magnitude | 423802 | F32-4321 | R | 257287731
|  | Spectral Components | Voltage C-N Harmonics | H26 Voltage C-N Magnitude RMS | H26 Voltage C-N Magnitude RMS | 423804 | F32-4321 | R | 257287832
|  | Spectral Components | Voltage C-N Harmonics | H27 Voltage C-N Angle | H27 Voltage C-N Angle | 423812 | F32-4321 | R | 257287734
|  | Spectral Components | Voltage C-N Harmonics | H27 Voltage C-N Magnitude | H27 Voltage C-N Magnitude | 423808 | F32-4321 | R | 257287733
|  | Spectral Components | Voltage C-N Harmonics | H27 Voltage C-N Magnitude RMS | H27 Voltage C-N Magnitude RMS | 423810 | F32-4321 | R | 257287833
|  | Spectral Components | Voltage C-N Harmonics | H28 Voltage C-N Angle | H28 Voltage C-N Angle | 423818 | F32-4321 | R | 257287736
|  | Spectral Components | Voltage C-N Harmonics | H28 Voltage C-N Magnitude | H28 Voltage C-N Magnitude | 423814 | F32-4321 | R | 257287735
|  | Spectral Components | Voltage C-N Harmonics | H28 Voltage C-N Magnitude RMS | H28 Voltage C-N Magnitude RMS | 423816 | F32-4321 | R | 257287834
|  | Spectral Components | Voltage C-N Harmonics | H29 Voltage C-N Angle | H29 Voltage C-N Angle | 423824 | F32-4321 | R | 257287738
|  | Spectral Components | Voltage C-N Harmonics | H29 Voltage C-N Magnitude | H29 Voltage C-N Magnitude | 423820 | F32-4321 | R | 257287737
|  | Spectral Components | Voltage C-N Harmonics | H29 Voltage C-N Magnitude RMS | H29 Voltage C-N Magnitude RMS | 423822 | F32-4321 | R | 257287835
|  | Spectral Components | Voltage C-N Harmonics | H30 Voltage C-N Angle | H30 Voltage C-N Angle | 423830 | F32-4321 | R | 257287740
|  | Spectral Components | Voltage C-N Harmonics | H30 Voltage C-N Magnitude | H30 Voltage C-N Magnitude | 423826 | F32-4321 | R | 257287739
|  | Spectral Components | Voltage C-N Harmonics | H30 Voltage C-N Magnitude RMS | H30 Voltage C-N Magnitude RMS | 423828 | F32-4321 | R | 257287836
|  | Spectral Components | Voltage C-N Harmonics | H31 Voltage C-N Angle | H31 Voltage C-N Angle | 423836 | F32-4321 | R | 257287742
|  | Spectral Components | Voltage C-N Harmonics | H31 Voltage C-N Magnitude | H31 Voltage C-N Magnitude | 423832 | F32-4321 | R | 257287741
|  | Spectral Components | Voltage C-N Harmonics | H31 Voltage C-N Magnitude RMS | H31 Voltage C-N Magnitude RMS | 423834 | F32-4321 | R | 257287837
|  | Spectral Components | Voltage C-N Harmonics | H32 Voltage C-N Angle | H32 Voltage C-N Angle | 423842 | F32-4321 | R | 257287744
|  | Spectral Components | Voltage C-N Harmonics | H32 Voltage C-N Magnitude | H32 Voltage C-N Magnitude | 423838 | F32-4321 | R | 257287743
|  | Spectral Components | Voltage C-N Harmonics | H32 Voltage C-N Magnitude RMS | H32 Voltage C-N Magnitude RMS | 423840 | F32-4321 | R | 257287838
|  | Spectral Components | Voltage C-N Harmonics | H33 Voltage C-N Angle | H33 Voltage C-N Angle | 423848 | F32-4321 | R | 257287746
|  | Spectral Components | Voltage C-N Harmonics | H33 Voltage C-N Magnitude | H33 Voltage C-N Magnitude | 423844 | F32-4321 | R | 257287745
|  | Spectral Components | Voltage C-N Harmonics | H33 Voltage C-N Magnitude RMS | H33 Voltage C-N Magnitude RMS | 423846 | F32-4321 | R | 257287839
|  | Spectral Components | Voltage C-N Harmonics | H34 Voltage C-N Angle | H34 Voltage C-N Angle | 423854 | F32-4321 | R | 257287748
|  | Spectral Components | Voltage C-N Harmonics | H34 Voltage C-N Magnitude | H34 Voltage C-N Magnitude | 423850 | F32-4321 | R | 257287747
|  | Spectral Components | Voltage C-N Harmonics | H34 Voltage C-N Magnitude RMS | H34 Voltage C-N Magnitude RMS | 423852 | F32-4321 | R | 257287840
|  | Spectral Components | Voltage C-N Harmonics | H35 Voltage C-N Angle | H35 Voltage C-N Angle | 423860 | F32-4321 | R | 257287750
|  | Spectral Components | Voltage C-N Harmonics | H35 Voltage C-N Magnitude | H35 Voltage C-N Magnitude | 423856 | F32-4321 | R | 257287749
|  | Spectral Components | Voltage C-N Harmonics | H35 Voltage C-N Magnitude RMS | H35 Voltage C-N Magnitude RMS | 423858 | F32-4321 | R | 257287841
|  | Spectral Components | Voltage C-N Harmonics | H36 Voltage C-N Angle | H36 Voltage C-N Angle | 423866 | F32-4321 | R | 257287752
|  | Spectral Components | Voltage C-N Harmonics | H36 Voltage C-N Magnitude | H36 Voltage C-N Magnitude | 423862 | F32-4321 | R | 257287751
|  | Spectral Components | Voltage C-N Harmonics | H36 Voltage C-N Magnitude RMS | H36 Voltage C-N Magnitude RMS | 423864 | F32-4321 | R | 257287842
|  | Spectral Components | Voltage C-N Harmonics | H37 Voltage C-N Angle | H37 Voltage C-N Angle | 423872 | F32-4321 | R | 257287754
|  | Spectral Components | Voltage C-N Harmonics | H37 Voltage C-N Magnitude | H37 Voltage C-N Magnitude | 423868 | F32-4321 | R | 257287753
|  | Spectral Components | Voltage C-N Harmonics | H37 Voltage C-N Magnitude RMS | H37 Voltage C-N Magnitude RMS | 423870 | F32-4321 | R | 257287843
|  | Spectral Components | Voltage C-N Harmonics | H38 Voltage C-N Angle | H38 Voltage C-N Angle | 423878 | F32-4321 | R | 257287756
|  | Spectral Components | Voltage C-N Harmonics | H38 Voltage C-N Magnitude | H38 Voltage C-N Magnitude | 423874 | F32-4321 | R | 257287755
|  | Spectral Components | Voltage C-N Harmonics | H38 Voltage C-N Magnitude RMS | H38 Voltage C-N Magnitude RMS | 423876 | F32-4321 | R | 257287844
|  | Spectral Components | Voltage C-N Harmonics | H39 Voltage C-N Angle | H39 Voltage C-N Angle | 423884 | F32-4321 | R | 257287758
|  | Spectral Components | Voltage C-N Harmonics | H39 Voltage C-N Magnitude | H39 Voltage C-N Magnitude | 423880 | F32-4321 | R | 257287757
|  | Spectral Components | Voltage C-N Harmonics | H39 Voltage C-N Magnitude RMS | H39 Voltage C-N Magnitude RMS | 423882 | F32-4321 | R | 257287845
|  | Spectral Components | Voltage C-N Harmonics | H40 Voltage C-N Angle | H40 Voltage C-N Angle | 423890 | F32-4321 | R | 257287760
|  | Spectral Components | Voltage C-N Harmonics | H40 Voltage C-N Magnitude | H40 Voltage C-N Magnitude | 423886 | F32-4321 | R | 257287759
|  | Spectral Components | Voltage C-N Harmonics | H40 Voltage C-N Magnitude RMS | H40 Voltage C-N Magnitude RMS | 423888 | F32-4321 | R | 257287846
|  | Spectral Components | Voltage C-N Harmonics | H41 Voltage C-N Angle | H41 Voltage C-N Angle | 423896 | F32-4321 | R | 257287762
|  | Spectral Components | Voltage C-N Harmonics | H41 Voltage C-N Magnitude | H41 Voltage C-N Magnitude | 423892 | F32-4321 | R | 257287761
|  | Spectral Components | Voltage C-N Harmonics | H41 Voltage C-N Magnitude RMS | H41 Voltage C-N Magnitude RMS | 423894 | F32-4321 | R | 257287847
|  | Spectral Components | Voltage C-N Harmonics | H42 Voltage C-N Angle | H42 Voltage C-N Angle | 423902 | F32-4321 | R | 257287764
|  | Spectral Components | Voltage C-N Harmonics | H42 Voltage C-N Magnitude | H42 Voltage C-N Magnitude | 423898 | F32-4321 | R | 257287763
|  | Spectral Components | Voltage C-N Harmonics | H42 Voltage C-N Magnitude RMS | H42 Voltage C-N Magnitude RMS | 423900 | F32-4321 | R | 257287848
|  | Spectral Components | Voltage C-N Harmonics | H43 Voltage C-N Angle | H43 Voltage C-N Angle | 423908 | F32-4321 | R | 257287766
|  | Spectral Components | Voltage C-N Harmonics | H43 Voltage C-N Magnitude | H43 Voltage C-N Magnitude | 423904 | F32-4321 | R | 257287765
|  | Spectral Components | Voltage C-N Harmonics | H43 Voltage C-N Magnitude RMS | H43 Voltage C-N Magnitude RMS | 423906 | F32-4321 | R | 257287849
|  | Spectral Components | Voltage C-N Harmonics | H44 Voltage C-N Angle | H44 Voltage C-N Angle | 423914 | F32-4321 | R | 257287768
|  | Spectral Components | Voltage C-N Harmonics | H44 Voltage C-N Magnitude | H44 Voltage C-N Magnitude | 423910 | F32-4321 | R | 257287767
|  | Spectral Components | Voltage C-N Harmonics | H44 Voltage C-N Magnitude RMS | H44 Voltage C-N Magnitude RMS | 423912 | F32-4321 | R | 257287850
|  | Spectral Components | Voltage C-N Harmonics | H45 Voltage C-N Angle | H45 Voltage C-N Angle | 423920 | F32-4321 | R | 257287770
|  | Spectral Components | Voltage C-N Harmonics | H45 Voltage C-N Magnitude | H45 Voltage C-N Magnitude | 423916 | F32-4321 | R | 257287769
|  | Spectral Components | Voltage C-N Harmonics | H45 Voltage C-N Magnitude RMS | H45 Voltage C-N Magnitude RMS | 423918 | F32-4321 | R | 257287851
|  | Spectral Components | Voltage C-N Harmonics | H46 Voltage C-N Angle | H46 Voltage C-N Angle | 423926 | F32-4321 | R | 257287772
|  | Spectral Components | Voltage C-N Harmonics | H46 Voltage C-N Magnitude | H46 Voltage C-N Magnitude | 423922 | F32-4321 | R | 257287771
|  | Spectral Components | Voltage C-N Harmonics | H46 Voltage C-N Magnitude RMS | H46 Voltage C-N Magnitude RMS | 423924 | F32-4321 | R | 257287852
|  | Spectral Components | Voltage C-N Harmonics | H47 Voltage C-N Angle | H47 Voltage C-N Angle | 423932 | F32-4321 | R | 257287774
|  | Spectral Components | Voltage C-N Harmonics | H47 Voltage C-N Magnitude | H47 Voltage C-N Magnitude | 423928 | F32-4321 | R | 257287773
|  | Spectral Components | Voltage C-N Harmonics | H47 Voltage C-N Magnitude RMS | H47 Voltage C-N Magnitude RMS | 423930 | F32-4321 | R | 257287853
|  | Spectral Components | Voltage C-N Harmonics | H48 Voltage C-N Angle | H48 Voltage C-N Angle | 423938 | F32-4321 | R | 257287776
|  | Spectral Components | Voltage C-N Harmonics | H48 Voltage C-N Magnitude | H48 Voltage C-N Magnitude | 423934 | F32-4321 | R | 257287775
|  | Spectral Components | Voltage C-N Harmonics | H48 Voltage C-N Magnitude RMS | H48 Voltage C-N Magnitude RMS | 423936 | F32-4321 | R | 257287854
|  | Spectral Components | Voltage C-N Harmonics | H49 Voltage C-N Angle | H49 Voltage C-N Angle | 423944 | F32-4321 | R | 257287778
|  | Spectral Components | Voltage C-N Harmonics | H49 Voltage C-N Magnitude | H49 Voltage C-N Magnitude | 423940 | F32-4321 | R | 257287777
|  | Spectral Components | Voltage C-N Harmonics | H49 Voltage C-N Magnitude RMS | H49 Voltage C-N Magnitude RMS | 423942 | F32-4321 | R | 257287855
|  | Spectral Components | Voltage C-N Harmonics | H50 Voltage C-N Angle | H50 Voltage C-N Angle | 423950 | F32-4321 | R | 257287780
|  | Spectral Components | Voltage C-N Harmonics | H50 Voltage C-N Magnitude | H50 Voltage C-N Magnitude | 423946 | F32-4321 | R | 257287779
|  | Spectral Components | Voltage C-N Harmonics | H50 Voltage C-N Magnitude RMS | H50 Voltage C-N Magnitude RMS | 423948 | F32-4321 | R | 257287856
|  | Spectral Components | Voltage C-N Harmonics | H51 Voltage C-N Angle | H51 Voltage C-N Angle | 423956 | F32-4321 | R | 257287782
|  | Spectral Components | Voltage C-N Harmonics | H51 Voltage C-N Magnitude | H51 Voltage C-N Magnitude | 423952 | F32-4321 | R | 257287781
|  | Spectral Components | Voltage C-N Harmonics | H51 Voltage C-N Magnitude RMS | H51 Voltage C-N Magnitude RMS | 423954 | F32-4321 | R | 257287857
|  | Spectral Components | Voltage C-N Harmonics | H52 Voltage C-N Angle | H52 Voltage C-N Angle | 423962 | F32-4321 | R | 257287784
|  | Spectral Components | Voltage C-N Harmonics | H52 Voltage C-N Magnitude | H52 Voltage C-N Magnitude | 423958 | F32-4321 | R | 257287783
|  | Spectral Components | Voltage C-N Harmonics | H52 Voltage C-N Magnitude RMS | H52 Voltage C-N Magnitude RMS | 423960 | F32-4321 | R | 257287858
|  | Spectral Components | Voltage C-N Harmonics | H53 Voltage C-N Angle | H53 Voltage C-N Angle | 423968 | F32-4321 | R | 257287786
|  | Spectral Components | Voltage C-N Harmonics | H53 Voltage C-N Magnitude | H53 Voltage C-N Magnitude | 423964 | F32-4321 | R | 257287785
|  | Spectral Components | Voltage C-N Harmonics | H53 Voltage C-N Magnitude RMS | H53 Voltage C-N Magnitude RMS | 423966 | F32-4321 | R | 257287859
|  | Spectral Components | Voltage C-N Harmonics | H54 Voltage C-N Angle | H54 Voltage C-N Angle | 423974 | F32-4321 | R | 257287788
|  | Spectral Components | Voltage C-N Harmonics | H54 Voltage C-N Magnitude | H54 Voltage C-N Magnitude | 423970 | F32-4321 | R | 257287787
|  | Spectral Components | Voltage C-N Harmonics | H54 Voltage C-N Magnitude RMS | H54 Voltage C-N Magnitude RMS | 423972 | F32-4321 | R | 257287860
|  | Spectral Components | Voltage C-N Harmonics | H55 Voltage C-N Angle | H55 Voltage C-N Angle | 423980 | F32-4321 | R | 257287790
|  | Spectral Components | Voltage C-N Harmonics | H55 Voltage C-N Magnitude | H55 Voltage C-N Magnitude | 423976 | F32-4321 | R | 257287789
|  | Spectral Components | Voltage C-N Harmonics | H55 Voltage C-N Magnitude RMS | H55 Voltage C-N Magnitude RMS | 423978 | F32-4321 | R | 257287861
|  | Spectral Components | Voltage C-N Harmonics | H56 Voltage C-N Angle | H56 Voltage C-N Angle | 423986 | F32-4321 | R | 257287792
|  | Spectral Components | Voltage C-N Harmonics | H56 Voltage C-N Magnitude | H56 Voltage C-N Magnitude | 423982 | F32-4321 | R | 257287791
|  | Spectral Components | Voltage C-N Harmonics | H56 Voltage C-N Magnitude RMS | H56 Voltage C-N Magnitude RMS | 423984 | F32-4321 | R | 257287862
|  | Spectral Components | Voltage C-N Harmonics | H57 Voltage C-N Angle | H57 Voltage C-N Angle | 423992 | F32-4321 | R | 257287794
|  | Spectral Components | Voltage C-N Harmonics | H57 Voltage C-N Magnitude | H57 Voltage C-N Magnitude | 423988 | F32-4321 | R | 257287793
|  | Spectral Components | Voltage C-N Harmonics | H57 Voltage C-N Magnitude RMS | H57 Voltage C-N Magnitude RMS | 423990 | F32-4321 | R | 257287863
|  | Spectral Components | Voltage C-N Harmonics | H58 Voltage C-N Angle | H58 Voltage C-N Angle | 423998 | F32-4321 | R | 257287796
|  | Spectral Components | Voltage C-N Harmonics | H58 Voltage C-N Magnitude | H58 Voltage C-N Magnitude | 423994 | F32-4321 | R | 257287795
|  | Spectral Components | Voltage C-N Harmonics | H58 Voltage C-N Magnitude RMS | H58 Voltage C-N Magnitude RMS | 423996 | F32-4321 | R | 257287864
|  | Spectral Components | Voltage C-N Harmonics | H59 Voltage C-N Angle | H59 Voltage C-N Angle | 424004 | F32-4321 | R | 257287798
|  | Spectral Components | Voltage C-N Harmonics | H59 Voltage C-N Magnitude | H59 Voltage C-N Magnitude | 424000 | F32-4321 | R | 257287797
|  | Spectral Components | Voltage C-N Harmonics | H59 Voltage C-N Magnitude RMS | H59 Voltage C-N Magnitude RMS | 424002 | F32-4321 | R | 257287865
|  | Spectral Components | Voltage C-N Harmonics | H60 Voltage C-N Angle | H60 Voltage C-N Angle | 424010 | F32-4321 | R | 257287800
|  | Spectral Components | Voltage C-N Harmonics | H60 Voltage C-N Magnitude | H60 Voltage C-N Magnitude | 424006 | F32-4321 | R | 257287799
|  | Spectral Components | Voltage C-N Harmonics | H60 Voltage C-N Magnitude RMS | H60 Voltage C-N Magnitude RMS | 424008 | F32-4321 | R | 257287866
|  | Spectral Components | Voltage C-N Harmonics | H61 Voltage C-N Angle | H61 Voltage C-N Angle | 424016 | F32-4321 | R | 257287802
|  | Spectral Components | Voltage C-N Harmonics | H61 Voltage C-N Magnitude | H61 Voltage C-N Magnitude | 424012 | F32-4321 | R | 257287801
|  | Spectral Components | Voltage C-N Harmonics | H61 Voltage C-N Magnitude RMS | H61 Voltage C-N Magnitude RMS | 424014 | F32-4321 | R | 257287867
|  | Spectral Components | Voltage C-N Harmonics | H62 Voltage C-N Angle | H62 Voltage C-N Angle | 424022 | F32-4321 | R | 257287804
|  | Spectral Components | Voltage C-N Harmonics | H62 Voltage C-N Magnitude | H62 Voltage C-N Magnitude | 424018 | F32-4321 | R | 257287803
|  | Spectral Components | Voltage C-N Harmonics | H62 Voltage C-N Magnitude RMS | H62 Voltage C-N Magnitude RMS | 424020 | F32-4321 | R | 257287868
|  | Spectral Components | Voltage C-N Harmonics | H63 Voltage C-N Angle | H63 Voltage C-N Angle | 424028 | F32-4321 | R | 257287806
|  | Spectral Components | Voltage C-N Harmonics | H63 Voltage C-N Magnitude | H63 Voltage C-N Magnitude | 424024 | F32-4321 | R | 257287805
|  | Spectral Components | Voltage C-N Harmonics | H63 Voltage C-N Magnitude RMS | H63 Voltage C-N Magnitude RMS | 424026 | F32-4321 | R | 257287869
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate A | Active Energy Delivered Rate A | 404196 | S64-87-21 | R | 258335489 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate B | Active Energy Delivered Rate B | 404200 | S64-87-21 | R | 258335490 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate C | Active Energy Delivered Rate C | 404204 | S64-87-21 | R | 258335491 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate D | Active Energy Delivered Rate D | 404208 | S64-87-21 | R | 258335492 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate E | Active Energy Delivered Rate E | 404212 | S64-87-21 | R | 258335493 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate F | Active Energy Delivered Rate F | 404216 | S64-87-21 | R | 258335494 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate G | Active Energy Delivered Rate G | 404220 | S64-87-21 | R | 258335495 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate H | Active Energy Delivered Rate H | 404224 | S64-87-21 | R | 258335496 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate A | Apparent Energy Delivered Rate A | 404324 | S64-87-21 | R | 258336001 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate B | Apparent Energy Delivered Rate B | 404328 | S64-87-21 | R | 258336002 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate C | Apparent Energy Delivered Rate C | 404332 | S64-87-21 | R | 258336003 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate D | Apparent Energy Delivered Rate D | 404336 | S64-87-21 | R | 258336004 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate E | Apparent Energy Delivered Rate E | 404340 | S64-87-21 | R | 258336005 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate F | Apparent Energy Delivered Rate F | 404344 | S64-87-21 | R | 258336006 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate G | Apparent Energy Delivered Rate G | 404348 | S64-87-21 | R | 258336007 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate H | Apparent Energy Delivered Rate H | 404352 | S64-87-21 | R | 258336008 |  | 1000
|  | Time of Use | DT Time of Use Last Reset | DT Time of Use Last Reset | DT Time of Use Last Reset | 404192 | DateTime_IEC870_UTC | R | 258335233
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate A | Reactive Energy Delivered Rate A | 404260 | S64-87-21 | R | 258335745 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate B | Reactive Energy Delivered Rate B | 404264 | S64-87-21 | R | 258335746 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate C | Reactive Energy Delivered Rate C | 404268 | S64-87-21 | R | 258335747 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate D | Reactive Energy Delivered Rate D | 404272 | S64-87-21 | R | 258335748 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate E | Reactive Energy Delivered Rate E | 404276 | S64-87-21 | R | 258335749 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate F | Reactive Energy Delivered Rate F | 404280 | S64-87-21 | R | 258335750 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate G | Reactive Energy Delivered Rate G | 404284 | S64-87-21 | R | 258335751 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate H | Reactive Energy Delivered Rate H | 404288 | S64-87-21 | R | 258335752 |  | 1000
|  | Time of Use | Time of Use Active Rate | Time of Use Active Rate | Time of Use Active Rate | 404191 | UINT16 | R | 258334977
|  | Time of Use | Active Energy Received | Active Energy Received Rate A | Active Energy Received Rate A | 404228 | S64-87-21 | R | 225443841 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate B | Active Energy Received Rate B | 404232 | S64-87-21 | R | 225443842 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate C | Active Energy Received Rate C | 404236 | S64-87-21 | R | 225443843 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate D | Active Energy Received Rate D | 404240 | S64-87-21 | R | 225443844 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate E | Active Energy Received Rate E | 404244 | S64-87-21 | R | 225443845 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate F | Active Energy Received Rate F | 404248 | S64-87-21 | R | 225443846 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate G | Active Energy Received Rate G | 404252 | S64-87-21 | R | 225443847 |  | 1000
|  | Time of Use | Active Energy Received | Active Energy Received Rate H | Active Energy Received Rate H | 404256 | S64-87-21 | R | 225443848 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate A | Reactive Energy Received Rate A | 404292 | S64-87-21 | R | 225444097 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate B | Reactive Energy Received Rate B | 404296 | S64-87-21 | R | 225444098 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate C | Reactive Energy Received Rate C | 404300 | S64-87-21 | R | 225444099 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate D | Reactive Energy Received Rate D | 404304 | S64-87-21 | R | 225444100 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate E | Reactive Energy Received Rate E | 404308 | S64-87-21 | R | 225444101 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate F | Reactive Energy Received Rate F | 404312 | S64-87-21 | R | 225444102 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate G | Reactive Energy Received Rate G | 404316 | S64-87-21 | R | 225444103 |  | 1000
|  | Time of Use | Reactive Energy Received | Reactive Energy Received Rate H | Reactive Energy Received Rate H | 404320 | S64-87-21 | R | 225444104 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate A | Apparent Energy Received Rate A | 404356 | S64-87-21 | R | 225444353 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate B | Apparent Energy Received Rate B | 404360 | S64-87-21 | R | 225444354 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate C | Apparent Energy Received Rate C | 404364 | S64-87-21 | R | 225444355 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate D | Apparent Energy Received Rate D | 404368 | S64-87-21 | R | 225444356 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate E | Apparent Energy Received Rate E | 404372 | S64-87-21 | R | 225444357 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate F | Apparent Energy Received Rate F | 404376 | S64-87-21 | R | 225444358 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate G | Apparent Energy Received Rate G | 404380 | S64-87-21 | R | 225444359 |  | 1000
|  | Time of Use | Apparent Energy Received | Apparent Energy Received Rate H | Apparent Energy Received Rate H | 404384 | S64-87-21 | R | 225444360 |  | 1000
|  | Unbalances | Current Unbalance | Current Unbalance A | Current Unbalance A | 403012 | F32-4321 | R | 198180865 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance B | Current Unbalance B | 403014 | F32-4321 | R | 198180866 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance C | Current Unbalance C | 403016 | F32-4321 | R | 198180867 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance Worst | Current Unbalance Worst | 403018 | F32-4321 | R | 198180868 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-B | Voltage Unbalance A-B | 403038 | F32-4321 | R | 198181121 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-N | Voltage Unbalance A-N | 403046 | F32-4321 | R | 198181125 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-C | Voltage Unbalance B-C | 403040 | F32-4321 | R | 198181122 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-N | Voltage Unbalance B-N | 403048 | F32-4321 | R | 198181126 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-A | Voltage Unbalance C-A | 403042 | F32-4321 | R | 198181123 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-N | Voltage Unbalance C-N | 403050 | F32-4321 | R | 198181127 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-L Worst | Voltage Unbalance L-L Worst | 403044 | F32-4321 | R | 198181124 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-N Worst | Voltage Unbalance L-N Worst | 403052 | F32-4321 | R | 198181128 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage A-B | Voltage A-B | 403020 | F32-4321 | R | 201326593 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage A-N | Voltage A-N | 403028 | F32-4321 | R | 201326597 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage B-C | Voltage B-C | 403022 | F32-4321 | R | 201326594 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage B-N | Voltage B-N | 403030 | F32-4321 | R | 201326598 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage C-A | Voltage C-A | 403024 | F32-4321 | R | 201326595 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage C-N | Voltage C-N | 403032 | F32-4321 | R | 201326599 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage L-L Avg | Voltage L-L Avg | 403026 | F32-4321 | R | 201326596 |  |  |  |  | 2
DR2 | 900 secs | Voltages | Voltage | Voltage L-N Avg | Voltage L-N Avg | 403036 | F32-4321 | R | 201326600 |  |  |  |  | 2
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Trigger |  |  |  |  | 202375171
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Period |  |  |  |  | 202375169
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Sync Mode |  |  |  |  | 202375170
|  | PeriodicTimer Modules | Periodic Tmr 2 | PT2 Trigger |  |  |  |  | 202375427
|  | PeriodicTimer Modules | Periodic Tmr 2 | PT2 Period |  |  |  |  | 202375425
|  | PeriodicTimer Modules | Periodic Tmr 2 | PT2 Sync Mode |  |  |  |  | 202375426
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  |  |  |  | 203423745
|  | Feedback Modules | Feedback 2 | FBK2 Pulse Out |  |  |  |  | 203424001
|  | DataRecorder Modules | Data Rec 1 | RE2 Data Log |  |  |  |  | 135266561
|  | DataRecorder Modules | Data Rec 1 | RE2 Log State |  |  |  |  | 135266562
|  | DataRecorder Modules | Data Rec 1 | RE2 Records Left |  |  |  |  | 135266563
|  | DataRecorder Modules | Data Rec 1 | RE2 Record Complete |  |  |  |  | 135266564
|  | DataRecorder Modules | Data Rec 1 | RE2 Depth |  |  |  |  | 135266565
|  | DataRecorder Modules | Data Rec 1 | RE2 RecordMode |  |  |  |  | 135266566
|  | DataRecorder Modules | Data Rec 1 | RE2 Staleness Threshold |  |  |  |  | 135266567
|  | DataRecorder Modules | Data Rec 1 | RE2 Staleness Action |  |  |  |  | 135266568
|  | DataRecorder Modules | Data Rec 2 | RE3 Data Log |  |  |  |  | 135266817
|  | DataRecorder Modules | Data Rec 2 | RE3 Log State |  |  |  |  | 135266818
|  | DataRecorder Modules | Data Rec 2 | RE3 Records Left |  |  |  |  | 135266819
|  | DataRecorder Modules | Data Rec 2 | RE3 Record Complete |  |  |  |  | 135266820
|  | DataRecorder Modules | Data Rec 2 | RE3 Depth |  |  |  |  | 135266821
|  | DataRecorder Modules | Data Rec 2 | RE3 RecordMode |  |  |  |  | 135266822
|  | DataRecorder Modules | Data Rec 2 | RE3 Staleness Threshold |  |  |  |  | 135266823
|  | DataRecorder Modules | Data Rec 2 | RE3 Staleness Action |  |  |  |  | 135266824
|  | DataRecorder Modules | Data Rec 3 | RE4 Data Log |  |  |  |  | 135267329
|  | DataRecorder Modules | Data Rec 3 | RE4 Log State |  |  |  |  | 135267330
|  | DataRecorder Modules | Data Rec 3 | RE4 Records Left |  |  |  |  | 135267331
|  | DataRecorder Modules | Data Rec 3 | RE4 Record Complete |  |  |  |  | 135267332
|  | DataRecorder Modules | Data Rec 3 | RE4 Depth |  |  |  |  | 135267333
|  | DataRecorder Modules | Data Rec 3 | RE4 RecordMode |  |  |  |  | 135267334
|  | DataRecorder Modules | Data Rec 3 | RE4 Staleness Threshold |  |  |  |  | 135267335
|  | DataRecorder Modules | Data Rec 3 | RE4 Staleness Action |  |  |  |  | 135267336

## PM5300_LE
PM5300_LE Series Translator Details
Data Recorder | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | ModbusAddr | Format | RequestType | IONHandle | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | 400090 | UINT16 | R | 4864 |  |  |  |  | 1
|  | Factory Information | Factory 1 | FAC1 Compliance |  |  |  |  | 4865
|  | Factory Information | Factory 1 | FAC1 Options |  |  |  |  | 4866
|  | Factory Information | Factory 1 | FAC1 Revision | FAC1 Revision | 401637 | UINT16 | R | 4867
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | 400130 | UINT32 | R | 4868 |  |  |  |  | 2
|  | Factory Information | Factory 1 | FAC1 ION Version |  |  |  |  | 30510
|  | Factory Information | Factory 1 | FAC1 Template |  |  |  |  | 4989
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | 400030 | ASCII | R | 22340 |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 Manuf Date Time | FAC1 Manuf Date Time | 400132 | DateTime3_IEC870_UTC | R | 30129
|  | Factory Information | Factory 1 | FAC1 Hardware Revision | FAC1 Hardware Revision | 400136 | ASCII | R | 30130 |  |  |  |  | 5
|  | Factory Information | Factory 1 | FAC1 FW Rev RS | FAC1 FW Rev RS | 401669 | UINT16 | R | 30131
|  | Alarm - Summary | Alarm Counters | High Priority Counter | High Priority Counter | 413522 | UINT16 | R | 160432388
|  | Alarm - Summary | Alarm Counters | Low Priority Counter | Low Priority Counter | 413520 | UINT16 | R | 160432386
|  | Alarm - Summary | Alarm Counters | Medium Priority Counter | Medium Priority Counter | 413521 | UINT16 | R | 160432387
|  | Alarm - Summary | Alarm Counters | Total Alarms Counter | Total Alarms Counter | 413519 | UINT16 | R | 160432385
|  | Alarm - Summary | Alarm Status | Alarm Active | Alarm Active | 411010 | MaskedBool | R | 160432129 | 0x0001
|  | Alarm - Summary | Alarm Status | High Priority Active | High Priority Active | 411010 | MaskedBool | R | 160432130 | 0x0002
|  | Alarm - Summary | Alarm Status | Low Priority Active | Low Priority Active | 411010 | MaskedBool | R | 160432132 | 0x0008
|  | Alarm - Summary | Alarm Status | Medium Priority Active | Medium Priority Active | 411010 | MaskedBool | R | 160432131 | 0x0004
|  | Alarm - Summary | Alarm Status | Priority None Active | Priority None Active | 411010 | MaskedBool | R | 160432133 | 0x0010
|  | Alarms - Over Under | Over Active Power | Over Active Power Alarm | Over Active Power Alarm | 411059 | MaskedBool | R | 209719297 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Ack Status | Over Active Power-Ack Status | 411078 | MaskedBool | R | 209719298 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Count | Over Active Power-Alarm Count | 413531 | UINT16 | R | 209719306
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Enabled | Over Active Power-Alarm Enabled | 411040 | MaskedBool | R | 209719299 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Output | Over Active Power-Alarm Output | 414173 | UINT16 | R | 209719305 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Priority | Over Active Power-Alarm Priority | 414160 | UINT32 | R | 209719300 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Delay | Over Active Power-Dropout Delay | 414171 | UINT32 | R | 209719304
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Setpoint | Over Active Power-Dropout Setpoint | 414169 | F32-4321 | R | 209719303
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Delay | Over Active Power-Pickup Delay | 414167 | UINT32 | R | 209719302
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Setpoint | Over Active Power-Pickup Setpoint | 414165 | F32-4321 | R | 209719301
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power Alarm | Over Apparent Power Alarm | 411059 | MaskedBool | R | 209717249 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Ack Status | Over Apparent Power-Ack Status | 411078 | MaskedBool | R | 209717250 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Count | Over Apparent Power-Alarm Count | 413533 | UINT16 | R | 209717258
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Enabled | Over Apparent Power-Alarm Enabled | 411040 | MaskedBool | R | 209717251 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Output | Over Apparent Power-Alarm Output | 414213 | UINT16 | R | 209717257 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Priority | Over Apparent Power-Alarm Priority | 414200 | UINT32 | R | 209717252 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Delay | Over Apparent Power-Dropout Delay | 414211 | UINT32 | R | 209717256
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Setpoint | Over Apparent Power-Dropout Setpoint | 414209 | F32-4321 | R | 209717255
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Delay | Over Apparent Power-Pickup Delay | 414207 | UINT32 | R | 209717254
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Setpoint | Over Apparent Power-Pickup Setpoint | 414205 | F32-4321 | R | 209717253
|  | Alarms - Over Under | Over Current N | Over Current Neutral Alarm | Over Current Neutral Alarm | 411059 | MaskedBool | R | 209716481 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Ack Status | Over Current Neutral-Ack Status | 411078 | MaskedBool | R | 209716482 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Count | Over Current Neutral-Alarm Count | 413525 | UINT16 | R | 209716490
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Enabled | Over Current Neutral-Alarm Enabled | 411040 | MaskedBool | R | 209716483 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Output | Over Current Neutral-Alarm Output | 414053 | UINT16 | R | 209716489 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Priority | Over Current Neutral-Alarm Priority | 414040 | UINT32 | R | 209716484 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Delay | Over Current Neutral-Dropout Delay | 414051 | UINT32 | R | 209716488
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Setpoint | Over Current Neutral-Dropout Setpoint | 414049 | F32-4321 | R | 209716487
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Delay | Over Current Neutral-Pickup Delay | 414047 | UINT32 | R | 209716486
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Setpoint | Over Current Neutral-Pickup Setpoint | 414045 | F32-4321 | R | 209716485
|  | Alarms - Over Under | Over Current Phase | Over Current Phase Alarm | Over Current Phase Alarm | 411059 | MaskedBool | R | 209716737 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Ack Status | Over Current Phase-Ack Status | 411078 | MaskedBool | R | 209716738 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Count | Over Current Phase-Alarm Count | 413523 | UINT16 | R | 209716746
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Enabled | Over Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209716739 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Output | Over Current Phase-Alarm Output | 414013 | UINT16 | R | 209716745 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Priority | Over Current Phase-Alarm Priority | 414000 | UINT32 | R | 209716740 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Delay | Over Current Phase-Dropout Delay | 414011 | UINT32 | R | 209716744
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Setpoint | Over Current Phase-Dropout Setpoint | 414009 | F32-4321 | R | 209716743
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Delay | Over Current Phase-Pickup Delay | 414007 | UINT32 | R | 209716742
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Setpoint | Over Current Phase-Pickup Setpoint | 414005 | F32-4321 | R | 209716741
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last Alarm | Over Demand Active Power Last Alarm | 411060 | MaskedBool | R | 209719553 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Ack Status | Over Demand Active Power Last-Ack Status | 411079 | MaskedBool | R | 209719554 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Count | Over Demand Active Power Last-Alarm Count | 413539 | UINT16 | R | 209719562
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Enabled | Over Demand Active Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209719555 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Output | Over Demand Active Power Last-Alarm Output | 414333 | UINT16 | R | 209719561 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Priority | Over Demand Active Power Last-Alarm Priority | 414320 | UINT32 | R | 209719556 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Delay | Over Demand Active Power Last-Dropout Delay | 414331 | UINT32 | R | 209719560
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Setpoint | Over Demand Active Power Last-Dropout Setpoint | 414329 | F32-4321 | R | 209719559
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Delay | Over Demand Active Power Last-Pickup Delay | 414327 | UINT32 | R | 209719558
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Setpoint | Over Demand Active Power Last-Pickup Setpoint | 414325 | F32-4321 | R | 209719557
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted Alarm | Over Demand Active Power Predicted Alarm | 411060 | MaskedBool | R | 209719809 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Ack Status | Over Demand Active Power Predicted-Ack Status | 411079 | MaskedBool | R | 209719810 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Count | Over Demand Active Power Predicted-Alarm Count | 413540 | UINT16 | R | 209719818
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Enabled | Over Demand Active Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209719811 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Output | Over Demand Active Power Predicted-Alarm Output | 414353 | UINT16 | R | 209719817 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Priority | Over Demand Active Power Predicted-Alarm Priority | 414340 | UINT32 | R | 209719812 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Delay | Over Demand Active Power Predicted-Dropout Delay | 414351 | UINT32 | R | 209719816
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Setpoint | Over Demand Active Power Predicted-Dropout Setpoint | 414349 | F32-4321 | R | 209719815
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Delay | Over Demand Active Power Predicted-Pickup Delay | 414347 | UINT32 | R | 209719814
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Setpoint | Over Demand Active Power Predicted-Pickup Setpoint | 414345 | F32-4321 | R | 209719813
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present Alarm | Over Demand Active Power Present Alarm | 411059 | MaskedBool | R | 209720065 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Ack Status | Over Demand Active Power Present-Ack Status | 411078 | MaskedBool | R | 209720066 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Count | Over Demand Active Power Present-Alarm Count | 413538 | UINT16 | R | 209720074
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Enabled | Over Demand Active Power Present-Alarm Enabled | 411040 | MaskedBool | R | 209720067 | 0x8000 | 32768 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Output | Over Demand Active Power Present-Alarm Output | 414313 | UINT16 | R | 209720073 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Priority | Over Demand Active Power Present-Alarm Priority | 414300 | UINT32 | R | 209720068 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Delay | Over Demand Active Power Present-Dropout Delay | 414311 | UINT32 | R | 209720072
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Setpoint | Over Demand Active Power Present-Dropout Setpoint | 414309 | F32-4321 | R | 209720071
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Delay | Over Demand Active Power Present-Pickup Delay | 414307 | UINT32 | R | 209720070
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Setpoint | Over Demand Active Power Present-Pickup Setpoint | 414305 | F32-4321 | R | 209720069
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last Alarm | Over Demand Apparent Power Last Alarm | 411060 | MaskedBool | R | 209717505 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Ack Status | Over Demand Apparent Power Last-Ack Status | 411079 | MaskedBool | R | 209717506 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Count | Over Demand Apparent Power Last-Alarm Count | 413545 | UINT16 | R | 209717514
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Enabled | Over Demand Apparent Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209717507 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Output | Over Demand Apparent Power Last-Alarm Output | 414453 | UINT16 | R | 209717513 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Priority | Over Demand Apparent Power Last-Alarm Priority | 414440 | UINT32 | R | 209717508 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Delay | Over Demand Apparent Power Last-Dropout Delay | 414451 | UINT32 | R | 209717512
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Setpoint | Over Demand Apparent Power Last-Dropout Setpoint | 414449 | F32-4321 | R | 209717511
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Delay | Over Demand Apparent Power Last-Pickup Delay | 414447 | UINT32 | R | 209717510
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Setpoint | Over Demand Apparent Power Last-Pickup Setpoint | 414445 | F32-4321 | R | 209717509
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted Alarm | Over Demand Apparent Power Predicted Alarm | 411060 | MaskedBool | R | 209717761 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Ack Status | Over Demand Apparent Power Predicted-Ack Status | 411079 | MaskedBool | R | 209717762 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Count | Over Demand Apparent Power Predicted-Alarm Count | 413546 | UINT16 | R | 209717770
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Enabled | Over Demand Apparent Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209717763 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Output | Over Demand Apparent Power Predicted-Alarm Output | 414473 | UINT16 | R | 209717769 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Priority | Over Demand Apparent Power Predicted-Alarm Priority | 414460 | UINT32 | R | 209717764 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Delay | Over Demand Apparent Power Predicted-Dropout Delay | 414471 | UINT32 | R | 209717768
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Setpoint | Over Demand Apparent Power Predicted-Dropout Setpoint | 414469 | F32-4321 | R | 209717767
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Delay | Over Demand Apparent Power Predicted-Pickup Delay | 414467 | UINT32 | R | 209717766
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Setpoint | Over Demand Apparent Power Predicted-Pickup Setpoint | 414465 | F32-4321 | R | 209717765
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present Alarm | Over Demand Apparent Power Present Alarm | 411060 | MaskedBool | R | 209718017 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Ack Status | Over Demand Apparent Power Present-Ack Status | 411079 | MaskedBool | R | 209718018 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Count | Over Demand Apparent Power Present-Alarm Count | 413544 | UINT16 | R | 209718026
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Enabled | Over Demand Apparent Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209718019 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Output | Over Demand Apparent Power Present-Alarm Output | 414433 | UINT16 | R | 209718025 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Priority | Over Demand Apparent Power Present-Alarm Priority | 414420 | UINT32 | R | 209718020 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Delay | Over Demand Apparent Power Present-Dropout Delay | 414431 | UINT32 | R | 209718024
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Setpoint | Over Demand Apparent Power Present-Dropout Setpoint | 414429 | F32-4321 | R | 209718023
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Delay | Over Demand Apparent Power Present-Pickup Delay | 414427 | UINT32 | R | 209718022
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Setpoint | Over Demand Apparent Power Present-Pickup Setpoint | 414425 | F32-4321 | R | 209718021
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last Alarm | Over Demand Reactive Power Last Alarm | 411060 | MaskedBool | R | 209718529 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Ack Status | Over Demand Reactive Power Last-Ack Status | 411079 | MaskedBool | R | 209718530 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Count | Over Demand Reactive Power Last-Alarm Count | 413542 | UINT16 | R | 209718538
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Enabled | Over Demand Reactive Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209718531 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Output | Over Demand Reactive Power Last-Alarm Output | 414393 | UINT16 | R | 209718537 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Priority | Over Demand Reactive Power Last-Alarm Priority | 414380 | UINT32 | R | 209718532 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Delay | Over Demand Reactive Power Last-Dropout Delay | 414391 | UINT32 | R | 209718536
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Setpoint | Over Demand Reactive Power Last-Dropout Setpoint | 414389 | F32-4321 | R | 209718535
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Delay | Over Demand Reactive Power Last-Pickup Delay | 414387 | UINT32 | R | 209718534
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Setpoint | Over Demand Reactive Power Last-Pickup Setpoint | 414385 | F32-4321 | R | 209718533
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted Alarm | Over Demand Reactive Power Predicted Alarm | 411060 | MaskedBool | R | 209718785 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Ack Status | Over Demand Reactive Power Predicted-Ack Status | 411079 | MaskedBool | R | 209718786 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Count | Over Demand Reactive Power Predicted-Alarm Count | 413543 | UINT16 | R | 209718794
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Enabled | Over Demand Reactive Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209718787 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Output | Over Demand Reactive Power Predicted-Alarm Output | 414413 | UINT16 | R | 209718793 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Priority | Over Demand Reactive Power Predicted-Alarm Priority | 414400 | UINT32 | R | 209718788 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Delay | Over Demand Reactive Power Predicted-Dropout Delay | 414411 | UINT32 | R | 209718792
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Setpoint | Over Demand Reactive Power Predicted-Dropout Setpoint | 414409 | F32-4321 | R | 209718791
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Delay | Over Demand Reactive Power Predicted-Pickup Delay | 414407 | UINT32 | R | 209718790
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Setpoint | Over Demand Reactive Power Predicted-Pickup Setpoint | 414405 | F32-4321 | R | 209718789
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present Alarm | Over Demand Reactive Power Present Alarm | 411060 | MaskedBool | R | 209719041 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Ack Status | Over Demand Reactive Power Present-Ack Status | 411079 | MaskedBool | R | 209719042 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Count | Over Demand Reactive Power Present-Alarm Count | 413541 | UINT16 | R | 209719050
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Enabled | Over Demand Reactive Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209719043 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Output | Over Demand Reactive Power Present-Alarm Output | 414373 | UINT16 | R | 209719049 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Priority | Over Demand Reactive Power Present-Alarm Priority | 414360 | UINT32 | R | 209719044 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Delay | Over Demand Reactive Power Present-Dropout Delay | 414371 | UINT32 | R | 209719048
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Setpoint | Over Demand Reactive Power Present-Dropout Setpoint | 414369 | F32-4321 | R | 209719047
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Delay | Over Demand Reactive Power Present-Pickup Delay | 414367 | UINT32 | R | 209719046
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Setpoint | Over Demand Reactive Power Present-Pickup Setpoint | 414365 | F32-4321 | R | 209719045
|  | Alarms - Over Under | Over Frequency | Over Frequency Alarm | Over Frequency Alarm | 411060 | MaskedBool | R | 209716993 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Ack Status | Over Frequency-Ack Status | 411079 | MaskedBool | R | 209716994 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Count | Over Frequency-Alarm Count | 413547 | UINT16 | R | 209717002
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Enabled | Over Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209716995 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Output | Over Frequency-Alarm Output | 414493 | UINT16 | R | 209717001 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Priority | Over Frequency-Alarm Priority | 414480 | UINT32 | R | 209716996 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Delay | Over Frequency-Dropout Delay | 414491 | UINT32 | R | 209717000
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Setpoint | Over Frequency-Dropout Setpoint | 414489 | F32-4321 | R | 209716999
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Delay | Over Frequency-Pickup Delay | 414487 | UINT32 | R | 209716998
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Setpoint | Over Frequency-Pickup Setpoint | 414485 | F32-4321 | R | 209716997
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor Alarm | Lagging Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715201 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Ack Status | Lagging Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715202 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Count | Lagging Displacement Power Factor-Alarm Count | 413537 | UINT16 | R | 209715210
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Enabled | Lagging Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715203 | 0x4000 | 16384 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Output | Lagging Displacement Power Factor-Alarm Output | 414293 | UINT16 | R | 209715209 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Priority | Lagging Displacement Power Factor-Alarm Priority | 414280 | UINT32 | R | 209715204 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Delay | Lagging Displacement Power Factor-Dropout Delay | 414291 | UINT32 | R | 209715208
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Setpoint | Lagging Displacement Power Factor-Dropout Setpoint | 414289 | F32-4321 | R | 209715207
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Delay | Lagging Displacement Power Factor-Pickup Delay | 414287 | UINT32 | R | 209715206
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Setpoint | Lagging Displacement Power Factor-Pickup Setpoint | 414285 | F32-4321 | R | 209715205
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor Alarm | Lagging Power Factor Alarm | 411059 | MaskedBool | R | 209715457 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Ack Status | Lagging Power Factor-Ack Status | 411078 | MaskedBool | R | 209715458 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Count | Lagging Power Factor-Alarm Count | 413535 | UINT16 | R | 209715466
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Enabled | Lagging Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715459 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Output | Lagging Power Factor-Alarm Output | 414253 | UINT16 | R | 209715465 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Priority | Lagging Power Factor-Alarm Priority | 414240 | UINT32 | R | 209715460 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Delay | Lagging Power Factor-Dropout Delay | 414251 | UINT32 | R | 209715464
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Setpoint | Lagging Power Factor-Dropout Setpoint | 414249 | F32-4321 | R | 209715463
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Delay | Lagging Power Factor-Pickup Delay | 414247 | UINT32 | R | 209715462
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Setpoint | Lagging Power Factor-Pickup Setpoint | 414245 | F32-4321 | R | 209715461
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor Alarm | Leading Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715713 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Ack Status | Leading Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715714 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Count | Leading Displacement Power Factor-Alarm Count | 413536 | UINT16 | R | 209715722
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Enabled | Leading Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715715 | 0x2000 | 8192 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Output | Leading Displacement Power Factor-Alarm Output | 414273 | UINT16 | R | 209715721 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Priority | Leading Displacement Power Factor-Alarm Priority | 414260 | UINT32 | R | 209715716 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Delay | Leading Displacement Power Factor-Dropout Delay | 414271 | UINT32 | R | 209715720
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Setpoint | Leading Displacement Power Factor-Dropout Setpoint | 414269 | F32-4321 | R | 209715719
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Delay | Leading Displacement Power Factor-Pickup Delay | 414267 | UINT32 | R | 209715718
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Setpoint | Leading Displacement Power Factor-Pickup Setpoint | 414265 | F32-4321 | R | 209715717
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor Alarm | Leading Power Factor Alarm | 411059 | MaskedBool | R | 209715970 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Ack Status | Leading Power Factor-Ack Status | 411078 | MaskedBool | R | 209715969 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Count | Leading Power Factor-Alarm Count | 413534 | UINT16 | R | 209715978
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Enabled | Leading Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715971 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Output | Leading Power Factor-Alarm Output | 414233 | UINT16 | R | 209715977 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Priority | Leading Power Factor-Alarm Priority | 414220 | UINT32 | R | 209715972 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Delay | Leading Power Factor-Dropout Delay | 414231 | UINT32 | R | 209715976
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Setpoint | Leading Power Factor-Dropout Setpoint | 414229 | F32-4321 | R | 209715975
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Delay | Leading Power Factor-Pickup Delay | 414227 | UINT32 | R | 209715974
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Setpoint | Leading Power Factor-Pickup Setpoint | 414225 | F32-4321 | R | 209715973
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power Alarm | Over Reactive Power Alarm | 411059 | MaskedBool | R | 209718273 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Ack Status | Over Reactive Power-Ack Status | 411078 | MaskedBool | R | 209718274 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Count | Over Reactive Power-Alarm Count | 413532 | UINT16 | R | 209718282
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Enabled | Over Reactive Power-Alarm Enabled | 411040 | MaskedBool | R | 209718275 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Output | Over Reactive Power-Alarm Output | 414193 | UINT16 | R | 209718281 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Priority | Over Reactive Power-Alarm Priority | 414180 | UINT32 | R | 209718276 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Delay | Over Reactive Power-Dropout Delay | 414191 | UINT32 | R | 209718280
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Setpoint | Over Reactive Power-Dropout Setpoint | 414189 | F32-4321 | R | 209718279
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Delay | Over Reactive Power-Pickup Delay | 414187 | UINT32 | R | 209718278
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Setpoint | Over Reactive Power-Pickup Setpoint | 414185 | F32-4321 | R | 209718277
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage Alarm | Over THD Voltage Alarm | 411060 | MaskedBool | R | 209720833 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Ack Status | Over THD Voltage-Ack Status | 411079 | MaskedBool | R | 209720834 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Count | Over THD Voltage-Alarm Count | 413550 | UINT16 | R | 209720842
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Enabled | Over THD Voltage-Alarm Enabled | 411041 | MaskedBool | R | 209720835 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Output | Over THD Voltage-Alarm Output | 414553 | UINT16 | R | 209720841 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Priority | Over THD Voltage-Alarm Priority | 414540 | UINT32 | R | 209720836 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Delay | Over THD Voltage-Dropout Delay | 414551 | UINT32 | R | 209720840
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Setpoint | Over THD Voltage-Dropout Setpoint | 414549 | F32-4321 | R | 209720839
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Delay | Over THD Voltage-Pickup Delay | 414547 | UINT32 | R | 209720838
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Setpoint | Over THD Voltage-Pickup Setpoint | 414545 | F32-4321 | R | 209720837
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L Alarm | Over Voltage L-L Alarm | 411059 | MaskedBool | R | 209720321 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Ack Status | Over Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209720322 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Count | Over Voltage L-L-Alarm Count | 413527 | UINT16 | R | 209720330
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Enabled | Over Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209720323 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Output | Over Voltage L-L-Alarm Output | 414093 | UINT16 | R | 209720329 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Priority | Over Voltage L-L-Alarm Priority | 414080 | UINT32 | R | 209720324 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Delay | Over Voltage L-L-Dropout Delay | 414091 | UINT32 | R | 209720328
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Setpoint | Over Voltage L-L-Dropout Setpoint | 414089 | F32-4321 | R | 209720327
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Delay | Over Voltage L-L-Pickup Delay | 414087 | UINT32 | R | 209720326
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Setpoint | Over Voltage L-L-Pickup Setpoint | 414085 | F32-4321 | R | 209720325
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N Alarm | Over Voltage L-N Alarm | 411059 | MaskedBool | R | 209720577 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Ack Status | Over Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209720578 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Count | Over Voltage L-N-Alarm Count | 413529 | UINT16 | R | 209720586
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Enabled | Over Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209720579 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Output | Over Voltage L-N-Alarm Output | 414133 | UINT16 | R | 209720585 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Priority | Over Voltage L-N-Alarm Priority | 414120 | UINT32 | R | 209720580 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Delay | Over Voltage L-N-Dropout Delay | 414131 | UINT32 | R | 209720584
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Setpoint | Over Voltage L-N-Dropout Setpoint | 414129 | F32-4321 | R | 209720583
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Delay | Over Voltage L-N-Pickup Delay | 414127 | UINT32 | R | 209720582
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Setpoint | Over Voltage L-N-Pickup Setpoint | 414125 | F32-4321 | R | 209720581
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance Alarm | Voltage Unbalance Alarm | 411060 | MaskedBool | R | 209721089 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Ack Status | Voltage Unbalance-Ack Status | 411079 | MaskedBool | R | 209721090 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Count | Voltage Unbalance-Alarm Count | 413549 | UINT16 | R | 209721098
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Enabled | Voltage Unbalance-Alarm Enabled | 411041 | MaskedBool | R | 209721091 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Output | Voltage Unbalance-Alarm Output | 414533 | UINT16 | R | 209721097 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Priority | Voltage Unbalance-Alarm Priority | 414520 | UINT32 | R | 209721092 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Delay | Voltage Unbalance-Dropout Delay | 414531 | UINT32 | R | 209721096
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Setpoint | Voltage Unbalance-Dropout Setpoint | 414529 | F32-4321 | R | 209721095
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Delay | Voltage Unbalance-Pickup Delay | 414527 | UINT32 | R | 209721094
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Setpoint | Voltage Unbalance-Pickup Setpoint | 414525 | F32-4321 | R | 209721093
|  | Alarms - Over Under | Phase Loss | Phase Loss Alarm | Phase Loss Alarm | 411060 | MaskedBool | R | 209721345 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Ack Status | Phase Loss-Ack Status | 411079 | MaskedBool | R | 209721346 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Count | Phase Loss-Alarm Count | 413551 | UINT16 | R | 209721354
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Enabled | Phase Loss-Alarm Enabled | 411041 | MaskedBool | R | 209721347 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Output | Phase Loss-Alarm Output | 414573 | UINT16 | R | 209721353 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Priority | Phase Loss-Alarm Priority | 414560 | UINT32 | R | 209721348 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Delay | Phase Loss-Dropout Delay | 414571 | UINT32 | R | 209721352
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Setpoint | Phase Loss-Dropout Setpoint | 414569 | F32-4321 | R | 209721351
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Delay | Phase Loss-Pickup Delay | 414567 | UINT32 | R | 209721350
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Setpoint | Phase Loss-Pickup Setpoint | 414565 | F32-4321 | R | 209721349
|  | Alarms - Over Under | Under Current Phase | Under Current Phase Alarm | Under Current Phase Alarm | 411059 | MaskedBool | R | 209721601 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Ack Status | Under Current Phase-Ack Status | 411078 | MaskedBool | R | 209721602 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Count | Under Current Phase-Alarm Count | 413524 | UINT16 | R | 209721610
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Enabled | Under Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209721603 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Output | Under Current Phase-Alarm Output | 414033 | UINT16 | R | 209721609 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Priority | Under Current Phase-Alarm Priority | 414020 | UINT32 | R | 209721604 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Delay | Under Current Phase-Dropout Delay | 414031 | UINT32 | R | 209721608
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Setpoint | Under Current Phase-Dropout Setpoint | 414029 | F32-4321 | R | 209721607
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Delay | Under Current Phase-Pickup Delay | 414027 | UINT32 | R | 209721606
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Setpoint | Under Current Phase-Pickup Setpoint | 414025 | F32-4321 | R | 209721605
|  | Alarms - Over Under | Under Frequency | Under Frequency Alarm | Under Frequency Alarm | 411060 | MaskedBool | R | 209721857 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Ack Status | Under Frequency-Ack Status | 411079 | MaskedBool | R | 209721858 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Count | Under Frequency-Alarm Count | 413548 | UINT16 | R | 209721866
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Enabled | Under Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209721859 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Output | Under Frequency-Alarm Output | 414513 | UINT16 | R | 209721865 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Priority | Under Frequency-Alarm Priority | 414500 | UINT32 | R | 209721860 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Delay | Under Frequency-Dropout Delay | 414511 | UINT32 | R | 209721864
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Setpoint | Under Frequency-Dropout Setpoint | 414509 | F32-4321 | R | 209721863
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Delay | Under Frequency-Pickup Delay | 414507 | UINT32 | R | 209721862
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Setpoint | Under Frequency-Pickup Setpoint | 414505 | F32-4321 | R | 209721861
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L Alarm | Under Voltage L-L Alarm | 411059 | MaskedBool | R | 209722113 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Ack Status | Under Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209722114 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Count | Under Voltage L-L-Alarm Count | 413528 | UINT16 | R | 209722122
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Enabled | Under Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209722115 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Output | Under Voltage L-L-Alarm Output | 414113 | UINT16 | R | 209722121 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Priority | Under Voltage L-L-Alarm Priority | 414100 | UINT32 | R | 209722116 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Delay | Under Voltage L-L-Dropout Delay | 414111 | UINT32 | R | 209722120
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Setpoint | Under Voltage L-L-Dropout Setpoint | 414109 | F32-4321 | R | 209722119
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Delay | Under Voltage L-L-Pickup Delay | 414107 | UINT32 | R | 209722118
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Setpoint | Under Voltage L-L-Pickup Setpoint | 414105 | F32-4321 | R | 209722117
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N Alarm | Under Voltage L-N Alarm | 411059 | MaskedBool | R | 209722369 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Ack Status | Under Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209722370 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Count | Under Voltage L-N-Alarm Count | 413530 | UINT16 | R | 209722378
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Enabled | Under Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209722371 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Output | Under Voltage L-N-Alarm Output | 414153 | UINT16 | R | 209722377 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Priority | Under Voltage L-N-Alarm Priority | 414140 | UINT32 | R | 209722372 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Delay | Under Voltage L-N-Dropout Delay | 414151 | UINT32 | R | 209722376
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Setpoint | Under Voltage L-N-Dropout Setpoint | 414149 | F32-4321 | R | 209722375
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Delay | Under Voltage L-N-Pickup Delay | 414147 | UINT32 | R | 209722374
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Setpoint | Under Voltage L-N-Pickup Setpoint | 414145 | F32-4321 | R | 209722373
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic Alarm | Meter Diagnostic Alarm | 411069 | MaskedBool | R | 208666625 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Ack Status | Meter Diagnostic-Ack Status | 411088 | MaskedBool | R | 208666626 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Count | Meter Diagnostic-Alarm Count | 413625 | UINT16 | R | 208666630
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Enabled | Meter Diagnostic-Alarm Enabled | 411050 | MaskedBool | R | 208666627 | 0x0004 | 4 |  | AlarmEnabledState
DR1 | 900 | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Output | Meter Diagnostic-Alarm Output | 416222 | UINT16 | R | 208666629 |  |  |  | AlarmDigitalOutputs5330
DR1 | 900 | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Priority | Meter Diagnostic-Alarm Priority | 416220 | UINT32 | R | 208666628 | 0x0018 | 8 |  | AlarmPriority
DR1 | 900 | Alarms - Unary | Meter Power Up | Meter Power Up Alarm | Meter Power Up Alarm | 411069 | MaskedBool | R | 208666881 | 0x0001
DR1 | 900 | Alarms - Unary | Meter Power Up | Meter Power Up-Ack Status | Meter Power Up-Ack Status | 411088 | MaskedBool | R | 208666882 | 0x0001
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Count | Meter Power Up-Alarm Count | 413623 | UINT16 | R | 208666886
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Enabled | Meter Power Up-Alarm Enabled | 411050 | MaskedBool | R | 208666883 | 0x0001 |  |  | AlarmEnabledState
DR2 | 900 | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Output | Meter Power Up-Alarm Output | 416202 | UINT16 | R | 208666885 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Priority | Meter Power Up-Alarm Priority | 416200 | UINT32 | R | 208666884 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Unary | Meter Reset | Meter Reset Alarm | Meter Reset Alarm | 411069 | MaskedBool | R | 208667137 | 0x0002
|  | Alarms - Unary | Meter Reset | Meter Reset-Ack Status | Meter Reset-Ack Status | 411088 | MaskedBool | R | 208667138 | 0x0002
DR2 | 900 | Alarms - Unary | Meter Reset | Meter Reset-Alarm Count | Meter Reset-Alarm Count | 413624 | UINT16 | R | 208667142
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Enabled | Meter Reset-Alarm Enabled | 411050 | MaskedBool | R | 208667139 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Output | Meter Reset-Alarm Output | 416212 | UINT16 | R | 208667141 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Priority | Meter Reset-Alarm Priority | 416210 | UINT32 | R | 208667140 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Unary | Phase Reversal | Phase Reversal Alarm | Phase Reversal Alarm | 411069 | MaskedBool | R | 208667393 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Ack Status | Phase Reversal-Ack Status | 411088 | MaskedBool | R | 208667394 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Count | Phase Reversal-Alarm Count | 413626 | UINT16 | R | 208667398
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Enabled | Phase Reversal-Alarm Enabled | 411050 | MaskedBool | R | 208667395 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Output | Phase Reversal-Alarm Output | 416232 | UINT16 | R | 208667397 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Priority | Phase Reversal-Alarm Priority | 416230 | UINT32 | R | 208667396 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Ack Status | Digital Alarm DI1 Ack Status | 411089 | MaskedBool | R | 206569474 | 0x0001
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Event Counter | Digital Alarm DI1 Event Counter | 413633 | UINT16 | R | 206569480
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Status | Digital Alarm DI1 Status | 411070 | MaskedBool | R | 206569473 | 0x0001
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Digital Output | Digital Alarm DI1 Digital Output | 416306 | UINT16 | R | 206569479 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Dropout Delay | Digital Alarm DI1 Dropout Delay | 416304 | UINT32 | R | 206569478
DR2 | 900 | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Pickup Delay | Digital Alarm DI1 Pickup Delay | 416302 | UINT32 | R | 206569477
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Enabled | Digital Alarm DI1 Enabled | 411051 | MaskedBool | R | 206569475 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Priority | Digital Alarm DI1 Priority | 416300 | UINT32 | R | 206569476 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Digital | Digital Alarm DI1 | Digital Alarm DI1 Setpoint | Digital Alarm DI1 Setpoint | 416300 | UINT32 | R | 206569481 | 0x0F800000 | 8388608
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Ack Status | Digital Alarm DI2 Ack Status | 411089 | MaskedBool | R | 206569730 | 0x0002
DR2 | 900 | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Event Counter | Digital Alarm DI2 Event Counter | 413634 | UINT16 | R | 206569736
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Status | Digital Alarm DI2 Status | 411070 | MaskedBool | R | 206569729 | 0x0002
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Digital Output | Digital Alarm DI2 Digital Output | 416320 | UINT16 | R | 206569735 |  |  |  | AlarmDigitalOutputs5330
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Dropout Delay | Digital Alarm DI2 Dropout Delay | 416318 | UINT32 | R | 206569734
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Pickup Delay | Digital Alarm DI2 Pickup Delay | 416316 | UINT32 | R | 206569733
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Enabled | Digital Alarm DI2 Enabled | 411051 | MaskedBool | R | 206569731 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Priority | Digital Alarm DI2 Priority | 416314 | UINT32 | R | 206569732 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Digital | Digital Alarm DI2 | Digital Alarm DI2 Setpoint | Digital Alarm DI2 Setpoint | 416314 | UINT32 | R | 206569737 | 0x0F800000 | 8388608
|  | Clocks | Clock | CL1 Day | CL1 Day | 401839 | UINT16 | R | 23424 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Hour | CL1 Hour | 401840 | UINT16 | R | 23425 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | 401845 | DateTime3_IEC870_UTC | R | 23421 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Millisecond | CL1 Millisecond | 401843 | UINT16 | R | 23428 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Minute | CL1 Minute | 401841 | UINT16 | R | 23426 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Month | CL1 Month | 401838 | UINT16 | R | 23423 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Second | CL1 Second | 401842 | UINT16 | R | 23427 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | 401845 | DateTime3_IEC870_LOCAL | R | 23420 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Year | CL1 Year | 401837 | UINT16 | R | 23422 |  |  |  |  | 1
|  | Currents | Current | Current A | Current A | 403000 | F32-4321 | R | 164626433 |  |  |  |  | 2
|  | Currents | Current | Current Avg | Current Avg | 403010 | F32-4321 | R | 164626439 |  |  |  |  | 2
|  | Currents | Current | Current B | Current B | 403002 | F32-4321 | R | 164626434 |  |  |  |  | 2
|  | Currents | Current | Current C | Current C | 403004 | F32-4321 | R | 164626435 |  |  |  |  | 2
|  | Currents | Current | Current N | Current N | 403006 | F32-4321 | R | 164626436 |  |  |  |  | 2
|  | Currents | Current | Current G | Current G | 403008 | F32-4321 | R | 164626437
|  | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power | Demand Apparent Power | 403796 | F32-4321 | R | 254143233
|  | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power (KVAD) - Present | Demand Apparent Power (KVAD) - Present | 403798 | F32-4321 | R | 254143234
|  | Demand Readings and History | Demand Apparent Power Total | DT Peak Demand Apparent Power | DT Peak Demand Apparent Power | 403804 | DateTime3_IEC870_UTC | R | 166724630
|  | Demand Readings and History | Demand Apparent Power Total | Peak Demand Apparent Power | Peak Demand Apparent Power | 403802 | F32-4321 | R | 254143236
|  | Demand Readings and History | Demand Apparent Power Total | Predicted KVA Demand | Predicted KVA Demand | 403800 | F32-4321 | R | 254143235
|  | Demand Readings and History | Demand Current Avg | Demand Current Avg | Demand Current Avg | 403876 | F32-4321 | R | 254145025
|  | Demand Readings and History | Demand Current Avg | Demand Current Avg - Present | Demand Current Avg - Present | 403878 | F32-4321 | R | 254145026
|  | Demand Readings and History | Demand Current Avg | DT Peak Demand Current Avg | DT Peak Demand Current Avg | 403884 | DateTime3_IEC870_UTC | R | 166724877
|  | Demand Readings and History | Demand Current Avg | Peak Demand Current Avg | Peak Demand Current Avg | 403882 | F32-4321 | R | 254145028
|  | Demand Readings and History | Demand Current Avg | Predicted Demand Current Avg | Predicted Demand Current Avg | 403880 | F32-4321 | R | 254145027
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method | Current Demand Calculation Method | 403711 | UINT16 | R | 166723841
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method Code | Current Demand Calculation Method Code | 403711 | UINT16 | R | 166723847
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Interval | Current Demand Elapsed Time in Interval | 403714 | UINT16 | R | 166723844
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Subinterval | Current Demand Elapsed Time in Subinterval | 403715 | UINT16 | R | 166723845
|  | Demand Readings and History | Demand Current Calculation | Current Demand Interval | Current Demand Interval | 403712 | UINT16 | R | 166723842
|  | Demand Readings and History | Demand Current Calculation | Current Demand Sub-Interval | Current Demand Sub-Interval | 403713 | UINT16 | R | 166723843
DR1 | 900 | Demand Readings and History | Demand Current Calculation | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | 403716 | DateTime3_IEC870_UTC | R | 166723846
|  | Demand Readings and History | Demand Power Calculation | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | 403706 | DateTime3_IEC870_UTC | R | 166723597
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method | Power Demand Calculation Method | 403701 | UINT16 | R | 166723593
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method Code | Power Demand Calculation Method Code | 403701 | UINT16 | R | 166723596
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Interval | Power Demand Elapsed Time in Interval | 403704 | UINT16 | R | 166723594
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Subinterval | Power Demand Elapsed Time in Subinterval | 403705 | UINT16 | R | 166723595
DR1 | 900 | Demand Readings and History | Demand Power Calculation | Power Demand Interval | Power Demand Interval | 403702 | UINT16 | R | 166723591
|  | Demand Readings and History | Demand Power Calculation | Power Demand Sub-Interval | Power Demand Sub-Interval | 403703 | UINT16 | R | 166723592
|  | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power | Demand Reactive Power | 403780 | F32-4321 | R | 254142209
|  | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power (KVARD) - Present | Demand Reactive Power (KVARD) - Present | 403782 | F32-4321 | R | 254142210
DR1 | 900 | Demand Readings and History | Demand Reactive Power Total | DT Peak Demand Reactive Power | DT Peak Demand Reactive Power | 403788 | DateTime3_IEC870_UTC | R | 166724629
|  | Demand Readings and History | Demand Reactive Power Total | Peak Demand Reactive Power | Peak Demand Reactive Power | 403786 | F32-4321 | R | 254142212
|  | Demand Readings and History | Demand Reactive Power Total | Predicted KVAR Demand | Predicted KVAR Demand | 403784 | F32-4321 | R | 254142211
|  | Demand Readings and History | Demand Real Power Total | Demand Real Power | Demand Real Power | 403764 | F32-4321 | R | 254141185
|  | Demand Readings and History | Demand Real Power Total | Demand Real Power (KWD) - Present | Demand Real Power (KWD) - Present | 403766 | F32-4321 | R | 254141186
|  | Demand Readings and History | Demand Real Power Total | DT Peak Demand Real Power | DT Peak Demand Real Power | 403772 | DateTime3_IEC870_UTC | R | 166724628
|  | Demand Readings and History | Demand Real Power Total | Peak Demand Real Power | Peak Demand Real Power | 403770 | F32-4321 | R | 254141188
|  | Demand Readings and History | Demand Real Power Total | Predicted KW Demand | Predicted KW Demand | 403768 | F32-4321 | R | 254141187
|  | Digital Input Output | Digital Input 1 | DI1 Control Mode | DI1 Control Mode | 407274 | UINT16 | R | 205520898 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 1 | DI1 Count | DI1 Count | 408915 | UINT32 | R | 205520902
|  | Digital Input Output | Digital Input 1 | DI1 Debounce Time | DI1 Debounce Time | 407295 | UINT16 | R | 205520900
|  | Digital Input Output | Digital Input 1 | DI1 Label | DI1 Label | 407275 | ASCII | R | 205520899 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 1 | DI1 On Time | DI1 On Time | 408917 | UINT32 | R | 205520903
|  | Digital Input Output | Digital Input 1 | DI1 Status | DI1 Status | 408906 | MaskedBool | R | 205520901 | 0x0001
|  | Digital Input Output | Digital Input 1 | DI1 Type | DI1 Type | 407273 | UINT16 | R | 205520897 |  |  |  | DIType
|  | Digital Input Output | Digital Input 2 | DI2 Control Mode | DI2 Control Mode | 407298 | UINT16 | R | 205521154 |  |  |  | DIControlModes
|  | Digital Input Output | Digital Input 2 | DI2 Count | DI2 Count | 408919 | UINT32 | R | 205521158
|  | Digital Input Output | Digital Input 2 | DI2 Debounce Time | DI2 Debounce Time | 407319 | UINT16 | R | 205521156
|  | Digital Input Output | Digital Input 2 | DI2 Label | DI2 Label | 407299 | ASCII | R | 205521155 |  |  |  |  | 20
|  | Digital Input Output | Digital Input 2 | DI2 On Time | DI2 On Time | 408921 | UINT32 | R | 205521159
|  | Digital Input Output | Digital Input 2 | DI2 Status | DI2 Status | 408906 | MaskedBool | R | 205521157 | 0x0002
|  | Digital Input Output | Digital Input 2 | DI2 Type | DI2 Type | 407297 | UINT16 | R | 205521153 |  |  |  | DIType
|  | Digital Input Output | Digital Output 1 | DO1 Behavioral Mode | DO1 Behavioral Mode | 409674 | UINT16 | R | 205521927 |  |  |  | DOBehavioralModes
|  | Digital Input Output | Digital Output 1 | DO1 Config On Time | DO1 Config On Time | 409210 | UINT16 | R | 205521923
|  | Digital Input Output | Digital Output 1 | DO1 Control Mode | DO1 Control Mode | 409673 | UINT16 | R | 205521926 |  |  |  | DOControlModes
|  | Digital Input Output | Digital Output 1 | DO1 Count | DO1 Count | 409675 | UINT32 | R | 205521928
|  | Digital Input Output | Digital Output 1 | DO1 Label | DO1 Label | 409188 | ASCII | R | 205521922 |  |  |  |  | 20
|  | Digital Input Output | Digital Output 1 | DO1 On Time | DO1 On Time | 409677 | UINT32 | R | 205521929
|  | Digital Input Output | Digital Output 1 | DO1 Operating Mode | DO1 Operating Mode | 409672 | UINT16 | R | 205521925 |  |  |  | DOOperatingModes
|  | Digital Input Output | Digital Output 1 | DO1 Status | DO1 Status | 409667 | MaskedBool | R | 205521924 | 0x0001
|  | Digital Input Output | Digital Output 1 | DO1 Type | DO1 Type | 409187 | UINT16 | R | 205521921 |  |  |  | DOTypes
|  | Digital Input Output | Digital Output 2 | DO2 Behavioral Mode | DO2 Behavioral Mode | 409682 | UINT16 | R | 205522183 |  |  |  | DOBehavioralModes
|  | Digital Input Output | Digital Output 2 | DO2 Config On Time | DO2 Config On Time | 409234 | UINT16 | R | 205522179
|  | Digital Input Output | Digital Output 2 | DO2 Control Mode | DO2 Control Mode | 409681 | UINT16 | R | 205522182 |  |  |  | DOControlModes
|  | Digital Input Output | Digital Output 2 | DO2 Count | DO2 Count | 409683 | UINT32 | R | 205522184
|  | Digital Input Output | Digital Output 2 | DO2 Label | DO2 Label | 409212 | ASCII | R | 205522178 |  |  |  |  | 20
|  | Digital Input Output | Digital Output 2 | DO2 On Time | DO2 On Time | 409685 | UINT32 | R | 205522185
|  | Digital Input Output | Digital Output 2 | DO2 Operating Mode | DO2 Operating Mode | 409680 | UINT16 | R | 205522181 |  |  |  | DOOperatingModes
|  | Digital Input Output | Digital Output 2 | DO2 Status | DO2 Status | 409667 | MaskedBool | R | 205522180 | 0x0002
|  | Digital Input Output | Digital Output 2 | DO2 Type | DO2 Type | 409211 | UINT16 | R | 205522177 |  |  |  | DOTypes
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Digital Output Association | EPO1 Digital Output Association | 402131 | UINT16 | R | 205522439 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Energy Channel | EPO1 Energy Channel | 402130 | UINT16 | R | 205522438 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Pulse Weight | EPO1 Pulse Weight | 402132 | UINT32 | R | 205522437
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Digital Output Association | EPO2 Digital Output Association | 402135 | UINT16 | R | 205522690 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Energy Channel | EPO2 Energy Channel | 402134 | UINT16 | R | 205522689 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Pulse Weight | EPO2 Pulse Weight | 402136 | UINT32 | R | 205522691
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Energy Channel | EPO3 Energy Channel | 402138 | UINT16 | R | 205521409 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Digital Output Association | EPO3 Digital Output Association | 402139 | UINT16 | R | 205521410 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 3 | EPO3 Pulse Weight | EPO3 Pulse Weight | 402140 | UINT32 | R | 205521411
|  | Power Meters | Power Meter | PM1 CT Count | PM1 CT Count | 402029 | UINT16 | R | 65555 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Location | PM1 CT Location | 402034 | UINT16 | R | 65554 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Current | PM1 Nominal Current | 402020 | F32-4321 | R | 65544 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Frequency | PM1 Nominal Frequency | 402017 | UINT16 | R | 65542
|  | Power Meters | Power Meter | PM1 Nominal Phase Rotation | PM1 Nominal Phase Rotation | 402024 | UINT16 | R | 65547 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Power Factor | PM1 Nominal Power Factor | 402022 | PF32 | R | 65545 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Power Factor Load Direction | PM1 Nominal Power Factor Load Direction | 402022 | F32-4321 | R | 65548 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Voltage | PM1 Nominal Voltage | 402018 | F32-4321 | R | 65543 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Connection Type | PM1 VT Connection Type | 402036 | UINT16 | R | 65541 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Count | PM1 VT Count | 402025 | UINT16 | R | 65552 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Location | PM1 VT Location | 402035 | UINT16 | R | 65553 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Volts Mode | PM1 Volts Mode | 402016 | UINT16 | R | 30720 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Primary | PM1 CT Primary | 402030 | UINT16 | R | 65539 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Secondary | PM1 CT Secondary | 402031 | UINT16 | R | 65540 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Primary | PM1 VT Primary | 402026 | F32-4321 | R | 65537 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Secondary | PM1 VT Secondary | 402028 | UINT16 | R | 65538 |  |  |  |  | 1
|  | Diagnostics | Meter | Calibration Error | Calibration Error | 420007 | MaskedBool | R | 157286669 | 0x0010
|  | Diagnostics | Meter | Cause of Last Meter Reset | Cause of Last Meter Reset | 401836 | UINT16 | R | 157286668
|  | Diagnostics | Meter | Clipping Detected | Clipping Detected | 420007 | MaskedBool | R | 157286662 | 0x0020
|  | Diagnostics | Meter | Control Power Outage Counter | Control Power Outage Counter | 401829 | UINT16 | R | 157286670
|  | Diagnostics | Meter | DT Last Control Power Outage | DT Last Control Power Outage | 401830 | DateTime3_IEC870_UTC | R | 157286671
|  | Diagnostics | Meter | DT Last Unit Restart | DT Last Unit Restart | 401824 | DateTime3_IEC870_UTC | R | 157286664
|  | Diagnostics | Meter | Meter Error Detected | Meter Error Detected | 420007 | MaskedBool | R | 157286657 | 0x0001
|  | Diagnostics | Meter | Metering System Restart Counter | Metering System Restart Counter | 401828 | UINT16 | R | 157286665
|  | Diagnostics | Meter | NVRAM Error | NVRAM Error | 420007 | MaskedBool | R | 157286672 | 0x0004
|  | Diagnostics | Meter | Over Run Energy Pulse Output | Over Run Energy Pulse Output | 420007 | MaskedBool | R | 157286663 | 0x0040
|  | Diagnostics | Meter | RAM Error | RAM Error | 420007 | MaskedBool | R | 157286673 | 0x0002
|  | Diagnostics | Meter | RTC Error | RTC Error | 420007 | MaskedBool | R | 157286674 | 0x0008
|  | Energies | Apparent Energy | Apparent Energy | Apparent Energy | 403244 | S64-87-21 | R | 256238595 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Delivered-Received | Apparent Energy Delivered-Received | 403248 | S64-87-21 | R | 256238596 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Into the Load | Apparent Energy Into the Load | 403236 | S64-87-21 | R | 256238593 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Out of the Load | Apparent Energy Out of the Load | 403240 | S64-87-21 | R | 256238594 |  | 1000
|  | Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | 403200 | DateTime3_IEC870_UTC | R | 169869321
|  | Energies | Reactive Energy | Reactive Energy Absolute | Reactive Energy Absolute | 403228 | S64-87-21 | R | 256238339 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Into the Load | Reactive Energy Into the Load | 403220 | S64-87-21 | R | 256238337 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Out of the Load | Reactive Energy Out of the Load | 403224 | S64-87-21 | R | 256238338 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Signed | Reactive Energy Signed | 403232 | S64-87-21 | R | 256238340 |  | 1000
|  | Energies | Real Energy | Real Energy Absolute | Real Energy Absolute | 403212 | S64-87-21 | R | 256238083 |  | 1000
|  | Energies | Real Energy | Real Energy Into the Load | Real Energy Into the Load | 403204 | S64-87-21 | R | 256238081 |  | 1000
|  | Energies | Real Energy | Real Energy Out of the Load | Real Energy Out of the Load | 403208 | S64-87-21 | R | 256238082 |  | 1000
|  | Energies | Real Energy | Real Energy Signed | Real Energy Signed | 403216 | S64-87-21 | R | 256238084 |  | 1000
|  | Maximum Readings | Max Current | Max Current A | Max Current A | 427694 | F32-4321 | R | 177209601 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current Avg | Max Current Avg | 427704 | F32-4321 | R | 177209607 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current B | Max Current B | 427696 | F32-4321 | R | 177209602 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current C | Max Current C | 427698 | F32-4321 | R | 177209604 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current N | Max Current N | 427700 | F32-4321 | R | 177209603 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current G | Max Current G | 427702 | F32-4321 | R | 177209605
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance A | Max Current Unbalance A | 427706 | F32-4321 | R | 177209857 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance B | Max Current Unbalance B | 427708 | F32-4321 | R | 177209858 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance C | Max Current Unbalance C | 427710 | F32-4321 | R | 177209859 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance Worst | Max Current Unbalance Worst | 427712 | F32-4321 | R | 177209860 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A | Max Displacement Power Factor A | 427790 | PF32 | R | 177210113 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A Load Direction | Max Displacement Power Factor A Load Direction | 427790 | F32-4321 | R | 177210114 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B | Max Displacement Power Factor B | 427792 | PF32 | R | 177210369 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B Load Direction | Max Displacement Power Factor B Load Direction | 427792 | F32-4321 | R | 177210370 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C | Max Displacement Power Factor C | 427794 | PF32 | R | 177210625 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C Load Direction | Max Displacement Power Factor C Load Direction | 427794 | F32-4321 | R | 177210626 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total | Max Displacement Power Factor Total | 427796 | PF32 | R | 177211137 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total Load Direction | Max Displacement Power Factor Total Load Direction | 427796 | F32-4321 | R | 177211138 |  |  |  |  | 2
|  | Maximum Readings | Max Frequency | Max Frequency | Max Frequency | 428092 | F32-4321 | R | 177210881 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power A | Max Apparent Power A | 427764 | F32-4321 | R | 177213449 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power B | Max Apparent Power B | 427766 | F32-4321 | R | 177213450 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power C | Max Apparent Power C | 427768 | F32-4321 | R | 177213451 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power Total | Max Apparent Power Total | 427770 | F32-4321 | R | 177213452 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power A | Max Reactive Power A | 427756 | F32-4321 | R | 177213445 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power B | Max Reactive Power B | 427758 | F32-4321 | R | 177213446 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power C | Max Reactive Power C | 427760 | F32-4321 | R | 177213447 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power Total | Max Reactive Power Total | 427762 | F32-4321 | R | 177213448 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power A | Max Real Power A | 427748 | F32-4321 | R | 177213441 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power B | Max Real Power B | 427750 | F32-4321 | R | 177213442 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power C | Max Real Power C | 427752 | F32-4321 | R | 177213443 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power Total | Max Real Power Total | 427754 | F32-4321 | R | 177213444 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A | Max Power Factor A | 427782 | PF32 | R | 177211393 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A Load Direction | Max Power Factor A Load Direction | 427782 | F32-4321 | R | 177211394 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B | Max Power Factor B | 427784 | PF32 | R | 177211649 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B Load Direction | Max Power Factor B Load Direction | 427784 | F32-4321 | R | 177211650 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C | Max Power Factor C | 427786 | PF32 | R | 177211905 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C Load Direction | Max Power Factor C Load Direction | 427786 | F32-4321 | R | 177211906 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total | Max Power Factor Total | 427788 | PF32 | R | 177212161 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total Load Direction | Max Power Factor Total Load Direction | 427788 | F32-4321 | R | 177212162 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current A | Max THD Current A | 427814 | F32-4321 | R | 177214466 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current B | Max THD Current B | 427816 | F32-4321 | R | 177214467 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current C | Max THD Current C | 427818 | F32-4321 | R | 177214468 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current N | Max THD Current N | 427820 | F32-4321 | R | 177214469 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current G | Max THD Current G | 427822 | F32-4321 | R | 177214465
|  | Maximum Readings | Max thd Current | Max thd_Current A | Max thd_Current A | 427824 | F32-4321 | R | 177214209 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current B | Max thd_Current B | 427826 | F32-4321 | R | 177214210 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current C | Max thd_Current C | 427828 | F32-4321 | R | 177214211 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current N | Max thd_Current N | 427830 | F32-4321 | R | 177214212 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current G | Max thd_Current G | 427832 | F32-4321 | R | 177214213
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-B | Max THD Voltage A-B | 427836 | F32-4321 | R | 177214977 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-N | Max THD Voltage A-N | 427844 | F32-4321 | R | 177214984 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-C | Max THD Voltage B-C | 427838 | F32-4321 | R | 177214978 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-N | Max THD Voltage B-N | 427846 | F32-4321 | R | 177214985 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-A | Max THD Voltage C-A | 427840 | F32-4321 | R | 177214979 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-N | Max THD Voltage C-N | 427848 | F32-4321 | R | 177214986 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-L | Max THD Voltage L-L | 427842 | F32-4321 | R | 177214980 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-N | Max THD Voltage L-N | 427852 | F32-4321 | R | 177214987 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-B | Max thd_Voltage A-B | 427854 | F32-4321 | R | 177214721 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-N | Max thd_Voltage A-N | 427862 | F32-4321 | R | 177214724 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-C | Max thd_Voltage B-C | 427856 | F32-4321 | R | 177214722 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-N | Max thd_Voltage B-N | 427864 | F32-4321 | R | 177214725 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-A | Max thd_Voltage C-A | 427858 | F32-4321 | R | 177214723 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-N | Max thd_Voltage C-N | 427866 | F32-4321 | R | 177214726 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-L | Max thd_Voltage L-L | 427860 | F32-4321 | R | 177214727 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-N | Max thd_Voltage L-N | 427870 | F32-4321 | R | 177214728 |  |  |  |  | 2
|  | Maximum Readings | Max Total Demand Distortion | Max Total Demand Distortion | Max Total Demand Distortion | 427834 | F32-4321 | R | 177209345 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-B | Max Voltage A-B | 427714 | F32-4321 | R | 177215489 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-N | Max Voltage A-N | 427722 | F32-4321 | R | 177215497 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-C | Max Voltage B-C | 427716 | F32-4321 | R | 177215490 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-N | Max Voltage B-N | 427724 | F32-4321 | R | 177215498 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-A | Max Voltage C-A | 427718 | F32-4321 | R | 177215491 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-N | Max Voltage C-N | 427726 | F32-4321 | R | 177215499 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-L Avg | Max Voltage L-L Avg | 427720 | F32-4321 | R | 177215493 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-N Avg | Max Voltage L-N Avg | 427730 | F32-4321 | R | 177215501 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-B | Max Voltage Unbalance A-B | 427732 | F32-4321 | R | 177215745 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-N | Max Voltage Unbalance A-N | 427740 | F32-4321 | R | 177215753 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-C | Max Voltage Unbalance B-C | 427734 | F32-4321 | R | 177215746 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-N | Max Voltage Unbalance B-N | 427742 | F32-4321 | R | 177215754 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-A | Max Voltage Unbalance C-A | 427736 | F32-4321 | R | 177215747 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-N | Max Voltage Unbalance C-N | 427744 | F32-4321 | R | 177215755 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-L Worst | Max Voltage Unbalance L-L Worst | 427738 | F32-4321 | R | 177215748 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-N Worst | Max Voltage Unbalance L-N Worst | 427746 | F32-4321 | R | 177215756 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current A | Min Current A | 427218 | F32-4321 | R | 178258178 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current Avg | Min Current Avg | 427228 | F32-4321 | R | 178258183 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current B | Min Current B | 427220 | F32-4321 | R | 178258179 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current C | Min Current C | 427222 | F32-4321 | R | 178258180 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current N | Min Current N | 427224 | F32-4321 | R | 178258181 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current G | Min Current G | 427226 | F32-4321 | R | 178258177 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance A | Min Current Unbalance A | 427230 | F32-4321 | R | 178258433 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance B | Min Current Unbalance B | 427232 | F32-4321 | R | 178258434 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance C | Min Current Unbalance C | 427234 | F32-4321 | R | 178258435 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance Worst | Min Current Unbalance Worst | 427236 | F32-4321 | R | 178258436 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A | Min Displacement Power Factor A | 427314 | PF32 | R | 178258689 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A Load Direction | Min Displacement Power Factor A Load Direction | 427314 | F32-4321 | R | 178258690 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B | Min Displacement Power Factor B | 427316 | PF32 | R | 178258945 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B Load Direction | Min Displacement Power Factor B Load Direction | 427316 | F32-4321 | R | 178258946 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C | Min Displacement Power Factor C | 427318 | PF32 | R | 178259201 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C Load Direction | Min Displacement Power Factor C Load Direction | 427318 | F32-4321 | R | 178259202 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total | Min Displacement Power Factor Total | 427320 | PF32 | R | 178259713 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total Load Direction | Min Displacement Power Factor Total Load Direction | 427320 | F32-4321 | R | 178259714 |  |  |  |  | 2
DR1 | 900 | Minimum Readings | Min Frequency | Min Frequency | Min Frequency | 427616 | F32-4321 | R | 178259457 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power A | Min Apparent Power A | 427288 | F32-4321 | R | 178262017 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power B | Min Apparent Power B | 427290 | F32-4321 | R | 178262018 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power C | Min Apparent Power C | 427292 | F32-4321 | R | 178262019 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power Total | Min Apparent Power Total | 427294 | F32-4321 | R | 178262020 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power A | Min Reactive Power A | 427280 | F32-4321 | R | 178262022 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power B | Min Reactive Power B | 427282 | F32-4321 | R | 178262023 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power C | Min Reactive Power C | 427284 | F32-4321 | R | 178262024 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power Total | Min Reactive Power Total | 427286 | F32-4321 | R | 178262025 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power A | Min Real Power A | 427272 | F32-4321 | R | 178262027 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power B | Min Real Power B | 427274 | F32-4321 | R | 178262028 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power C | Min Real Power C | 427276 | F32-4321 | R | 178262029 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power Total | Min Real Power Total | 427278 | F32-4321 | R | 178262030 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A | Min Power Factor A | 427306 | PF32 | R | 178259969 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A Load Direction | Min Power Factor A Load Direction | 427306 | F32-4321 | R | 178259970 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B | Min Power Factor B | 427308 | PF32 | R | 178260225 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B Load Direction | Min Power Factor B Load Direction | 427308 | F32-4321 | R | 178260226 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C | Min Power Factor C | 427310 | PF32 | R | 178260481 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C Load Direction | Min Power Factor C Load Direction | 427310 | F32-4321 | R | 178260482 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total | Min Power Factor Total | 427312 | PF32 | R | 178260737 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total Load Direction | Min Power Factor Total Load Direction | 427312 | F32-4321 | R | 178260738 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current A | Min THD Current A | 427338 | F32-4321 | R | 178263042 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current B | Min THD Current B | 427340 | F32-4321 | R | 178263043 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current C | Min THD Current C | 427342 | F32-4321 | R | 178263044 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current N | Min THD Current N | 427344 | F32-4321 | R | 178263045 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current G | Min THD Current G | 427346 | F32-4321 | R | 178263041
|  | Minimum Readings | Min thd Current | Min thd_Current A | Min thd_Current A | 427348 | F32-4321 | R | 178262785 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current B | Min thd_Current B | 427350 | F32-4321 | R | 178262786 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current C | Min thd_Current C | 427352 | F32-4321 | R | 178262787 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current N | Min thd_Current N | 427354 | F32-4321 | R | 178262788 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current G | Min thd_Current G | 427356 | F32-4321 | R | 178262789
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-B | Min THD Voltage A-B | 427360 | F32-4321 | R | 178263553 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-N | Min THD Voltage A-N | 427368 | F32-4321 | R | 178263556 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-C | Min THD Voltage B-C | 427362 | F32-4321 | R | 178263554 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-N | Min THD Voltage B-N | 427370 | F32-4321 | R | 178263557 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-A | Min THD Voltage C-A | 427364 | F32-4321 | R | 178263555 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-N | Min THD Voltage C-N | 427372 | F32-4321 | R | 178263558 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-L | Min THD Voltage L-L | 427366 | F32-4321 | R | 178263559 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-N | Min THD Voltage L-N | 427376 | F32-4321 | R | 178263563 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-B | Min thd_Voltage A-B | 427378 | F32-4321 | R | 178263297 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-N | Min thd_Voltage A-N | 427386 | F32-4321 | R | 178263300 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-C | Min thd_Voltage B-C | 427380 | F32-4321 | R | 178263298 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-N | Min thd_Voltage B-N | 427388 | F32-4321 | R | 178263301 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-A | Min thd_Voltage C-A | 427382 | F32-4321 | R | 178263299 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-N | Min thd_Voltage C-N | 427390 | F32-4321 | R | 178263302 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-L | Min thd_Voltage L-L | 427384 | F32-4321 | R | 178263303 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-N | Min thd_Voltage L-N | 427394 | F32-4321 | R | 178263304 |  |  |  |  | 2
|  | Minimum Readings | Min Total Demand Distortion | Min Total Demand Distortion | Min Total Demand Distortion | 427358 | F32-4321 | R | 178257921 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-B | Min Voltage A-B | 427238 | F32-4321 | R | 178264065 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-N | Min Voltage A-N | 427246 | F32-4321 | R | 178264068 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-C | Min Voltage B-C | 427240 | F32-4321 | R | 178264066 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-N | Min Voltage B-N | 427248 | F32-4321 | R | 178264069 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-A | Min Voltage C-A | 427242 | F32-4321 | R | 178264067 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-N | Min Voltage C-N | 427250 | F32-4321 | R | 178264070 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-L Avg | Min Voltage L-L Avg | 427244 | F32-4321 | R | 178264072 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-N Avg | Min Voltage L-N Avg | 427254 | F32-4321 | R | 178264077 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-B | Min Voltage Unbalance A-B | 427256 | F32-4321 | R | 178264321 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-N | Min Voltage Unbalance A-N | 427264 | F32-4321 | R | 178264324 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-C | Min Voltage Unbalance B-C | 427258 | F32-4321 | R | 178264322 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-N | Min Voltage Unbalance B-N | 427266 | F32-4321 | R | 178264325 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-A | Min Voltage Unbalance C-A | 427260 | F32-4321 | R | 178264323 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-N | Min Voltage Unbalance C-N | 427268 | F32-4321 | R | 178264326 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-L Worst | Min Voltage Unbalance L-L Worst | 427262 | F32-4321 | R | 178264331 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-N Worst | Min Voltage Unbalance L-N Worst | 427270 | F32-4321 | R | 178264336 |  |  |  |  | 2
|  | Miscellaneous | Active Load Timer | Active Load Timer | Active Load Timer | 402002 | UINT32 | R | 179307265
|  | Miscellaneous | Active Load Timer | Active Load Timer Setpoint | Active Load Timer Setpoint | 402050 | F32-4321 | R | 179307266
|  | Miscellaneous | Cycle Count | Cycle Count | Cycle Count | 402006 | UINT32 | R | 179307521
|  | Miscellaneous | DT Last Reset MinMax | DT Last Reset MinMax | DT Last Reset MinMax | 427214 | DateTime3_IEC870_UTC | R | 179308289
|  | Miscellaneous | Frequency | Frequency | Frequency | 403110 | F32-4321 | R | 179307009
|  | Miscellaneous | LED Mode | LED Mode | LED Mode | 402126 | UINT16 | R | 179306753
|  | Miscellaneous | Meter ON Duration | Meter ON Duration | Meter ON Duration | 402004 | UINT32 | R | 179308545 |  | 3600
|  | Miscellaneous | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | 402048 | F32-4321 | R | 179308033
|  | Miscellaneous | Revenue Security Status | Revenue Security Status | Revenue Security Status | 401921 | UINT16 | R | 179307777
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A | Displacement Power Factor A | 403086 | PF32 | R | 186647553
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A Load Direction | Displacement Power Factor A Load Direction | 403086 | F32-4321 | R | 186647554
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B | Displacement Power Factor B | 403088 | PF32 | R | 186647809
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B Load Direction | Displacement Power Factor B Load Direction | 403088 | F32-4321 | R | 186647810
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C | Displacement Power Factor C | 403090 | PF32 | R | 186648065
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C Load Direction | Displacement Power Factor C Load Direction | 403090 | F32-4321 | R | 186648066
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total | Displacement Power Factor Total | 403092 | PF32 | R | 186648321
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total Load Direction | Displacement Power Factor Total Load Direction | 403092 | F32-4321 | R | 186648322
|  | Power Factors | Power Factor A | Power Factor A | Power Factor A | 403078 | PF32 | R | 186646529
|  | Power Factors | Power Factor A | Power Factor A Load Direction | Power Factor A Load Direction | 403078 | F32-4321 | R | 186646530
|  | Power Factors | Power Factor B | Power Factor B | Power Factor B | 403080 | PF32 | R | 186646785
|  | Power Factors | Power Factor B | Power Factor B Load Direction | Power Factor B Load Direction | 403080 | F32-4321 | R | 186646786
|  | Power Factors | Power Factor C | Power Factor C | Power Factor C | 403082 | PF32 | R | 186647041
|  | Power Factors | Power Factor C | Power Factor C Load Direction | Power Factor C Load Direction | 403082 | F32-4321 | R | 186647042
|  | Power Factors | Power Factor Total | Power Factor Total | Power Factor Total | 403084 | PF32 | R | 186647297
|  | Power Factors | Power Factor Total | Power Factor Total Load Direction | Power Factor Total Load Direction | 403084 | F32-4321 | R | 186647298
|  | Power Quality | THD Current | THD Current A | THD Current A | 421300 | F32-4321 | R | 187696897 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current B | THD Current B | 421302 | F32-4321 | R | 187696898 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current C | THD Current C | 421304 | F32-4321 | R | 187696899 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current N | THD Current N | 421306 | F32-4321 | R | 187696900 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current G | THD Current G | 421308 | F32-4321 | R | 187696901
|  | Power Quality | THD Voltage | THD Voltage A-B | THD Voltage A-B | 421322 | F32-4321 | R | 187697153 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage A-N | THD Voltage A-N | 421330 | F32-4321 | R | 187697156 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-C | THD Voltage B-C | 421324 | F32-4321 | R | 187697154 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-N | THD Voltage B-N | 421332 | F32-4321 | R | 187697157 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-A | THD Voltage C-A | 421326 | F32-4321 | R | 187697155 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-N | THD Voltage C-N | 421334 | F32-4321 | R | 187697158 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-L | THD Voltage L-L | 421328 | F32-4321 | R | 187697159 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-N | THD Voltage L-N | 421338 | F32-4321 | R | 187697160 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current A | thd_Current A | 421310 | F32-4321 | R | 187697665 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current B | thd_Current B | 421312 | F32-4321 | R | 187697666 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current C | thd_Current C | 421314 | F32-4321 | R | 187697667 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current N | thd_Current N | 421316 | F32-4321 | R | 187697668 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current G | thd_Current G | 421318 | F32-4321 | R | 187697669
|  | Power Quality | thd_Voltage | thd_Voltage A-B | thd_Voltage A-B | 421340 | F32-4321 | R | 187697921 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage A-N | thd_Voltage A-N | 421348 | F32-4321 | R | 187697924 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-C | thd_Voltage B-C | 421342 | F32-4321 | R | 187697922 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-N | thd_Voltage B-N | 421350 | F32-4321 | R | 187697925 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-A | thd_Voltage C-A | 421344 | F32-4321 | R | 187697923 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-N | thd_Voltage C-N | 421352 | F32-4321 | R | 187697926 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-L | thd_Voltage L-L | 421346 | F32-4321 | R | 187697927 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-N | thd_Voltage L-N | 421356 | F32-4321 | R | 187697928 |  |  |  |  | 2
|  | Power Quality | Total Demand Distortion | Total Demand Distortion | Total Demand Distortion | 421320 | F32-4321 | R | 187698177 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power A | Apparent Power A | 403070 | F32-4321 | R | 190840841 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power B | Apparent Power B | 403072 | F32-4321 | R | 190840842 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power C | Apparent Power C | 403074 | F32-4321 | R | 190840843 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power Total | Apparent Power Total | 403076 | F32-4321 | R | 190840844 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power A | Reactive Power A | 403062 | F32-4321 | R | 190840837 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power B | Reactive Power B | 403064 | F32-4321 | R | 190840838 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power C | Reactive Power C | 403066 | F32-4321 | R | 190840839 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power Total | Reactive Power Total | 403068 | F32-4321 | R | 190840840 |  |  |  |  | 2
|  | Powers | Real Power | Real Power A | Real Power A | 403054 | F32-4321 | R | 190840833 |  |  |  |  | 2
|  | Powers | Real Power | Real Power B | Real Power B | 403056 | F32-4321 | R | 190840834 |  |  |  |  | 2
|  | Powers | Real Power | Real Power C | Real Power C | 403058 | F32-4321 | R | 190840835 |  |  |  |  | 2
|  | Powers | Real Power | Real Power Total | Real Power Total | 403060 | F32-4321 | R | 190840836 |  |  |  |  | 2
|  | Resets and Triggers | Digital Inputs | DI1 Counter Reset | DI1 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238593
|  | Resets and Triggers | Digital Inputs | DI2 Counter Reset | DI2 Counter Reset | 405250 | U16-21-ARRAY | CW | 156238595
|  | Resets and Triggers | Resets | Accumulated Energy Reset | Accumulated Energy Reset | 405250 | U16-21-ARRAY | CW | 156237828
|  | Resets and Triggers | Resets | All Demand Interval Reset | All Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237839
|  | Resets and Triggers | Resets | Current Demand Interval Reset | Current Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237829
|  | Resets and Triggers | Resets | Current Demand Reset | Current Demand Reset | 405250 | U16-21-ARRAY | CW | 156237837
|  | Resets and Triggers | Resets | Min Max Reset | Min Max Reset | 405250 | U16-21-ARRAY | CW | 156237840
|  | Resets and Triggers | Resets | Peak Demand Current Reset | Peak Demand Current Reset | 405250 | U16-21-ARRAY | CW | 156237825
|  | Resets and Triggers | Resets | Power Demand Interval Reset | Power Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237830
|  | Resets and Triggers | Resets | Reset Active Load Timer | Reset Active Load Timer | 405250 | U16-21-ARRAY | CW | 156237831
|  | Resets and Triggers | Resets | Time of Use Reset | Time of Use Reset | 405250 | U16-21-ARRAY | CW | 156237841
|  | Spectral Components | Current A Harmonics | H1 Current A Magnitude | H1 Current A Magnitude | 424428 | F32-4321 | R | 257287937
|  | Spectral Components | Current A Harmonics | H2 Current A Magnitude | H2 Current A Magnitude | 424434 | F32-4321 | R | 257287939
|  | Spectral Components | Current A Harmonics | H3 Current A Magnitude | H3 Current A Magnitude | 424440 | F32-4321 | R | 257287941
|  | Spectral Components | Current A Harmonics | H4 Current A Magnitude | H4 Current A Magnitude | 424446 | F32-4321 | R | 257287943
|  | Spectral Components | Current A Harmonics | H5 Current A Magnitude | H5 Current A Magnitude | 424452 | F32-4321 | R | 257287945
|  | Spectral Components | Current A Harmonics | H6 Current A Magnitude | H6 Current A Magnitude | 424458 | F32-4321 | R | 257287947
|  | Spectral Components | Current A Harmonics | H7 Current A Magnitude | H7 Current A Magnitude | 424464 | F32-4321 | R | 257287949
|  | Spectral Components | Current A Harmonics | H8 Current A Magnitude | H8 Current A Magnitude | 424470 | F32-4321 | R | 257287951
|  | Spectral Components | Current A Harmonics | H9 Current A Magnitude | H9 Current A Magnitude | 424476 | F32-4321 | R | 257287953
|  | Spectral Components | Current A Harmonics | H10 Current A Magnitude | H10 Current A Magnitude | 424482 | F32-4321 | R | 257287955
|  | Spectral Components | Current A Harmonics | H11 Current A Magnitude | H11 Current A Magnitude | 424488 | F32-4321 | R | 257287957
|  | Spectral Components | Current A Harmonics | H12 Current A Magnitude | H12 Current A Magnitude | 424494 | F32-4321 | R | 257287959
|  | Spectral Components | Current A Harmonics | H13 Current A Magnitude | H13 Current A Magnitude | 424500 | F32-4321 | R | 257287961
|  | Spectral Components | Current A Harmonics | H14 Current A Magnitude | H14 Current A Magnitude | 424506 | F32-4321 | R | 257287963
|  | Spectral Components | Current A Harmonics | H15 Current A Magnitude | H15 Current A Magnitude | 424512 | F32-4321 | R | 257287965
|  | Spectral Components | Current A Harmonics | H16 Current A Magnitude | H16 Current A Magnitude | 424518 | F32-4321 | R | 257287967
DR1 | 900 | Spectral Components | Current A Harmonics | H17 Current A Magnitude | H17 Current A Magnitude | 424524 | F32-4321 | R | 257287969
DR1 | 900 | Spectral Components | Current A Harmonics | H18 Current A Magnitude | H18 Current A Magnitude | 424530 | F32-4321 | R | 257287971
DR1 | 900 | Spectral Components | Current A Harmonics | H19 Current A Magnitude | H19 Current A Magnitude | 424536 | F32-4321 | R | 257287973
DR1 | 900 | Spectral Components | Current A Harmonics | H20 Current A Magnitude | H20 Current A Magnitude | 424542 | F32-4321 | R | 257287975
DR1 | 900 | Spectral Components | Current A Harmonics | H21 Current A Magnitude | H21 Current A Magnitude | 424548 | F32-4321 | R | 257287977
DR1 | 900 | Spectral Components | Current A Harmonics | H22 Current A Magnitude | H22 Current A Magnitude | 424554 | F32-4321 | R | 257287979
DR1 | 900 | Spectral Components | Current A Harmonics | H23 Current A Magnitude | H23 Current A Magnitude | 424560 | F32-4321 | R | 257287981
DR1 | 900 | Spectral Components | Current A Harmonics | H24 Current A Magnitude | H24 Current A Magnitude | 424566 | F32-4321 | R | 257287983
|  | Spectral Components | Current A Harmonics | H25 Current A Magnitude | H25 Current A Magnitude | 424572 | F32-4321 | R | 257287985
|  | Spectral Components | Current A Harmonics | H26 Current A Magnitude | H26 Current A Magnitude | 424578 | F32-4321 | R | 257287987
|  | Spectral Components | Current A Harmonics | H27 Current A Magnitude | H27 Current A Magnitude | 424584 | F32-4321 | R | 257287989
|  | Spectral Components | Current A Harmonics | H28 Current A Magnitude | H28 Current A Magnitude | 424590 | F32-4321 | R | 257287991
|  | Spectral Components | Current A Harmonics | H29 Current A Magnitude | H29 Current A Magnitude | 424596 | F32-4321 | R | 257287993
|  | Spectral Components | Current A Harmonics | H30 Current A Magnitude | H30 Current A Magnitude | 424602 | F32-4321 | R | 257287995
|  | Spectral Components | Current A Harmonics | H31 Current A Magnitude | H31 Current A Magnitude | 424608 | F32-4321 | R | 257287997
|  | Spectral Components | Current B Harmonics | H1 Current B Magnitude | H1 Current B Magnitude | 424816 | F32-4321 | R | 257288193
|  | Spectral Components | Current B Harmonics | H2 Current B Magnitude | H2 Current B Magnitude | 424822 | F32-4321 | R | 257288195
|  | Spectral Components | Current B Harmonics | H3 Current B Magnitude | H3 Current B Magnitude | 424828 | F32-4321 | R | 257288197
|  | Spectral Components | Current B Harmonics | H4 Current B Magnitude | H4 Current B Magnitude | 424834 | F32-4321 | R | 257288199
|  | Spectral Components | Current B Harmonics | H5 Current B Magnitude | H5 Current B Magnitude | 424840 | F32-4321 | R | 257288201
|  | Spectral Components | Current B Harmonics | H6 Current B Magnitude | H6 Current B Magnitude | 424846 | F32-4321 | R | 257288203
|  | Spectral Components | Current B Harmonics | H7 Current B Magnitude | H7 Current B Magnitude | 424852 | F32-4321 | R | 257288205
|  | Spectral Components | Current B Harmonics | H8 Current B Magnitude | H8 Current B Magnitude | 424858 | F32-4321 | R | 257288207
|  | Spectral Components | Current B Harmonics | H9 Current B Magnitude | H9 Current B Magnitude | 424864 | F32-4321 | R | 257288209
|  | Spectral Components | Current B Harmonics | H10 Current B Magnitude | H10 Current B Magnitude | 424870 | F32-4321 | R | 257288211
|  | Spectral Components | Current B Harmonics | H11 Current B Magnitude | H11 Current B Magnitude | 424876 | F32-4321 | R | 257288213
|  | Spectral Components | Current B Harmonics | H12 Current B Magnitude | H12 Current B Magnitude | 424882 | F32-4321 | R | 257288215
|  | Spectral Components | Current B Harmonics | H13 Current B Magnitude | H13 Current B Magnitude | 424888 | F32-4321 | R | 257288217
|  | Spectral Components | Current B Harmonics | H14 Current B Magnitude | H14 Current B Magnitude | 424894 | F32-4321 | R | 257288219
|  | Spectral Components | Current B Harmonics | H15 Current B Magnitude | H15 Current B Magnitude | 424900 | F32-4321 | R | 257288221
|  | Spectral Components | Current B Harmonics | H16 Current B Magnitude | H16 Current B Magnitude | 424906 | F32-4321 | R | 257288223
|  | Spectral Components | Current B Harmonics | H17 Current B Magnitude | H17 Current B Magnitude | 424912 | F32-4321 | R | 257288225
|  | Spectral Components | Current B Harmonics | H18 Current B Magnitude | H18 Current B Magnitude | 424918 | F32-4321 | R | 257288227
|  | Spectral Components | Current B Harmonics | H19 Current B Magnitude | H19 Current B Magnitude | 424924 | F32-4321 | R | 257288229
|  | Spectral Components | Current B Harmonics | H20 Current B Magnitude | H20 Current B Magnitude | 424930 | F32-4321 | R | 257288231
|  | Spectral Components | Current B Harmonics | H21 Current B Magnitude | H21 Current B Magnitude | 424936 | F32-4321 | R | 257288233
|  | Spectral Components | Current B Harmonics | H22 Current B Magnitude | H22 Current B Magnitude | 424942 | F32-4321 | R | 257288235
|  | Spectral Components | Current B Harmonics | H23 Current B Magnitude | H23 Current B Magnitude | 424948 | F32-4321 | R | 257288237
|  | Spectral Components | Current B Harmonics | H24 Current B Magnitude | H24 Current B Magnitude | 424954 | F32-4321 | R | 257288239
|  | Spectral Components | Current B Harmonics | H25 Current B Magnitude | H25 Current B Magnitude | 424960 | F32-4321 | R | 257288241
|  | Spectral Components | Current B Harmonics | H26 Current B Magnitude | H26 Current B Magnitude | 424966 | F32-4321 | R | 257288243
|  | Spectral Components | Current B Harmonics | H27 Current B Magnitude | H27 Current B Magnitude | 424972 | F32-4321 | R | 257288245
|  | Spectral Components | Current B Harmonics | H28 Current B Magnitude | H28 Current B Magnitude | 424978 | F32-4321 | R | 257288247
|  | Spectral Components | Current B Harmonics | H29 Current B Magnitude | H29 Current B Magnitude | 424984 | F32-4321 | R | 257288249
|  | Spectral Components | Current B Harmonics | H30 Current B Magnitude | H30 Current B Magnitude | 424990 | F32-4321 | R | 257288251
|  | Spectral Components | Current B Harmonics | H31 Current B Magnitude | H31 Current B Magnitude | 424996 | F32-4321 | R | 257288253
|  | Spectral Components | Current C Harmonics | H1 Current C Magnitude | H1 Current C Magnitude | 425204 | F32-4321 | R | 257288449
|  | Spectral Components | Current C Harmonics | H2 Current C Magnitude | H2 Current C Magnitude | 425210 | F32-4321 | R | 257288451
|  | Spectral Components | Current C Harmonics | H3 Current C Magnitude | H3 Current C Magnitude | 425216 | F32-4321 | R | 257288453
|  | Spectral Components | Current C Harmonics | H4 Current C Magnitude | H4 Current C Magnitude | 425222 | F32-4321 | R | 257288455
|  | Spectral Components | Current C Harmonics | H5 Current C Magnitude | H5 Current C Magnitude | 425228 | F32-4321 | R | 257288457
|  | Spectral Components | Current C Harmonics | H6 Current C Magnitude | H6 Current C Magnitude | 425234 | F32-4321 | R | 257288459
|  | Spectral Components | Current C Harmonics | H7 Current C Magnitude | H7 Current C Magnitude | 425240 | F32-4321 | R | 257288461
|  | Spectral Components | Current C Harmonics | H8 Current C Magnitude | H8 Current C Magnitude | 425246 | F32-4321 | R | 257288463
|  | Spectral Components | Current C Harmonics | H9 Current C Magnitude | H9 Current C Magnitude | 425252 | F32-4321 | R | 257288465
|  | Spectral Components | Current C Harmonics | H10 Current C Magnitude | H10 Current C Magnitude | 425258 | F32-4321 | R | 257288467
|  | Spectral Components | Current C Harmonics | H11 Current C Magnitude | H11 Current C Magnitude | 425264 | F32-4321 | R | 257288469
|  | Spectral Components | Current C Harmonics | H12 Current C Magnitude | H12 Current C Magnitude | 425270 | F32-4321 | R | 257288471
|  | Spectral Components | Current C Harmonics | H13 Current C Magnitude | H13 Current C Magnitude | 425276 | F32-4321 | R | 257288473
|  | Spectral Components | Current C Harmonics | H14 Current C Magnitude | H14 Current C Magnitude | 425282 | F32-4321 | R | 257288475
|  | Spectral Components | Current C Harmonics | H15 Current C Magnitude | H15 Current C Magnitude | 425288 | F32-4321 | R | 257288477
|  | Spectral Components | Current C Harmonics | H16 Current C Magnitude | H16 Current C Magnitude | 425294 | F32-4321 | R | 257288479
|  | Spectral Components | Current C Harmonics | H17 Current C Magnitude | H17 Current C Magnitude | 425300 | F32-4321 | R | 257288481
|  | Spectral Components | Current C Harmonics | H18 Current C Magnitude | H18 Current C Magnitude | 425306 | F32-4321 | R | 257288483
|  | Spectral Components | Current C Harmonics | H19 Current C Magnitude | H19 Current C Magnitude | 425312 | F32-4321 | R | 257288485
|  | Spectral Components | Current C Harmonics | H20 Current C Magnitude | H20 Current C Magnitude | 425318 | F32-4321 | R | 257288487
|  | Spectral Components | Current C Harmonics | H21 Current C Magnitude | H21 Current C Magnitude | 425324 | F32-4321 | R | 257288489
|  | Spectral Components | Current C Harmonics | H22 Current C Magnitude | H22 Current C Magnitude | 425330 | F32-4321 | R | 257288491
|  | Spectral Components | Current C Harmonics | H23 Current C Magnitude | H23 Current C Magnitude | 425336 | F32-4321 | R | 257288493
|  | Spectral Components | Current C Harmonics | H24 Current C Magnitude | H24 Current C Magnitude | 425342 | F32-4321 | R | 257288495
|  | Spectral Components | Current C Harmonics | H25 Current C Magnitude | H25 Current C Magnitude | 425348 | F32-4321 | R | 257288497
|  | Spectral Components | Current C Harmonics | H26 Current C Magnitude | H26 Current C Magnitude | 425354 | F32-4321 | R | 257288499
|  | Spectral Components | Current C Harmonics | H27 Current C Magnitude | H27 Current C Magnitude | 425360 | F32-4321 | R | 257288501
|  | Spectral Components | Current C Harmonics | H28 Current C Magnitude | H28 Current C Magnitude | 425366 | F32-4321 | R | 257288503
|  | Spectral Components | Current C Harmonics | H29 Current C Magnitude | H29 Current C Magnitude | 425372 | F32-4321 | R | 257288505
|  | Spectral Components | Current C Harmonics | H30 Current C Magnitude | H30 Current C Magnitude | 425378 | F32-4321 | R | 257288507
|  | Spectral Components | Current C Harmonics | H31 Current C Magnitude | H31 Current C Magnitude | 425384 | F32-4321 | R | 257288509
|  | Spectral Components | Voltage A-B Harmonics | H1 Voltage A-B Magnitude | H1 Voltage A-B Magnitude | 421712 | F32-4321 | R | 257286401
|  | Spectral Components | Voltage A-B Harmonics | H2 Voltage A-B Magnitude | H2 Voltage A-B Magnitude | 421718 | F32-4321 | R | 257286403
|  | Spectral Components | Voltage A-B Harmonics | H3 Voltage A-B Magnitude | H3 Voltage A-B Magnitude | 421724 | F32-4321 | R | 257286405
|  | Spectral Components | Voltage A-B Harmonics | H4 Voltage A-B Magnitude | H4 Voltage A-B Magnitude | 421730 | F32-4321 | R | 257286407
|  | Spectral Components | Voltage A-B Harmonics | H5 Voltage A-B Magnitude | H5 Voltage A-B Magnitude | 421736 | F32-4321 | R | 257286409
|  | Spectral Components | Voltage A-B Harmonics | H6 Voltage A-B Magnitude | H6 Voltage A-B Magnitude | 421742 | F32-4321 | R | 257286411
|  | Spectral Components | Voltage A-B Harmonics | H7 Voltage A-B Magnitude | H7 Voltage A-B Magnitude | 421748 | F32-4321 | R | 257286413
|  | Spectral Components | Voltage A-B Harmonics | H8 Voltage A-B Magnitude | H8 Voltage A-B Magnitude | 421754 | F32-4321 | R | 257286415
|  | Spectral Components | Voltage A-B Harmonics | H9 Voltage A-B Magnitude | H9 Voltage A-B Magnitude | 421760 | F32-4321 | R | 257286417
|  | Spectral Components | Voltage A-B Harmonics | H10 Voltage A-B Magnitude | H10 Voltage A-B Magnitude | 421766 | F32-4321 | R | 257286419
|  | Spectral Components | Voltage A-B Harmonics | H11 Voltage A-B Magnitude | H11 Voltage A-B Magnitude | 421772 | F32-4321 | R | 257286421
|  | Spectral Components | Voltage A-B Harmonics | H12 Voltage A-B Magnitude | H12 Voltage A-B Magnitude | 421778 | F32-4321 | R | 257286423
|  | Spectral Components | Voltage A-B Harmonics | H13 Voltage A-B Magnitude | H13 Voltage A-B Magnitude | 421784 | F32-4321 | R | 257286425
|  | Spectral Components | Voltage A-B Harmonics | H14 Voltage A-B Magnitude | H14 Voltage A-B Magnitude | 421790 | F32-4321 | R | 257286427
|  | Spectral Components | Voltage A-B Harmonics | H15 Voltage A-B Magnitude | H15 Voltage A-B Magnitude | 421796 | F32-4321 | R | 257286429
|  | Spectral Components | Voltage A-B Harmonics | H16 Voltage A-B Magnitude | H16 Voltage A-B Magnitude | 421802 | F32-4321 | R | 257286431
|  | Spectral Components | Voltage A-B Harmonics | H17 Voltage A-B Magnitude | H17 Voltage A-B Magnitude | 421808 | F32-4321 | R | 257286433
|  | Spectral Components | Voltage A-B Harmonics | H18 Voltage A-B Magnitude | H18 Voltage A-B Magnitude | 421814 | F32-4321 | R | 257286435
|  | Spectral Components | Voltage A-B Harmonics | H19 Voltage A-B Magnitude | H19 Voltage A-B Magnitude | 421820 | F32-4321 | R | 257286437
|  | Spectral Components | Voltage A-B Harmonics | H20 Voltage A-B Magnitude | H20 Voltage A-B Magnitude | 421826 | F32-4321 | R | 257286439
|  | Spectral Components | Voltage A-B Harmonics | H21 Voltage A-B Magnitude | H21 Voltage A-B Magnitude | 421832 | F32-4321 | R | 257286441
|  | Spectral Components | Voltage A-B Harmonics | H22 Voltage A-B Magnitude | H22 Voltage A-B Magnitude | 421838 | F32-4321 | R | 257286443
|  | Spectral Components | Voltage A-B Harmonics | H23 Voltage A-B Magnitude | H23 Voltage A-B Magnitude | 421844 | F32-4321 | R | 257286445
|  | Spectral Components | Voltage A-B Harmonics | H24 Voltage A-B Magnitude | H24 Voltage A-B Magnitude | 421850 | F32-4321 | R | 257286447
|  | Spectral Components | Voltage A-B Harmonics | H25 Voltage A-B Magnitude | H25 Voltage A-B Magnitude | 421856 | F32-4321 | R | 257286449
|  | Spectral Components | Voltage A-B Harmonics | H26 Voltage A-B Magnitude | H26 Voltage A-B Magnitude | 421862 | F32-4321 | R | 257286451
|  | Spectral Components | Voltage A-B Harmonics | H27 Voltage A-B Magnitude | H27 Voltage A-B Magnitude | 421868 | F32-4321 | R | 257286453
|  | Spectral Components | Voltage A-B Harmonics | H28 Voltage A-B Magnitude | H28 Voltage A-B Magnitude | 421874 | F32-4321 | R | 257286455
|  | Spectral Components | Voltage A-B Harmonics | H29 Voltage A-B Magnitude | H29 Voltage A-B Magnitude | 421880 | F32-4321 | R | 257286457
|  | Spectral Components | Voltage A-B Harmonics | H30 Voltage A-B Magnitude | H30 Voltage A-B Magnitude | 421886 | F32-4321 | R | 257286459
|  | Spectral Components | Voltage A-B Harmonics | H31 Voltage A-B Magnitude | H31 Voltage A-B Magnitude | 421892 | F32-4321 | R | 257286461
|  | Spectral Components | Voltage A-N Harmonics | H1 Voltage A-N Magnitude | H1 Voltage A-N Magnitude | 422876 | F32-4321 | R | 257287169
|  | Spectral Components | Voltage A-N Harmonics | H2 Voltage A-N Magnitude | H2 Voltage A-N Magnitude | 422882 | F32-4321 | R | 257287171
|  | Spectral Components | Voltage A-N Harmonics | H3 Voltage A-N Magnitude | H3 Voltage A-N Magnitude | 422888 | F32-4321 | R | 257287173
|  | Spectral Components | Voltage A-N Harmonics | H4 Voltage A-N Magnitude | H4 Voltage A-N Magnitude | 422894 | F32-4321 | R | 257287175
|  | Spectral Components | Voltage A-N Harmonics | H5 Voltage A-N Magnitude | H5 Voltage A-N Magnitude | 422900 | F32-4321 | R | 257287177
|  | Spectral Components | Voltage A-N Harmonics | H6 Voltage A-N Magnitude | H6 Voltage A-N Magnitude | 422906 | F32-4321 | R | 257287179
|  | Spectral Components | Voltage A-N Harmonics | H7 Voltage A-N Magnitude | H7 Voltage A-N Magnitude | 422912 | F32-4321 | R | 257287181
|  | Spectral Components | Voltage A-N Harmonics | H8 Voltage A-N Magnitude | H8 Voltage A-N Magnitude | 422918 | F32-4321 | R | 257287183
|  | Spectral Components | Voltage A-N Harmonics | H9 Voltage A-N Magnitude | H9 Voltage A-N Magnitude | 422924 | F32-4321 | R | 257287185
|  | Spectral Components | Voltage A-N Harmonics | H10 Voltage A-N Magnitude | H10 Voltage A-N Magnitude | 422930 | F32-4321 | R | 257287187
|  | Spectral Components | Voltage A-N Harmonics | H11 Voltage A-N Magnitude | H11 Voltage A-N Magnitude | 422936 | F32-4321 | R | 257287189
|  | Spectral Components | Voltage A-N Harmonics | H12 Voltage A-N Magnitude | H12 Voltage A-N Magnitude | 422942 | F32-4321 | R | 257287191
|  | Spectral Components | Voltage A-N Harmonics | H13 Voltage A-N Magnitude | H13 Voltage A-N Magnitude | 422948 | F32-4321 | R | 257287193
|  | Spectral Components | Voltage A-N Harmonics | H14 Voltage A-N Magnitude | H14 Voltage A-N Magnitude | 422954 | F32-4321 | R | 257287195
|  | Spectral Components | Voltage A-N Harmonics | H15 Voltage A-N Magnitude | H15 Voltage A-N Magnitude | 422960 | F32-4321 | R | 257287197
|  | Spectral Components | Voltage A-N Harmonics | H16 Voltage A-N Magnitude | H16 Voltage A-N Magnitude | 422966 | F32-4321 | R | 257287199
|  | Spectral Components | Voltage A-N Harmonics | H17 Voltage A-N Magnitude | H17 Voltage A-N Magnitude | 422972 | F32-4321 | R | 257287201
|  | Spectral Components | Voltage A-N Harmonics | H18 Voltage A-N Magnitude | H18 Voltage A-N Magnitude | 422978 | F32-4321 | R | 257287203
|  | Spectral Components | Voltage A-N Harmonics | H19 Voltage A-N Magnitude | H19 Voltage A-N Magnitude | 422984 | F32-4321 | R | 257287205
|  | Spectral Components | Voltage A-N Harmonics | H20 Voltage A-N Magnitude | H20 Voltage A-N Magnitude | 422990 | F32-4321 | R | 257287207
|  | Spectral Components | Voltage A-N Harmonics | H21 Voltage A-N Magnitude | H21 Voltage A-N Magnitude | 422996 | F32-4321 | R | 257287209
|  | Spectral Components | Voltage A-N Harmonics | H22 Voltage A-N Magnitude | H22 Voltage A-N Magnitude | 423002 | F32-4321 | R | 257287211
|  | Spectral Components | Voltage A-N Harmonics | H23 Voltage A-N Magnitude | H23 Voltage A-N Magnitude | 423008 | F32-4321 | R | 257287213
|  | Spectral Components | Voltage A-N Harmonics | H24 Voltage A-N Magnitude | H24 Voltage A-N Magnitude | 423014 | F32-4321 | R | 257287215
|  | Spectral Components | Voltage A-N Harmonics | H25 Voltage A-N Magnitude | H25 Voltage A-N Magnitude | 423020 | F32-4321 | R | 257287217
|  | Spectral Components | Voltage A-N Harmonics | H26 Voltage A-N Magnitude | H26 Voltage A-N Magnitude | 423026 | F32-4321 | R | 257287219
|  | Spectral Components | Voltage A-N Harmonics | H27 Voltage A-N Magnitude | H27 Voltage A-N Magnitude | 423032 | F32-4321 | R | 257287221
|  | Spectral Components | Voltage A-N Harmonics | H28 Voltage A-N Magnitude | H28 Voltage A-N Magnitude | 423038 | F32-4321 | R | 257287223
|  | Spectral Components | Voltage A-N Harmonics | H29 Voltage A-N Magnitude | H29 Voltage A-N Magnitude | 423044 | F32-4321 | R | 257287225
|  | Spectral Components | Voltage A-N Harmonics | H30 Voltage A-N Magnitude | H30 Voltage A-N Magnitude | 423050 | F32-4321 | R | 257287227
|  | Spectral Components | Voltage A-N Harmonics | H31 Voltage A-N Magnitude | H31 Voltage A-N Magnitude | 423056 | F32-4321 | R | 257287229
|  | Spectral Components | Voltage B-C Harmonics | H1 Voltage B-C Magnitude | H1 Voltage B-C Magnitude | 422100 | F32-4321 | R | 257286657
|  | Spectral Components | Voltage B-C Harmonics | H2 Voltage B-C Magnitude | H2 Voltage B-C Magnitude | 422106 | F32-4321 | R | 257286659
|  | Spectral Components | Voltage B-C Harmonics | H3 Voltage B-C Magnitude | H3 Voltage B-C Magnitude | 422112 | F32-4321 | R | 257286661
|  | Spectral Components | Voltage B-C Harmonics | H4 Voltage B-C Magnitude | H4 Voltage B-C Magnitude | 422118 | F32-4321 | R | 257286663
|  | Spectral Components | Voltage B-C Harmonics | H5 Voltage B-C Magnitude | H5 Voltage B-C Magnitude | 422124 | F32-4321 | R | 257286665
|  | Spectral Components | Voltage B-C Harmonics | H6 Voltage B-C Magnitude | H6 Voltage B-C Magnitude | 422130 | F32-4321 | R | 257286667
|  | Spectral Components | Voltage B-C Harmonics | H7 Voltage B-C Magnitude | H7 Voltage B-C Magnitude | 422136 | F32-4321 | R | 257286669
|  | Spectral Components | Voltage B-C Harmonics | H8 Voltage B-C Magnitude | H8 Voltage B-C Magnitude | 422142 | F32-4321 | R | 257286671
|  | Spectral Components | Voltage B-C Harmonics | H9 Voltage B-C Magnitude | H9 Voltage B-C Magnitude | 422148 | F32-4321 | R | 257286673
|  | Spectral Components | Voltage B-C Harmonics | H10 Voltage B-C Magnitude | H10 Voltage B-C Magnitude | 422154 | F32-4321 | R | 257286675
|  | Spectral Components | Voltage B-C Harmonics | H11 Voltage B-C Magnitude | H11 Voltage B-C Magnitude | 422160 | F32-4321 | R | 257286677
|  | Spectral Components | Voltage B-C Harmonics | H12 Voltage B-C Magnitude | H12 Voltage B-C Magnitude | 422166 | F32-4321 | R | 257286679
|  | Spectral Components | Voltage B-C Harmonics | H13 Voltage B-C Magnitude | H13 Voltage B-C Magnitude | 422172 | F32-4321 | R | 257286681
|  | Spectral Components | Voltage B-C Harmonics | H14 Voltage B-C Magnitude | H14 Voltage B-C Magnitude | 422178 | F32-4321 | R | 257286683
|  | Spectral Components | Voltage B-C Harmonics | H15 Voltage B-C Magnitude | H15 Voltage B-C Magnitude | 422184 | F32-4321 | R | 257286685
|  | Spectral Components | Voltage B-C Harmonics | H16 Voltage B-C Magnitude | H16 Voltage B-C Magnitude | 422190 | F32-4321 | R | 257286687
|  | Spectral Components | Voltage B-C Harmonics | H17 Voltage B-C Magnitude | H17 Voltage B-C Magnitude | 422196 | F32-4321 | R | 257286689
|  | Spectral Components | Voltage B-C Harmonics | H18 Voltage B-C Magnitude | H18 Voltage B-C Magnitude | 422202 | F32-4321 | R | 257286691
|  | Spectral Components | Voltage B-C Harmonics | H19 Voltage B-C Magnitude | H19 Voltage B-C Magnitude | 422208 | F32-4321 | R | 257286693
|  | Spectral Components | Voltage B-C Harmonics | H20 Voltage B-C Magnitude | H20 Voltage B-C Magnitude | 422214 | F32-4321 | R | 257286695
|  | Spectral Components | Voltage B-C Harmonics | H21 Voltage B-C Magnitude | H21 Voltage B-C Magnitude | 422220 | F32-4321 | R | 257286697
|  | Spectral Components | Voltage B-C Harmonics | H22 Voltage B-C Magnitude | H22 Voltage B-C Magnitude | 422226 | F32-4321 | R | 257286699
|  | Spectral Components | Voltage B-C Harmonics | H23 Voltage B-C Magnitude | H23 Voltage B-C Magnitude | 422232 | F32-4321 | R | 257286701
|  | Spectral Components | Voltage B-C Harmonics | H24 Voltage B-C Magnitude | H24 Voltage B-C Magnitude | 422238 | F32-4321 | R | 257286703
|  | Spectral Components | Voltage B-C Harmonics | H25 Voltage B-C Magnitude | H25 Voltage B-C Magnitude | 422244 | F32-4321 | R | 257286705
|  | Spectral Components | Voltage B-C Harmonics | H26 Voltage B-C Magnitude | H26 Voltage B-C Magnitude | 422250 | F32-4321 | R | 257286707
|  | Spectral Components | Voltage B-C Harmonics | H27 Voltage B-C Magnitude | H27 Voltage B-C Magnitude | 422256 | F32-4321 | R | 257286709
|  | Spectral Components | Voltage B-C Harmonics | H28 Voltage B-C Magnitude | H28 Voltage B-C Magnitude | 422262 | F32-4321 | R | 257286711
|  | Spectral Components | Voltage B-C Harmonics | H29 Voltage B-C Magnitude | H29 Voltage B-C Magnitude | 422268 | F32-4321 | R | 257286713
|  | Spectral Components | Voltage B-C Harmonics | H30 Voltage B-C Magnitude | H30 Voltage B-C Magnitude | 422274 | F32-4321 | R | 257286715
|  | Spectral Components | Voltage B-C Harmonics | H31 Voltage B-C Magnitude | H31 Voltage B-C Magnitude | 422280 | F32-4321 | R | 257286717
|  | Spectral Components | Voltage B-N Harmonics | H1 Voltage B-N Magnitude | H1 Voltage B-N Magnitude | 423264 | F32-4321 | R | 257287425
|  | Spectral Components | Voltage B-N Harmonics | H2 Voltage B-N Magnitude | H2 Voltage B-N Magnitude | 423270 | F32-4321 | R | 257287427
|  | Spectral Components | Voltage B-N Harmonics | H3 Voltage B-N Magnitude | H3 Voltage B-N Magnitude | 423276 | F32-4321 | R | 257287429
|  | Spectral Components | Voltage B-N Harmonics | H4 Voltage B-N Magnitude | H4 Voltage B-N Magnitude | 423282 | F32-4321 | R | 257287431
|  | Spectral Components | Voltage B-N Harmonics | H5 Voltage B-N Magnitude | H5 Voltage B-N Magnitude | 423288 | F32-4321 | R | 257287433
|  | Spectral Components | Voltage B-N Harmonics | H6 Voltage B-N Magnitude | H6 Voltage B-N Magnitude | 423294 | F32-4321 | R | 257287435
|  | Spectral Components | Voltage B-N Harmonics | H7 Voltage B-N Magnitude | H7 Voltage B-N Magnitude | 423300 | F32-4321 | R | 257287437
|  | Spectral Components | Voltage B-N Harmonics | H8 Voltage B-N Magnitude | H8 Voltage B-N Magnitude | 423306 | F32-4321 | R | 257287439
|  | Spectral Components | Voltage B-N Harmonics | H9 Voltage B-N Magnitude | H9 Voltage B-N Magnitude | 423312 | F32-4321 | R | 257287441
|  | Spectral Components | Voltage B-N Harmonics | H10 Voltage B-N Magnitude | H10 Voltage B-N Magnitude | 423318 | F32-4321 | R | 257287443
|  | Spectral Components | Voltage B-N Harmonics | H11 Voltage B-N Magnitude | H11 Voltage B-N Magnitude | 423324 | F32-4321 | R | 257287445
|  | Spectral Components | Voltage B-N Harmonics | H12 Voltage B-N Magnitude | H12 Voltage B-N Magnitude | 423330 | F32-4321 | R | 257287447
|  | Spectral Components | Voltage B-N Harmonics | H13 Voltage B-N Magnitude | H13 Voltage B-N Magnitude | 423336 | F32-4321 | R | 257287449
|  | Spectral Components | Voltage B-N Harmonics | H14 Voltage B-N Magnitude | H14 Voltage B-N Magnitude | 423342 | F32-4321 | R | 257287451
|  | Spectral Components | Voltage B-N Harmonics | H15 Voltage B-N Magnitude | H15 Voltage B-N Magnitude | 423348 | F32-4321 | R | 257287453
|  | Spectral Components | Voltage B-N Harmonics | H16 Voltage B-N Magnitude | H16 Voltage B-N Magnitude | 423354 | F32-4321 | R | 257287455
|  | Spectral Components | Voltage B-N Harmonics | H17 Voltage B-N Magnitude | H17 Voltage B-N Magnitude | 423360 | F32-4321 | R | 257287457
|  | Spectral Components | Voltage B-N Harmonics | H18 Voltage B-N Magnitude | H18 Voltage B-N Magnitude | 423366 | F32-4321 | R | 257287459
|  | Spectral Components | Voltage B-N Harmonics | H19 Voltage B-N Magnitude | H19 Voltage B-N Magnitude | 423372 | F32-4321 | R | 257287461
|  | Spectral Components | Voltage B-N Harmonics | H20 Voltage B-N Magnitude | H20 Voltage B-N Magnitude | 423378 | F32-4321 | R | 257287463
|  | Spectral Components | Voltage B-N Harmonics | H21 Voltage B-N Magnitude | H21 Voltage B-N Magnitude | 423384 | F32-4321 | R | 257287465
|  | Spectral Components | Voltage B-N Harmonics | H22 Voltage B-N Magnitude | H22 Voltage B-N Magnitude | 423390 | F32-4321 | R | 257287467
|  | Spectral Components | Voltage B-N Harmonics | H23 Voltage B-N Magnitude | H23 Voltage B-N Magnitude | 423396 | F32-4321 | R | 257287469
|  | Spectral Components | Voltage B-N Harmonics | H24 Voltage B-N Magnitude | H24 Voltage B-N Magnitude | 423402 | F32-4321 | R | 257287471
|  | Spectral Components | Voltage B-N Harmonics | H25 Voltage B-N Magnitude | H25 Voltage B-N Magnitude | 423408 | F32-4321 | R | 257287473
|  | Spectral Components | Voltage B-N Harmonics | H26 Voltage B-N Magnitude | H26 Voltage B-N Magnitude | 423414 | F32-4321 | R | 257287475
|  | Spectral Components | Voltage B-N Harmonics | H27 Voltage B-N Magnitude | H27 Voltage B-N Magnitude | 423420 | F32-4321 | R | 257287477
|  | Spectral Components | Voltage B-N Harmonics | H28 Voltage B-N Magnitude | H28 Voltage B-N Magnitude | 423426 | F32-4321 | R | 257287479
|  | Spectral Components | Voltage B-N Harmonics | H29 Voltage B-N Magnitude | H29 Voltage B-N Magnitude | 423432 | F32-4321 | R | 257287481
|  | Spectral Components | Voltage B-N Harmonics | H30 Voltage B-N Magnitude | H30 Voltage B-N Magnitude | 423438 | F32-4321 | R | 257287483
|  | Spectral Components | Voltage B-N Harmonics | H31 Voltage B-N Magnitude | H31 Voltage B-N Magnitude | 423444 | F32-4321 | R | 257287485
|  | Spectral Components | Voltage C-A Harmonics | H1 Voltage C-A Magnitude | H1 Voltage C-A Magnitude | 422488 | F32-4321 | R | 257286913
|  | Spectral Components | Voltage C-A Harmonics | H2 Voltage C-A Magnitude | H2 Voltage C-A Magnitude | 422494 | F32-4321 | R | 257286915
|  | Spectral Components | Voltage C-A Harmonics | H3 Voltage C-A Magnitude | H3 Voltage C-A Magnitude | 422500 | F32-4321 | R | 257286917
|  | Spectral Components | Voltage C-A Harmonics | H4 Voltage C-A Magnitude | H4 Voltage C-A Magnitude | 422506 | F32-4321 | R | 257286919
|  | Spectral Components | Voltage C-A Harmonics | H5 Voltage C-A Magnitude | H5 Voltage C-A Magnitude | 422512 | F32-4321 | R | 257286921
|  | Spectral Components | Voltage C-A Harmonics | H6 Voltage C-A Magnitude | H6 Voltage C-A Magnitude | 422518 | F32-4321 | R | 257286923
|  | Spectral Components | Voltage C-A Harmonics | H7 Voltage C-A Magnitude | H7 Voltage C-A Magnitude | 422524 | F32-4321 | R | 257286925
|  | Spectral Components | Voltage C-A Harmonics | H8 Voltage C-A Magnitude | H8 Voltage C-A Magnitude | 422530 | F32-4321 | R | 257286927
|  | Spectral Components | Voltage C-A Harmonics | H9 Voltage C-A Magnitude | H9 Voltage C-A Magnitude | 422536 | F32-4321 | R | 257286929
|  | Spectral Components | Voltage C-A Harmonics | H10 Voltage C-A Magnitude | H10 Voltage C-A Magnitude | 422542 | F32-4321 | R | 257286931
|  | Spectral Components | Voltage C-A Harmonics | H11 Voltage C-A Magnitude | H11 Voltage C-A Magnitude | 422548 | F32-4321 | R | 257286933
|  | Spectral Components | Voltage C-A Harmonics | H12 Voltage C-A Magnitude | H12 Voltage C-A Magnitude | 422554 | F32-4321 | R | 257286935
|  | Spectral Components | Voltage C-A Harmonics | H13 Voltage C-A Magnitude | H13 Voltage C-A Magnitude | 422560 | F32-4321 | R | 257286937
|  | Spectral Components | Voltage C-A Harmonics | H14 Voltage C-A Magnitude | H14 Voltage C-A Magnitude | 422566 | F32-4321 | R | 257286939
|  | Spectral Components | Voltage C-A Harmonics | H15 Voltage C-A Magnitude | H15 Voltage C-A Magnitude | 422572 | F32-4321 | R | 257286941
|  | Spectral Components | Voltage C-A Harmonics | H16 Voltage C-A Magnitude | H16 Voltage C-A Magnitude | 422578 | F32-4321 | R | 257286943
|  | Spectral Components | Voltage C-A Harmonics | H17 Voltage C-A Magnitude | H17 Voltage C-A Magnitude | 422584 | F32-4321 | R | 257286945
|  | Spectral Components | Voltage C-A Harmonics | H18 Voltage C-A Magnitude | H18 Voltage C-A Magnitude | 422590 | F32-4321 | R | 257286947
|  | Spectral Components | Voltage C-A Harmonics | H19 Voltage C-A Magnitude | H19 Voltage C-A Magnitude | 422596 | F32-4321 | R | 257286949
|  | Spectral Components | Voltage C-A Harmonics | H20 Voltage C-A Magnitude | H20 Voltage C-A Magnitude | 422602 | F32-4321 | R | 257286951
|  | Spectral Components | Voltage C-A Harmonics | H21 Voltage C-A Magnitude | H21 Voltage C-A Magnitude | 422608 | F32-4321 | R | 257286953
|  | Spectral Components | Voltage C-A Harmonics | H22 Voltage C-A Magnitude | H22 Voltage C-A Magnitude | 422614 | F32-4321 | R | 257286955
|  | Spectral Components | Voltage C-A Harmonics | H23 Voltage C-A Magnitude | H23 Voltage C-A Magnitude | 422620 | F32-4321 | R | 257286957
|  | Spectral Components | Voltage C-A Harmonics | H24 Voltage C-A Magnitude | H24 Voltage C-A Magnitude | 422626 | F32-4321 | R | 257286959
|  | Spectral Components | Voltage C-A Harmonics | H25 Voltage C-A Magnitude | H25 Voltage C-A Magnitude | 422632 | F32-4321 | R | 257286961
|  | Spectral Components | Voltage C-A Harmonics | H26 Voltage C-A Magnitude | H26 Voltage C-A Magnitude | 422638 | F32-4321 | R | 257286963
|  | Spectral Components | Voltage C-A Harmonics | H27 Voltage C-A Magnitude | H27 Voltage C-A Magnitude | 422644 | F32-4321 | R | 257286965
|  | Spectral Components | Voltage C-A Harmonics | H28 Voltage C-A Magnitude | H28 Voltage C-A Magnitude | 422650 | F32-4321 | R | 257286967
|  | Spectral Components | Voltage C-A Harmonics | H29 Voltage C-A Magnitude | H29 Voltage C-A Magnitude | 422656 | F32-4321 | R | 257286969
|  | Spectral Components | Voltage C-A Harmonics | H30 Voltage C-A Magnitude | H30 Voltage C-A Magnitude | 422662 | F32-4321 | R | 257286971
|  | Spectral Components | Voltage C-A Harmonics | H31 Voltage C-A Magnitude | H31 Voltage C-A Magnitude | 422668 | F32-4321 | R | 257286973
|  | Spectral Components | Voltage C-N Harmonics | H1 Voltage C-N Magnitude | H1 Voltage C-N Magnitude | 423652 | F32-4321 | R | 257287681
|  | Spectral Components | Voltage C-N Harmonics | H2 Voltage C-N Magnitude | H2 Voltage C-N Magnitude | 423658 | F32-4321 | R | 257287683
|  | Spectral Components | Voltage C-N Harmonics | H3 Voltage C-N Magnitude | H3 Voltage C-N Magnitude | 423664 | F32-4321 | R | 257287685
|  | Spectral Components | Voltage C-N Harmonics | H4 Voltage C-N Magnitude | H4 Voltage C-N Magnitude | 423670 | F32-4321 | R | 257287687
|  | Spectral Components | Voltage C-N Harmonics | H5 Voltage C-N Magnitude | H5 Voltage C-N Magnitude | 423676 | F32-4321 | R | 257287689
|  | Spectral Components | Voltage C-N Harmonics | H6 Voltage C-N Magnitude | H6 Voltage C-N Magnitude | 423682 | F32-4321 | R | 257287691
|  | Spectral Components | Voltage C-N Harmonics | H7 Voltage C-N Magnitude | H7 Voltage C-N Magnitude | 423688 | F32-4321 | R | 257287693
|  | Spectral Components | Voltage C-N Harmonics | H8 Voltage C-N Magnitude | H8 Voltage C-N Magnitude | 423694 | F32-4321 | R | 257287695
|  | Spectral Components | Voltage C-N Harmonics | H9 Voltage C-N Magnitude | H9 Voltage C-N Magnitude | 423700 | F32-4321 | R | 257287697
|  | Spectral Components | Voltage C-N Harmonics | H10 Voltage C-N Magnitude | H10 Voltage C-N Magnitude | 423706 | F32-4321 | R | 257287699
|  | Spectral Components | Voltage C-N Harmonics | H11 Voltage C-N Magnitude | H11 Voltage C-N Magnitude | 423712 | F32-4321 | R | 257287701
|  | Spectral Components | Voltage C-N Harmonics | H12 Voltage C-N Magnitude | H12 Voltage C-N Magnitude | 423718 | F32-4321 | R | 257287703
|  | Spectral Components | Voltage C-N Harmonics | H13 Voltage C-N Magnitude | H13 Voltage C-N Magnitude | 423724 | F32-4321 | R | 257287705
|  | Spectral Components | Voltage C-N Harmonics | H14 Voltage C-N Magnitude | H14 Voltage C-N Magnitude | 423730 | F32-4321 | R | 257287707
|  | Spectral Components | Voltage C-N Harmonics | H15 Voltage C-N Magnitude | H15 Voltage C-N Magnitude | 423736 | F32-4321 | R | 257287709
|  | Spectral Components | Voltage C-N Harmonics | H16 Voltage C-N Magnitude | H16 Voltage C-N Magnitude | 423742 | F32-4321 | R | 257287711
|  | Spectral Components | Voltage C-N Harmonics | H17 Voltage C-N Magnitude | H17 Voltage C-N Magnitude | 423748 | F32-4321 | R | 257287713
|  | Spectral Components | Voltage C-N Harmonics | H18 Voltage C-N Magnitude | H18 Voltage C-N Magnitude | 423754 | F32-4321 | R | 257287715
|  | Spectral Components | Voltage C-N Harmonics | H19 Voltage C-N Magnitude | H19 Voltage C-N Magnitude | 423760 | F32-4321 | R | 257287717
|  | Spectral Components | Voltage C-N Harmonics | H20 Voltage C-N Magnitude | H20 Voltage C-N Magnitude | 423766 | F32-4321 | R | 257287719
|  | Spectral Components | Voltage C-N Harmonics | H21 Voltage C-N Magnitude | H21 Voltage C-N Magnitude | 423772 | F32-4321 | R | 257287721
|  | Spectral Components | Voltage C-N Harmonics | H22 Voltage C-N Magnitude | H22 Voltage C-N Magnitude | 423778 | F32-4321 | R | 257287723
|  | Spectral Components | Voltage C-N Harmonics | H23 Voltage C-N Magnitude | H23 Voltage C-N Magnitude | 423784 | F32-4321 | R | 257287725
|  | Spectral Components | Voltage C-N Harmonics | H24 Voltage C-N Magnitude | H24 Voltage C-N Magnitude | 423790 | F32-4321 | R | 257287727
|  | Spectral Components | Voltage C-N Harmonics | H25 Voltage C-N Magnitude | H25 Voltage C-N Magnitude | 423796 | F32-4321 | R | 257287729
|  | Spectral Components | Voltage C-N Harmonics | H26 Voltage C-N Magnitude | H26 Voltage C-N Magnitude | 423802 | F32-4321 | R | 257287731
|  | Spectral Components | Voltage C-N Harmonics | H27 Voltage C-N Magnitude | H27 Voltage C-N Magnitude | 423808 | F32-4321 | R | 257287733
|  | Spectral Components | Voltage C-N Harmonics | H28 Voltage C-N Magnitude | H28 Voltage C-N Magnitude | 423814 | F32-4321 | R | 257287735
|  | Spectral Components | Voltage C-N Harmonics | H29 Voltage C-N Magnitude | H29 Voltage C-N Magnitude | 423820 | F32-4321 | R | 257287737
|  | Spectral Components | Voltage C-N Harmonics | H30 Voltage C-N Magnitude | H30 Voltage C-N Magnitude | 423826 | F32-4321 | R | 257287739
|  | Spectral Components | Voltage C-N Harmonics | H31 Voltage C-N Magnitude | H31 Voltage C-N Magnitude | 423832 | F32-4321 | R | 257287741
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate A | Active Energy Delivered Rate A | 404196 | S64-87-21 | R | 258335489 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate B | Active Energy Delivered Rate B | 404200 | S64-87-21 | R | 258335490 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate C | Active Energy Delivered Rate C | 404204 | S64-87-21 | R | 258335491 |  | 1000
|  | Time of Use | Active Energy Delivered | Active Energy Delivered Rate D | Active Energy Delivered Rate D | 404208 | S64-87-21 | R | 258335492 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate A | Apparent Energy Delivered Rate A | 404324 | S64-87-21 | R | 258336001 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate B | Apparent Energy Delivered Rate B | 404328 | S64-87-21 | R | 258336002 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate C | Apparent Energy Delivered Rate C | 404332 | S64-87-21 | R | 258336003 |  | 1000
|  | Time of Use | Apparent Energy Delivered | Apparent Energy Delivered Rate D | Apparent Energy Delivered Rate D | 404336 | S64-87-21 | R | 258336004 |  | 1000
|  | Time of Use | DT Time of Use Last Reset | DT Time of Use Last Reset | DT Time of Use Last Reset | 404192 | DateTime_IEC870_UTC | R | 258335233
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate A | Reactive Energy Delivered Rate A | 404260 | S64-87-21 | R | 258335745 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate B | Reactive Energy Delivered Rate B | 404264 | S64-87-21 | R | 258335746 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate C | Reactive Energy Delivered Rate C | 404268 | S64-87-21 | R | 258335747 |  | 1000
|  | Time of Use | Reactive Energy Delivered | Reactive Energy Delivered Rate D | Reactive Energy Delivered Rate D | 404272 | S64-87-21 | R | 258335748 |  | 1000
|  | Time of Use | Time of Use Active Rate | Time of Use Active Rate | Time of Use Active Rate | 404191 | UINT16 | R | 258334977
|  | Unbalances | Current Unbalance | Current Unbalance A | Current Unbalance A | 403012 | F32-4321 | R | 198180865 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance B | Current Unbalance B | 403014 | F32-4321 | R | 198180866 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance C | Current Unbalance C | 403016 | F32-4321 | R | 198180867 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance Worst | Current Unbalance Worst | 403018 | F32-4321 | R | 198180868 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-B | Voltage Unbalance A-B | 403038 | F32-4321 | R | 198181121 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-N | Voltage Unbalance A-N | 403046 | F32-4321 | R | 198181125 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-C | Voltage Unbalance B-C | 403040 | F32-4321 | R | 198181122 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-N | Voltage Unbalance B-N | 403048 | F32-4321 | R | 198181126 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-A | Voltage Unbalance C-A | 403042 | F32-4321 | R | 198181123 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-N | Voltage Unbalance C-N | 403050 | F32-4321 | R | 198181127 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-L Worst | Voltage Unbalance L-L Worst | 403044 | F32-4321 | R | 198181124 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-N Worst | Voltage Unbalance L-N Worst | 403052 | F32-4321 | R | 198181128 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage A-B | Voltage A-B | 403020 | F32-4321 | R | 201326593 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage A-N | Voltage A-N | 403028 | F32-4321 | R | 201326597 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage B-C | Voltage B-C | 403022 | F32-4321 | R | 201326594 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage B-N | Voltage B-N | 403030 | F32-4321 | R | 201326598 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage C-A | Voltage C-A | 403024 | F32-4321 | R | 201326595 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage C-N | Voltage C-N | 403032 | F32-4321 | R | 201326599 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage L-L Avg | Voltage L-L Avg | 403026 | F32-4321 | R | 201326596 |  |  |  |  | 2
|  | Voltages | Voltage | Voltage L-N Avg | Voltage L-N Avg | 403036 | F32-4321 | R | 201326600 |  |  |  |  | 2
|  | Relay Output | Relay1 | R1 Type | R1 Type | 409235 | UINT16 | R | 136314881 |  |  |  | DOTypes
|  | Relay Output | Relay1 | R1 Status | R1 Status | 409667 | MaskedBool | R | 136314882 | 0x0004
|  | Relay Output | Relay1 | R1 Operating Mode | R1 Operating Mode | 409688 | UINT16 | R | 136314883 |  |  |  | DOOperatingModes
|  | Relay Output | Relay1 | R1 On Time | R1 On Time | 409693 | UINT32 | R | 136314884
|  | Relay Output | Relay1 | R1 Label | R1 Label | 409236 | ASCII | R | 136314885 |  |  |  |  | 20
|  | Relay Output | Relay1 | R1 Count | R1 Count | 409691 | UINT32 | R | 136314886
|  | Relay Output | Relay1 | R1 Config On Time | R1 Config On Time | 409258 | UINT16 | R | 136314887
|  | Relay Output | Relay1 | R1 Behavioral Mode | R1 Behavioral Mode | 409690 | UINT16 | R | 136314888 |  |  |  | DOBehavioralModes
|  | Relay Output | Relay1 | R1 Control Mode | R1 Control Mode | 409689 | UINT16 | R | 136314889 |  |  |  | DOControlModes
|  | Relay Output | Relay2 | R2 Type | R2 Type | 409259 | UINT16 | R | 136315137 |  |  |  | DOTypes
|  | Relay Output | Relay2 | R2 Status | R2 Status | 409667 | MaskedBool | R | 136315138 | 0x0008
|  | Relay Output | Relay2 | R2 Operating Mode | R2 Operating Mode | 409696 | UINT16 | R | 136315139 |  |  |  | DOOperatingModes
|  | Relay Output | Relay2 | R2 On Time | R2 On Time | 409701 | UINT32 | R | 136315140
|  | Relay Output | Relay2 | R2 Label | R2 Label | 409260 | ASCII | R | 136315141 |  |  |  |  | 20
|  | Relay Output | Relay2 | R2 Count | R2 Count | 409699 | UINT32 | R | 136315142
|  | Relay Output | Relay2 | R2 Control Mode | R2 Control Mode | 409697 | UINT16 | R | 136315143 |  |  |  | DOControlModes
|  | Relay Output | Relay2 | R2 Config On Time | R2 Config On Time | 409282 | UINT16 | R | 136315144
|  | Relay Output | Relay2 | R2 Behavioral Mode | R2 Behavioral Mode | 409698 | UINT16 | R | 136315145 |  |  |  | DOBehavioralModes
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Trigger |  |  |  |  | 137363459
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Period |  |  |  |  | 137363457
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Sync Mode |  |  |  |  | 137363458
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  |  |  |  | 138412033
|  | DataRecorder Modules | Data Rec 1 | RE1 Data Log |  |  |  |  | 139460609
|  | DataRecorder Modules | Data Rec 1 | RE1 Log State |  |  |  |  | 139460610
|  | DataRecorder Modules | Data Rec 1 | RE1 Records Left |  |  |  |  | 139460611
|  | DataRecorder Modules | Data Rec 1 | RE1 Record Complete |  |  |  |  | 139460612
|  | DataRecorder Modules | Data Rec 1 | RE1 Depth |  |  |  |  | 139460613
|  | DataRecorder Modules | Data Rec 1 | RE1 RecordMode |  |  |  |  | 139460614
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Threshold |  |  |  |  | 139460615
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Action |  |  |  |  | 139460616
|  | DataRecorder Modules | Data Rec 2 | RE2 Data Log |  |  |  |  | 139460865
|  | DataRecorder Modules | Data Rec 2 | RE2 Log State |  |  |  |  | 139460866
|  | DataRecorder Modules | Data Rec 2 | RE2 Records Left |  |  |  |  | 139460867
|  | DataRecorder Modules | Data Rec 2 | RE2 Record Complete |  |  |  |  | 139460868
|  | DataRecorder Modules | Data Rec 2 | RE2 Depth |  |  |  |  | 139460869
|  | DataRecorder Modules | Data Rec 2 | RE2 RecordMode |  |  |  |  | 139460870
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Threshold |  |  |  |  | 139460871
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Action |  |  |  |  | 139460872

## PM5100_LE
PM5100_LE Series Translator Details
Data Recorder | Log Interval | ManagerLabel | ModuleLabel | RegisterLabel | Name | ModbusAddr | Format | RequestType | IONHandle | Mask | Scale | Multiplier | EnumName | NumberOfRegisters
|  | Factory Information | Factory 1 | FAC1 DeviceType | FAC1 DeviceType | 400090 | UINT16 | R | 4864 |  |  |  |  | 1
|  | Factory Information | Factory 1 | FAC1 Compliance |  |  |  |  | 4865
|  | Factory Information | Factory 1 | FAC1 Options |  |  |  |  | 4866
|  | Factory Information | Factory 1 | FAC1 Revision | FAC1 Revision | 401637 | UINT16 | R | 4867
|  | Factory Information | Factory 1 | FAC1 SerialNum | FAC1 SerialNum | 400130 | UINT32 | R | 4868 |  |  |  |  | 2
|  | Factory Information | Factory 1 | FAC1 ION Version |  |  |  |  | 30510
|  | Factory Information | Factory 1 | FAC1 Template |  |  |  |  | 4989
|  | Factory Information | Factory 1 | FAC1 Device Name | FAC1 Device Name | 400030 | ASCII | R | 22340 |  |  |  |  | 20
|  | Factory Information | Factory 1 | FAC1 Manuf Date Time | FAC1 Manuf Date Time | 400132 | DateTime3_IEC870_UTC | R | 30129
|  | Factory Information | Factory 1 | FAC1 Hardware Revision | FAC1 Hardware Revision | 400136 | ASCII | R | 30130 |  |  |  |  | 5
|  | Factory Information | Factory 1 | FAC1 FW Rev RS | FAC1 FW Rev RS | 401669 | UINT16 | R | 30131
|  | Alarm - Summary | Alarm Counters | High Priority Counter | High Priority Counter | 413522 | UINT16 | R | 160432388
|  | Alarm - Summary | Alarm Counters | Low Priority Counter | Low Priority Counter | 413520 | UINT16 | R | 160432386
|  | Alarm - Summary | Alarm Counters | Medium Priority Counter | Medium Priority Counter | 413521 | UINT16 | R | 160432387
|  | Alarm - Summary | Alarm Counters | Total Alarms Counter | Total Alarms Counter | 413519 | UINT16 | R | 160432385
|  | Alarm - Summary | Alarm Status | Alarm Active | Alarm Active | 411010 | MaskedBool | R | 160432129 | 0x0001
|  | Alarm - Summary | Alarm Status | High Priority Active | High Priority Active | 411010 | MaskedBool | R | 160432130 | 0x0002
|  | Alarm - Summary | Alarm Status | Low Priority Active | Low Priority Active | 411010 | MaskedBool | R | 160432132 | 0x0008
|  | Alarm - Summary | Alarm Status | Medium Priority Active | Medium Priority Active | 411010 | MaskedBool | R | 160432131 | 0x0004
|  | Alarm - Summary | Alarm Status | Priority None Active | Priority None Active | 411010 | MaskedBool | R | 160432133 | 0x0010
|  | Alarms - Over Under | Over Active Power | Over Active Power Alarm | Over Active Power Alarm | 411059 | MaskedBool | R | 209719297 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Ack Status | Over Active Power-Ack Status | 411078 | MaskedBool | R | 209719298 | 0x0100
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Count | Over Active Power-Alarm Count | 413531 | UINT16 | R | 209719306
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Enabled | Over Active Power-Alarm Enabled | 411040 | MaskedBool | R | 209719299 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Output | Over Active Power-Alarm Output | 414173 | UINT16 | R | 209719305 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Active Power | Over Active Power-Alarm Priority | Over Active Power-Alarm Priority | 414160 | UINT32 | R | 209719300 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Delay | Over Active Power-Dropout Delay | 414171 | UINT32 | R | 209719304
|  | Alarms - Over Under | Over Active Power | Over Active Power-Dropout Setpoint | Over Active Power-Dropout Setpoint | 414169 | F32-4321 | R | 209719303
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Delay | Over Active Power-Pickup Delay | 414167 | UINT32 | R | 209719302
|  | Alarms - Over Under | Over Active Power | Over Active Power-Pickup Setpoint | Over Active Power-Pickup Setpoint | 414165 | F32-4321 | R | 209719301
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power Alarm | Over Apparent Power Alarm | 411059 | MaskedBool | R | 209717249 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Ack Status | Over Apparent Power-Ack Status | 411078 | MaskedBool | R | 209717250 | 0x0400
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Count | Over Apparent Power-Alarm Count | 413533 | UINT16 | R | 209717258
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Enabled | Over Apparent Power-Alarm Enabled | 411040 | MaskedBool | R | 209717251 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Output | Over Apparent Power-Alarm Output | 414213 | UINT16 | R | 209717257 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Alarm Priority | Over Apparent Power-Alarm Priority | 414200 | UINT32 | R | 209717252 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Delay | Over Apparent Power-Dropout Delay | 414211 | UINT32 | R | 209717256
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Dropout Setpoint | Over Apparent Power-Dropout Setpoint | 414209 | F32-4321 | R | 209717255
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Delay | Over Apparent Power-Pickup Delay | 414207 | UINT32 | R | 209717254
|  | Alarms - Over Under | Over Apparent Power | Over Apparent Power-Pickup Setpoint | Over Apparent Power-Pickup Setpoint | 414205 | F32-4321 | R | 209717253
|  | Alarms - Over Under | Over Current N | Over Current Neutral Alarm | Over Current Neutral Alarm | 411059 | MaskedBool | R | 209716481 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Ack Status | Over Current Neutral-Ack Status | 411078 | MaskedBool | R | 209716482 | 0x0004
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Count | Over Current Neutral-Alarm Count | 413525 | UINT16 | R | 209716490
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Enabled | Over Current Neutral-Alarm Enabled | 411040 | MaskedBool | R | 209716483 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Output | Over Current Neutral-Alarm Output | 414053 | UINT16 | R | 209716489 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Alarm Priority | Over Current Neutral-Alarm Priority | 414040 | UINT32 | R | 209716484 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Delay | Over Current Neutral-Dropout Delay | 414051 | UINT32 | R | 209716488
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Dropout Setpoint | Over Current Neutral-Dropout Setpoint | 414049 | F32-4321 | R | 209716487
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Delay | Over Current Neutral-Pickup Delay | 414047 | UINT32 | R | 209716486
|  | Alarms - Over Under | Over Current N | Over Current Neutral-Pickup Setpoint | Over Current Neutral-Pickup Setpoint | 414045 | F32-4321 | R | 209716485
|  | Alarms - Over Under | Over Current Phase | Over Current Phase Alarm | Over Current Phase Alarm | 411059 | MaskedBool | R | 209716737 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Ack Status | Over Current Phase-Ack Status | 411078 | MaskedBool | R | 209716738 | 0x0001
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Count | Over Current Phase-Alarm Count | 413523 | UINT16 | R | 209716746
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Enabled | Over Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209716739 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Output | Over Current Phase-Alarm Output | 414013 | UINT16 | R | 209716745 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Alarm Priority | Over Current Phase-Alarm Priority | 414000 | UINT32 | R | 209716740 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Delay | Over Current Phase-Dropout Delay | 414011 | UINT32 | R | 209716744
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Dropout Setpoint | Over Current Phase-Dropout Setpoint | 414009 | F32-4321 | R | 209716743
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Delay | Over Current Phase-Pickup Delay | 414007 | UINT32 | R | 209716742
|  | Alarms - Over Under | Over Current Phase | Over Current Phase-Pickup Setpoint | Over Current Phase-Pickup Setpoint | 414005 | F32-4321 | R | 209716741
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last Alarm | Over Demand Active Power Last Alarm | 411060 | MaskedBool | R | 209719553 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Ack Status | Over Demand Active Power Last-Ack Status | 411079 | MaskedBool | R | 209719554 | 0x0001
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Count | Over Demand Active Power Last-Alarm Count | 413539 | UINT16 | R | 209719562
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Enabled | Over Demand Active Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209719555 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Output | Over Demand Active Power Last-Alarm Output | 414333 | UINT16 | R | 209719561 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Alarm Priority | Over Demand Active Power Last-Alarm Priority | 414320 | UINT32 | R | 209719556 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Delay | Over Demand Active Power Last-Dropout Delay | 414331 | UINT32 | R | 209719560
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Dropout Setpoint | Over Demand Active Power Last-Dropout Setpoint | 414329 | F32-4321 | R | 209719559
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Delay | Over Demand Active Power Last-Pickup Delay | 414327 | UINT32 | R | 209719558
|  | Alarms - Over Under | Over Demand Active Power Last | Over Demand Active Power Last-Pickup Setpoint | Over Demand Active Power Last-Pickup Setpoint | 414325 | F32-4321 | R | 209719557
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted Alarm | Over Demand Active Power Predicted Alarm | 411060 | MaskedBool | R | 209719809 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Ack Status | Over Demand Active Power Predicted-Ack Status | 411079 | MaskedBool | R | 209719810 | 0x0002
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Count | Over Demand Active Power Predicted-Alarm Count | 413540 | UINT16 | R | 209719818
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Enabled | Over Demand Active Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209719811 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Output | Over Demand Active Power Predicted-Alarm Output | 414353 | UINT16 | R | 209719817 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Alarm Priority | Over Demand Active Power Predicted-Alarm Priority | 414340 | UINT32 | R | 209719812 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Delay | Over Demand Active Power Predicted-Dropout Delay | 414351 | UINT32 | R | 209719816
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Dropout Setpoint | Over Demand Active Power Predicted-Dropout Setpoint | 414349 | F32-4321 | R | 209719815
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Delay | Over Demand Active Power Predicted-Pickup Delay | 414347 | UINT32 | R | 209719814
|  | Alarms - Over Under | Over Demand Active Power Predicted | Over Demand Active Power Predicted-Pickup Setpoint | Over Demand Active Power Predicted-Pickup Setpoint | 414345 | F32-4321 | R | 209719813
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present Alarm | Over Demand Active Power Present Alarm | 411059 | MaskedBool | R | 209720065 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Ack Status | Over Demand Active Power Present-Ack Status | 411078 | MaskedBool | R | 209720066 | 0x8000
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Count | Over Demand Active Power Present-Alarm Count | 413538 | UINT16 | R | 209720074
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Enabled | Over Demand Active Power Present-Alarm Enabled | 411040 | MaskedBool | R | 209720067 | 0x8000 | 32768 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Output | Over Demand Active Power Present-Alarm Output | 414313 | UINT16 | R | 209720073 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Alarm Priority | Over Demand Active Power Present-Alarm Priority | 414300 | UINT32 | R | 209720068 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Delay | Over Demand Active Power Present-Dropout Delay | 414311 | UINT32 | R | 209720072
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Dropout Setpoint | Over Demand Active Power Present-Dropout Setpoint | 414309 | F32-4321 | R | 209720071
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Delay | Over Demand Active Power Present-Pickup Delay | 414307 | UINT32 | R | 209720070
|  | Alarms - Over Under | Over Demand Active Power Present | Over Demand Active Power Present-Pickup Setpoint | Over Demand Active Power Present-Pickup Setpoint | 414305 | F32-4321 | R | 209720069
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last Alarm | Over Demand Apparent Power Last Alarm | 411060 | MaskedBool | R | 209717505 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Ack Status | Over Demand Apparent Power Last-Ack Status | 411079 | MaskedBool | R | 209717506 | 0x0040
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Count | Over Demand Apparent Power Last-Alarm Count | 413545 | UINT16 | R | 209717514
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Enabled | Over Demand Apparent Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209717507 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Output | Over Demand Apparent Power Last-Alarm Output | 414453 | UINT16 | R | 209717513 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Alarm Priority | Over Demand Apparent Power Last-Alarm Priority | 414440 | UINT32 | R | 209717508 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Delay | Over Demand Apparent Power Last-Dropout Delay | 414451 | UINT32 | R | 209717512
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Dropout Setpoint | Over Demand Apparent Power Last-Dropout Setpoint | 414449 | F32-4321 | R | 209717511
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Delay | Over Demand Apparent Power Last-Pickup Delay | 414447 | UINT32 | R | 209717510
|  | Alarms - Over Under | Over Demand Apparent Power Last | Over Demand Apparent Power Last-Pickup Setpoint | Over Demand Apparent Power Last-Pickup Setpoint | 414445 | F32-4321 | R | 209717509
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted Alarm | Over Demand Apparent Power Predicted Alarm | 411060 | MaskedBool | R | 209717761 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Ack Status | Over Demand Apparent Power Predicted-Ack Status | 411079 | MaskedBool | R | 209717762 | 0x0080
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Count | Over Demand Apparent Power Predicted-Alarm Count | 413546 | UINT16 | R | 209717770
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Enabled | Over Demand Apparent Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209717763 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Output | Over Demand Apparent Power Predicted-Alarm Output | 414473 | UINT16 | R | 209717769 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Alarm Priority | Over Demand Apparent Power Predicted-Alarm Priority | 414460 | UINT32 | R | 209717764 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Delay | Over Demand Apparent Power Predicted-Dropout Delay | 414471 | UINT32 | R | 209717768
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Dropout Setpoint | Over Demand Apparent Power Predicted-Dropout Setpoint | 414469 | F32-4321 | R | 209717767
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Delay | Over Demand Apparent Power Predicted-Pickup Delay | 414467 | UINT32 | R | 209717766
|  | Alarms - Over Under | Over Demand Apparent Power Predicted | Over Demand Apparent Power Predicted-Pickup Setpoint | Over Demand Apparent Power Predicted-Pickup Setpoint | 414465 | F32-4321 | R | 209717765
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present Alarm | Over Demand Apparent Power Present Alarm | 411060 | MaskedBool | R | 209718017 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Ack Status | Over Demand Apparent Power Present-Ack Status | 411079 | MaskedBool | R | 209718018 | 0x0020
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Count | Over Demand Apparent Power Present-Alarm Count | 413544 | UINT16 | R | 209718026
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Enabled | Over Demand Apparent Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209718019 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Output | Over Demand Apparent Power Present-Alarm Output | 414433 | UINT16 | R | 209718025 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Alarm Priority | Over Demand Apparent Power Present-Alarm Priority | 414420 | UINT32 | R | 209718020 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Delay | Over Demand Apparent Power Present-Dropout Delay | 414431 | UINT32 | R | 209718024
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Dropout Setpoint | Over Demand Apparent Power Present-Dropout Setpoint | 414429 | F32-4321 | R | 209718023
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Delay | Over Demand Apparent Power Present-Pickup Delay | 414427 | UINT32 | R | 209718022
|  | Alarms - Over Under | Over Demand Apparent Power Present | Over Demand Apparent Power Present-Pickup Setpoint | Over Demand Apparent Power Present-Pickup Setpoint | 414425 | F32-4321 | R | 209718021
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last Alarm | Over Demand Reactive Power Last Alarm | 411060 | MaskedBool | R | 209718529 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Ack Status | Over Demand Reactive Power Last-Ack Status | 411079 | MaskedBool | R | 209718530 | 0x0008
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Count | Over Demand Reactive Power Last-Alarm Count | 413542 | UINT16 | R | 209718538
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Enabled | Over Demand Reactive Power Last-Alarm Enabled | 411041 | MaskedBool | R | 209718531 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Output | Over Demand Reactive Power Last-Alarm Output | 414393 | UINT16 | R | 209718537 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Alarm Priority | Over Demand Reactive Power Last-Alarm Priority | 414380 | UINT32 | R | 209718532 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Delay | Over Demand Reactive Power Last-Dropout Delay | 414391 | UINT32 | R | 209718536
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Dropout Setpoint | Over Demand Reactive Power Last-Dropout Setpoint | 414389 | F32-4321 | R | 209718535
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Delay | Over Demand Reactive Power Last-Pickup Delay | 414387 | UINT32 | R | 209718534
|  | Alarms - Over Under | Over Demand Reactive Power Last | Over Demand Reactive Power Last-Pickup Setpoint | Over Demand Reactive Power Last-Pickup Setpoint | 414385 | F32-4321 | R | 209718533
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted Alarm | Over Demand Reactive Power Predicted Alarm | 411060 | MaskedBool | R | 209718785 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Ack Status | Over Demand Reactive Power Predicted-Ack Status | 411079 | MaskedBool | R | 209718786 | 0x0010
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Count | Over Demand Reactive Power Predicted-Alarm Count | 413543 | UINT16 | R | 209718794
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Enabled | Over Demand Reactive Power Predicted-Alarm Enabled | 411041 | MaskedBool | R | 209718787 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Output | Over Demand Reactive Power Predicted-Alarm Output | 414413 | UINT16 | R | 209718793 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Alarm Priority | Over Demand Reactive Power Predicted-Alarm Priority | 414400 | UINT32 | R | 209718788 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Delay | Over Demand Reactive Power Predicted-Dropout Delay | 414411 | UINT32 | R | 209718792
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Dropout Setpoint | Over Demand Reactive Power Predicted-Dropout Setpoint | 414409 | F32-4321 | R | 209718791
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Delay | Over Demand Reactive Power Predicted-Pickup Delay | 414407 | UINT32 | R | 209718790
|  | Alarms - Over Under | Over Demand Reactive Power Predicted | Over Demand Reactive Power Predicted-Pickup Setpoint | Over Demand Reactive Power Predicted-Pickup Setpoint | 414405 | F32-4321 | R | 209718789
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present Alarm | Over Demand Reactive Power Present Alarm | 411060 | MaskedBool | R | 209719041 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Ack Status | Over Demand Reactive Power Present-Ack Status | 411079 | MaskedBool | R | 209719042 | 0x0004
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Count | Over Demand Reactive Power Present-Alarm Count | 413541 | UINT16 | R | 209719050
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Enabled | Over Demand Reactive Power Present-Alarm Enabled | 411041 | MaskedBool | R | 209719043 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Output | Over Demand Reactive Power Present-Alarm Output | 414373 | UINT16 | R | 209719049 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Alarm Priority | Over Demand Reactive Power Present-Alarm Priority | 414360 | UINT32 | R | 209719044 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Delay | Over Demand Reactive Power Present-Dropout Delay | 414371 | UINT32 | R | 209719048
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Dropout Setpoint | Over Demand Reactive Power Present-Dropout Setpoint | 414369 | F32-4321 | R | 209719047
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Delay | Over Demand Reactive Power Present-Pickup Delay | 414367 | UINT32 | R | 209719046
|  | Alarms - Over Under | Over Demand Reactive Power Present | Over Demand Reactive Power Present-Pickup Setpoint | Over Demand Reactive Power Present-Pickup Setpoint | 414365 | F32-4321 | R | 209719045
|  | Alarms - Over Under | Over Frequency | Over Frequency Alarm | Over Frequency Alarm | 411060 | MaskedBool | R | 209716993 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Ack Status | Over Frequency-Ack Status | 411079 | MaskedBool | R | 209716994 | 0x0100
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Count | Over Frequency-Alarm Count | 413547 | UINT16 | R | 209717002
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Enabled | Over Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209716995 | 0x0100 | 256 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Output | Over Frequency-Alarm Output | 414493 | UINT16 | R | 209717001 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Frequency | Over Frequency-Alarm Priority | Over Frequency-Alarm Priority | 414480 | UINT32 | R | 209716996 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Delay | Over Frequency-Dropout Delay | 414491 | UINT32 | R | 209717000
|  | Alarms - Over Under | Over Frequency | Over Frequency-Dropout Setpoint | Over Frequency-Dropout Setpoint | 414489 | F32-4321 | R | 209716999
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Delay | Over Frequency-Pickup Delay | 414487 | UINT32 | R | 209716998
|  | Alarms - Over Under | Over Frequency | Over Frequency-Pickup Setpoint | Over Frequency-Pickup Setpoint | 414485 | F32-4321 | R | 209716997
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor Alarm | Lagging Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715201 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Ack Status | Lagging Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715202 | 0x4000
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Count | Lagging Displacement Power Factor-Alarm Count | 413537 | UINT16 | R | 209715210
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Enabled | Lagging Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715203 | 0x4000 | 16384 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Output | Lagging Displacement Power Factor-Alarm Output | 414293 | UINT16 | R | 209715209 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Alarm Priority | Lagging Displacement Power Factor-Alarm Priority | 414280 | UINT32 | R | 209715204 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Delay | Lagging Displacement Power Factor-Dropout Delay | 414291 | UINT32 | R | 209715208
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Dropout Setpoint | Lagging Displacement Power Factor-Dropout Setpoint | 414289 | F32-4321 | R | 209715207
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Delay | Lagging Displacement Power Factor-Pickup Delay | 414287 | UINT32 | R | 209715206
|  | Alarms - Over Under | Over Lagging Displacement Power Factor | Lagging Displacement Power Factor-Pickup Setpoint | Lagging Displacement Power Factor-Pickup Setpoint | 414285 | F32-4321 | R | 209715205
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor Alarm | Lagging Power Factor Alarm | 411059 | MaskedBool | R | 209715457 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Ack Status | Lagging Power Factor-Ack Status | 411078 | MaskedBool | R | 209715458 | 0x1000
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Count | Lagging Power Factor-Alarm Count | 413535 | UINT16 | R | 209715466
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Enabled | Lagging Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715459 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Output | Lagging Power Factor-Alarm Output | 414253 | UINT16 | R | 209715465 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Alarm Priority | Lagging Power Factor-Alarm Priority | 414240 | UINT32 | R | 209715460 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Delay | Lagging Power Factor-Dropout Delay | 414251 | UINT32 | R | 209715464
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Dropout Setpoint | Lagging Power Factor-Dropout Setpoint | 414249 | F32-4321 | R | 209715463
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Delay | Lagging Power Factor-Pickup Delay | 414247 | UINT32 | R | 209715462
|  | Alarms - Over Under | Over Lagging Power Factor | Lagging Power Factor-Pickup Setpoint | Lagging Power Factor-Pickup Setpoint | 414245 | F32-4321 | R | 209715461
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor Alarm | Leading Displacement Power Factor Alarm | 411059 | MaskedBool | R | 209715713 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Ack Status | Leading Displacement Power Factor-Ack Status | 411078 | MaskedBool | R | 209715714 | 0x2000
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Count | Leading Displacement Power Factor-Alarm Count | 413536 | UINT16 | R | 209715722
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Enabled | Leading Displacement Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715715 | 0x2000 | 8192 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Output | Leading Displacement Power Factor-Alarm Output | 414273 | UINT16 | R | 209715721 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Alarm Priority | Leading Displacement Power Factor-Alarm Priority | 414260 | UINT32 | R | 209715716 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Delay | Leading Displacement Power Factor-Dropout Delay | 414271 | UINT32 | R | 209715720
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Dropout Setpoint | Leading Displacement Power Factor-Dropout Setpoint | 414269 | F32-4321 | R | 209715719
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Delay | Leading Displacement Power Factor-Pickup Delay | 414267 | UINT32 | R | 209715718
|  | Alarms - Over Under | Over Leading Displacement Power Factor | Leading Displacement Power Factor-Pickup Setpoint | Leading Displacement Power Factor-Pickup Setpoint | 414265 | F32-4321 | R | 209715717
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor Alarm | Leading Power Factor Alarm | 411059 | MaskedBool | R | 209715970 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Ack Status | Leading Power Factor-Ack Status | 411078 | MaskedBool | R | 209715969 | 0x0800
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Count | Leading Power Factor-Alarm Count | 413534 | UINT16 | R | 209715978
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Enabled | Leading Power Factor-Alarm Enabled | 411040 | MaskedBool | R | 209715971 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Output | Leading Power Factor-Alarm Output | 414233 | UINT16 | R | 209715977 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Alarm Priority | Leading Power Factor-Alarm Priority | 414220 | UINT32 | R | 209715972 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Delay | Leading Power Factor-Dropout Delay | 414231 | UINT32 | R | 209715976
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Dropout Setpoint | Leading Power Factor-Dropout Setpoint | 414229 | F32-4321 | R | 209715975
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Delay | Leading Power Factor-Pickup Delay | 414227 | UINT32 | R | 209715974
|  | Alarms - Over Under | Over Leading Power Factor | Leading Power Factor-Pickup Setpoint | Leading Power Factor-Pickup Setpoint | 414225 | F32-4321 | R | 209715973
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power Alarm | Over Reactive Power Alarm | 411059 | MaskedBool | R | 209718273 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Ack Status | Over Reactive Power-Ack Status | 411078 | MaskedBool | R | 209718274 | 0x0200
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Count | Over Reactive Power-Alarm Count | 413532 | UINT16 | R | 209718282
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Enabled | Over Reactive Power-Alarm Enabled | 411040 | MaskedBool | R | 209718275 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Output | Over Reactive Power-Alarm Output | 414193 | UINT16 | R | 209718281 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Alarm Priority | Over Reactive Power-Alarm Priority | 414180 | UINT32 | R | 209718276 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Delay | Over Reactive Power-Dropout Delay | 414191 | UINT32 | R | 209718280
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Dropout Setpoint | Over Reactive Power-Dropout Setpoint | 414189 | F32-4321 | R | 209718279
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Delay | Over Reactive Power-Pickup Delay | 414187 | UINT32 | R | 209718278
|  | Alarms - Over Under | Over Reactive Power | Over Reactive Power-Pickup Setpoint | Over Reactive Power-Pickup Setpoint | 414185 | F32-4321 | R | 209718277
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage Alarm | Over THD Voltage Alarm | 411060 | MaskedBool | R | 209720833 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Ack Status | Over THD Voltage-Ack Status | 411079 | MaskedBool | R | 209720834 | 0x0800
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Count | Over THD Voltage-Alarm Count | 413550 | UINT16 | R | 209720842
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Enabled | Over THD Voltage-Alarm Enabled | 411041 | MaskedBool | R | 209720835 | 0x0800 | 2048 |  | AlarmEnabledState
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Output | Over THD Voltage-Alarm Output | 414553 | UINT16 | R | 209720841 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Alarm Priority | Over THD Voltage-Alarm Priority | 414540 | UINT32 | R | 209720836 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Delay | Over THD Voltage-Dropout Delay | 414551 | UINT32 | R | 209720840
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Dropout Setpoint | Over THD Voltage-Dropout Setpoint | 414549 | F32-4321 | R | 209720839
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Delay | Over THD Voltage-Pickup Delay | 414547 | UINT32 | R | 209720838
|  | Alarms - Over Under | Over THD Voltage | Over THD Voltage-Pickup Setpoint | Over THD Voltage-Pickup Setpoint | 414545 | F32-4321 | R | 209720837
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L Alarm | Over Voltage L-L Alarm | 411059 | MaskedBool | R | 209720321 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Ack Status | Over Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209720322 | 0x0010
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Count | Over Voltage L-L-Alarm Count | 413527 | UINT16 | R | 209720330
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Enabled | Over Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209720323 | 0x0010 | 16 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Output | Over Voltage L-L-Alarm Output | 414093 | UINT16 | R | 209720329 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Alarm Priority | Over Voltage L-L-Alarm Priority | 414080 | UINT32 | R | 209720324 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Delay | Over Voltage L-L-Dropout Delay | 414091 | UINT32 | R | 209720328
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Dropout Setpoint | Over Voltage L-L-Dropout Setpoint | 414089 | F32-4321 | R | 209720327
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Delay | Over Voltage L-L-Pickup Delay | 414087 | UINT32 | R | 209720326
|  | Alarms - Over Under | Over Voltage L-L | Over Voltage L-L-Pickup Setpoint | Over Voltage L-L-Pickup Setpoint | 414085 | F32-4321 | R | 209720325
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N Alarm | Over Voltage L-N Alarm | 411059 | MaskedBool | R | 209720577 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Ack Status | Over Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209720578 | 0x0040
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Count | Over Voltage L-N-Alarm Count | 413529 | UINT16 | R | 209720586
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Enabled | Over Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209720579 | 0x0040 | 64 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Output | Over Voltage L-N-Alarm Output | 414133 | UINT16 | R | 209720585 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Alarm Priority | Over Voltage L-N-Alarm Priority | 414120 | UINT32 | R | 209720580 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Delay | Over Voltage L-N-Dropout Delay | 414131 | UINT32 | R | 209720584
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Dropout Setpoint | Over Voltage L-N-Dropout Setpoint | 414129 | F32-4321 | R | 209720583
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Delay | Over Voltage L-N-Pickup Delay | 414127 | UINT32 | R | 209720582
|  | Alarms - Over Under | Over Voltage L-N | Over Voltage L-N-Pickup Setpoint | Over Voltage L-N-Pickup Setpoint | 414125 | F32-4321 | R | 209720581
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance Alarm | Voltage Unbalance Alarm | 411060 | MaskedBool | R | 209721089 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Ack Status | Voltage Unbalance-Ack Status | 411079 | MaskedBool | R | 209721090 | 0x0400
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Count | Voltage Unbalance-Alarm Count | 413549 | UINT16 | R | 209721098
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Enabled | Voltage Unbalance-Alarm Enabled | 411041 | MaskedBool | R | 209721091 | 0x0400 | 1024 |  | AlarmEnabledState
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Output | Voltage Unbalance-Alarm Output | 414533 | UINT16 | R | 209721097 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Alarm Priority | Voltage Unbalance-Alarm Priority | 414520 | UINT32 | R | 209721092 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Delay | Voltage Unbalance-Dropout Delay | 414531 | UINT32 | R | 209721096
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Dropout Setpoint | Voltage Unbalance-Dropout Setpoint | 414529 | F32-4321 | R | 209721095
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Delay | Voltage Unbalance-Pickup Delay | 414527 | UINT32 | R | 209721094
|  | Alarms - Over Under | Over Voltage Unbalance | Voltage Unbalance-Pickup Setpoint | Voltage Unbalance-Pickup Setpoint | 414525 | F32-4321 | R | 209721093
|  | Alarms - Over Under | Phase Loss | Phase Loss Alarm | Phase Loss Alarm | 411060 | MaskedBool | R | 209721345 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Ack Status | Phase Loss-Ack Status | 411079 | MaskedBool | R | 209721346 | 0x1000
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Count | Phase Loss-Alarm Count | 413551 | UINT16 | R | 209721354
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Enabled | Phase Loss-Alarm Enabled | 411041 | MaskedBool | R | 209721347 | 0x1000 | 4096 |  | AlarmEnabledState
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Output | Phase Loss-Alarm Output | 414573 | UINT16 | R | 209721353 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Phase Loss | Phase Loss-Alarm Priority | Phase Loss-Alarm Priority | 414560 | UINT32 | R | 209721348 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Delay | Phase Loss-Dropout Delay | 414571 | UINT32 | R | 209721352
|  | Alarms - Over Under | Phase Loss | Phase Loss-Dropout Setpoint | Phase Loss-Dropout Setpoint | 414569 | F32-4321 | R | 209721351
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Delay | Phase Loss-Pickup Delay | 414567 | UINT32 | R | 209721350
|  | Alarms - Over Under | Phase Loss | Phase Loss-Pickup Setpoint | Phase Loss-Pickup Setpoint | 414565 | F32-4321 | R | 209721349
|  | Alarms - Over Under | Under Current Phase | Under Current Phase Alarm | Under Current Phase Alarm | 411059 | MaskedBool | R | 209721601 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Ack Status | Under Current Phase-Ack Status | 411078 | MaskedBool | R | 209721602 | 0x0002
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Count | Under Current Phase-Alarm Count | 413524 | UINT16 | R | 209721610
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Enabled | Under Current Phase-Alarm Enabled | 411040 | MaskedBool | R | 209721603 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Output | Under Current Phase-Alarm Output | 414033 | UINT16 | R | 209721609 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Alarm Priority | Under Current Phase-Alarm Priority | 414020 | UINT32 | R | 209721604 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Delay | Under Current Phase-Dropout Delay | 414031 | UINT32 | R | 209721608
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Dropout Setpoint | Under Current Phase-Dropout Setpoint | 414029 | F32-4321 | R | 209721607
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Delay | Under Current Phase-Pickup Delay | 414027 | UINT32 | R | 209721606
|  | Alarms - Over Under | Under Current Phase | Under Current Phase-Pickup Setpoint | Under Current Phase-Pickup Setpoint | 414025 | F32-4321 | R | 209721605
|  | Alarms - Over Under | Under Frequency | Under Frequency Alarm | Under Frequency Alarm | 411060 | MaskedBool | R | 209721857 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Ack Status | Under Frequency-Ack Status | 411079 | MaskedBool | R | 209721858 | 0x0200
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Count | Under Frequency-Alarm Count | 413548 | UINT16 | R | 209721866
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Enabled | Under Frequency-Alarm Enabled | 411041 | MaskedBool | R | 209721859 | 0x0200 | 512 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Output | Under Frequency-Alarm Output | 414513 | UINT16 | R | 209721865 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Frequency | Under Frequency-Alarm Priority | Under Frequency-Alarm Priority | 414500 | UINT32 | R | 209721860 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Delay | Under Frequency-Dropout Delay | 414511 | UINT32 | R | 209721864
|  | Alarms - Over Under | Under Frequency | Under Frequency-Dropout Setpoint | Under Frequency-Dropout Setpoint | 414509 | F32-4321 | R | 209721863
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Delay | Under Frequency-Pickup Delay | 414507 | UINT32 | R | 209721862
|  | Alarms - Over Under | Under Frequency | Under Frequency-Pickup Setpoint | Under Frequency-Pickup Setpoint | 414505 | F32-4321 | R | 209721861
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L Alarm | Under Voltage L-L Alarm | 411059 | MaskedBool | R | 209722113 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Ack Status | Under Voltage L-L-Ack Status | 411078 | MaskedBool | R | 209722114 | 0x0020
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Count | Under Voltage L-L-Alarm Count | 413528 | UINT16 | R | 209722122
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Enabled | Under Voltage L-L-Alarm Enabled | 411040 | MaskedBool | R | 209722115 | 0x0020 | 32 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Output | Under Voltage L-L-Alarm Output | 414113 | UINT16 | R | 209722121 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Alarm Priority | Under Voltage L-L-Alarm Priority | 414100 | UINT32 | R | 209722116 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Delay | Under Voltage L-L-Dropout Delay | 414111 | UINT32 | R | 209722120
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Dropout Setpoint | Under Voltage L-L-Dropout Setpoint | 414109 | F32-4321 | R | 209722119
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Delay | Under Voltage L-L-Pickup Delay | 414107 | UINT32 | R | 209722118
|  | Alarms - Over Under | Under Voltage L-L | Under Voltage L-L-Pickup Setpoint | Under Voltage L-L-Pickup Setpoint | 414105 | F32-4321 | R | 209722117
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N Alarm | Under Voltage L-N Alarm | 411059 | MaskedBool | R | 209722369 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Ack Status | Under Voltage L-N-Ack Status | 411078 | MaskedBool | R | 209722370 | 0x0080
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Count | Under Voltage L-N-Alarm Count | 413530 | UINT16 | R | 209722378
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Enabled | Under Voltage L-N-Alarm Enabled | 411040 | MaskedBool | R | 209722371 | 0x0080 | 128 |  | AlarmEnabledState
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Output | Under Voltage L-N-Alarm Output | 414153 | UINT16 | R | 209722377 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Alarm Priority | Under Voltage L-N-Alarm Priority | 414140 | UINT32 | R | 209722372 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Delay | Under Voltage L-N-Dropout Delay | 414151 | UINT32 | R | 209722376
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Dropout Setpoint | Under Voltage L-N-Dropout Setpoint | 414149 | F32-4321 | R | 209722375
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Delay | Under Voltage L-N-Pickup Delay | 414147 | UINT32 | R | 209722374
|  | Alarms - Over Under | Under Voltage L-N | Under Voltage L-N-Pickup Setpoint | Under Voltage L-N-Pickup Setpoint | 414145 | F32-4321 | R | 209722373
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic Alarm | Meter Diagnostic Alarm | 411069 | MaskedBool | R | 208666625 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Ack Status | Meter Diagnostic-Ack Status | 411088 | MaskedBool | R | 208666626 | 0x0004
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Count | Meter Diagnostic-Alarm Count | 413625 | UINT16 | R | 208666630
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Enabled | Meter Diagnostic-Alarm Enabled | 411050 | MaskedBool | R | 208666627 | 0x0004 | 4 |  | AlarmEnabledState
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Output | Meter Diagnostic-Alarm Output | 416222 | UINT16 | R | 208666629 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Unary | Meter Diagnostic | Meter Diagnostic-Alarm Priority | Meter Diagnostic-Alarm Priority | 416220 | UINT32 | R | 208666628 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Unary | Meter Power Up | Meter Power Up Alarm | Meter Power Up Alarm | 411069 | MaskedBool | R | 208666881 | 0x0001
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Ack Status | Meter Power Up-Ack Status | 411088 | MaskedBool | R | 208666882 | 0x0001
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Count | Meter Power Up-Alarm Count | 413623 | UINT16 | R | 208666886
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Enabled | Meter Power Up-Alarm Enabled | 411050 | MaskedBool | R | 208666883 | 0x0001 |  |  | AlarmEnabledState
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Output | Meter Power Up-Alarm Output | 416202 | UINT16 | R | 208666885 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Unary | Meter Power Up | Meter Power Up-Alarm Priority | Meter Power Up-Alarm Priority | 416200 | UINT32 | R | 208666884 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Unary | Meter Reset | Meter Reset Alarm | Meter Reset Alarm | 411069 | MaskedBool | R | 208667137 | 0x0002
|  | Alarms - Unary | Meter Reset | Meter Reset-Ack Status | Meter Reset-Ack Status | 411088 | MaskedBool | R | 208667138 | 0x0002
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Count | Meter Reset-Alarm Count | 413624 | UINT16 | R | 208667142
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Enabled | Meter Reset-Alarm Enabled | 411050 | MaskedBool | R | 208667139 | 0x0002 | 2 |  | AlarmEnabledState
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Output | Meter Reset-Alarm Output | 416212 | UINT16 | R | 208667141 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Unary | Meter Reset | Meter Reset-Alarm Priority | Meter Reset-Alarm Priority | 416210 | UINT32 | R | 208667140 | 0x0018 | 8 |  | AlarmPriority
|  | Alarms - Unary | Phase Reversal | Phase Reversal Alarm | Phase Reversal Alarm | 411069 | MaskedBool | R | 208667393 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Ack Status | Phase Reversal-Ack Status | 411088 | MaskedBool | R | 208667394 | 0x0008
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Count | Phase Reversal-Alarm Count | 413626 | UINT16 | R | 208667398
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Enabled | Phase Reversal-Alarm Enabled | 411050 | MaskedBool | R | 208667395 | 0x0008 | 8 |  | AlarmEnabledState
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Output | Phase Reversal-Alarm Output | 416232 | UINT16 | R | 208667397 |  |  |  | AlarmDigitalOutputs
|  | Alarms - Unary | Phase Reversal | Phase Reversal-Alarm Priority | Phase Reversal-Alarm Priority | 416230 | UINT32 | R | 208667396 | 0x0018 | 8 |  | AlarmPriority
|  | Clocks | Clock | CL1 Day | CL1 Day | 401839 | UINT16 | R | 23424 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Hour | CL1 Hour | 401840 | UINT16 | R | 23425 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Local Time | CL1 Local Time | 401845 | DateTime3_IEC870_UTC | R | 23421 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Millisecond | CL1 Millisecond | 401843 | UINT16 | R | 23428 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Minute | CL1 Minute | 401841 | UINT16 | R | 23426 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Month | CL1 Month | 401838 | UINT16 | R | 23423 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Second | CL1 Second | 401842 | UINT16 | R | 23427 |  |  |  |  | 1
|  | Clocks | Clock | CL1 Universal Time | CL1 Universal Time | 401845 | DateTime3_IEC870_LOCAL | R | 23420 |  |  |  |  | 4
|  | Clocks | Clock | CL1 Year | CL1 Year | 401837 | UINT16 | R | 23422 |  |  |  |  | 1
DR1 | 900 | Currents | Current | Current A | Current A | 403000 | F32-4321 | R | 164626433 |  |  |  |  | 2
DR1 | 900 | Currents | Current | Current Avg | Current Avg | 403010 | F32-4321 | R | 164626439 |  |  |  |  | 2
DR1 | 900 | Currents | Current | Current B | Current B | 403002 | F32-4321 | R | 164626434 |  |  |  |  | 2
DR1 | 900 | Currents | Current | Current C | Current C | 403004 | F32-4321 | R | 164626435 |  |  |  |  | 2
|  | Currents | Current | Current N | Current N | 403006 | F32-4321 | R | 164626436 |  |  |  |  | 2
|  | Currents | Current | Current G | Current G | 403008 | F32-4321 | R | 164626437
DR2 | 900 | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power | Demand Apparent Power | 403796 | F32-4321 | R | 254143233
|  | Demand Readings and History | Demand Apparent Power Total | Demand Apparent Power (KVAD) - Present | Demand Apparent Power (KVAD) - Present | 403798 | F32-4321 | R | 254143234
|  | Demand Readings and History | Demand Apparent Power Total | DT Peak Demand Apparent Power | DT Peak Demand Apparent Power | 403804 | DateTime3_IEC870_UTC | R | 166724630
|  | Demand Readings and History | Demand Apparent Power Total | Peak Demand Apparent Power | Peak Demand Apparent Power | 403802 | F32-4321 | R | 254143236
|  | Demand Readings and History | Demand Apparent Power Total | Predicted KVA Demand | Predicted KVA Demand | 403800 | F32-4321 | R | 254143235
DR2 | 900 | Demand Readings and History | Demand Current Avg | Demand Current Avg | Demand Current Avg | 403876 | F32-4321 | R | 254145025
|  | Demand Readings and History | Demand Current Avg | Demand Current Avg - Present | Demand Current Avg - Present | 403878 | F32-4321 | R | 254145026
|  | Demand Readings and History | Demand Current Avg | DT Peak Demand Current Avg | DT Peak Demand Current Avg | 403884 | DateTime3_IEC870_UTC | R | 166724877
|  | Demand Readings and History | Demand Current Avg | Peak Demand Current Avg | Peak Demand Current Avg | 403882 | F32-4321 | R | 254145028
|  | Demand Readings and History | Demand Current Avg | Predicted Demand Current Avg | Predicted Demand Current Avg | 403880 | F32-4321 | R | 254145027
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method | Current Demand Calculation Method | 403711 | UINT16 | R | 166723841
|  | Demand Readings and History | Demand Current Calculation | Current Demand Calculation Method Code | Current Demand Calculation Method Code | 403711 | UINT16 | R | 166723847
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Interval | Current Demand Elapsed Time in Interval | 403714 | UINT16 | R | 166723844
|  | Demand Readings and History | Demand Current Calculation | Current Demand Elapsed Time in Subinterval | Current Demand Elapsed Time in Subinterval | 403715 | UINT16 | R | 166723845
|  | Demand Readings and History | Demand Current Calculation | Current Demand Interval | Current Demand Interval | 403712 | UINT16 | R | 166723842
|  | Demand Readings and History | Demand Current Calculation | Current Demand Sub-Interval | Current Demand Sub-Interval | 403713 | UINT16 | R | 166723843
|  | Demand Readings and History | Demand Current Calculation | DT Last Reset Peak Dmd Currents | DT Last Reset Peak Dmd Currents | 403716 | DateTime3_IEC870_UTC | R | 166723846
|  | Demand Readings and History | Demand Power Calculation | DT Last Reset Peak Dmd Power | DT Last Reset Peak Dmd Power | 403706 | DateTime3_IEC870_UTC | R | 166723597
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method | Power Demand Calculation Method | 403701 | UINT16 | R | 166723593
|  | Demand Readings and History | Demand Power Calculation | Power Demand Calculation Method Code | Power Demand Calculation Method Code | 403701 | UINT16 | R | 166723596
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Interval | Power Demand Elapsed Time in Interval | 403704 | UINT16 | R | 166723594
|  | Demand Readings and History | Demand Power Calculation | Power Demand Elapsed Time in Subinterval | Power Demand Elapsed Time in Subinterval | 403705 | UINT16 | R | 166723595
|  | Demand Readings and History | Demand Power Calculation | Power Demand Interval | Power Demand Interval | 403702 | UINT16 | R | 166723591
|  | Demand Readings and History | Demand Power Calculation | Power Demand Sub-Interval | Power Demand Sub-Interval | 403703 | UINT16 | R | 166723592
DR2 | 900 | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power | Demand Reactive Power | 403780 | F32-4321 | R | 254142209
|  | Demand Readings and History | Demand Reactive Power Total | Demand Reactive Power (KVARD) - Present | Demand Reactive Power (KVARD) - Present | 403782 | F32-4321 | R | 254142210
|  | Demand Readings and History | Demand Reactive Power Total | DT Peak Demand Reactive Power | DT Peak Demand Reactive Power | 403788 | DateTime3_IEC870_UTC | R | 166724629
|  | Demand Readings and History | Demand Reactive Power Total | Peak Demand Reactive Power | Peak Demand Reactive Power | 403786 | F32-4321 | R | 254142212
|  | Demand Readings and History | Demand Reactive Power Total | Predicted KVAR Demand | Predicted KVAR Demand | 403784 | F32-4321 | R | 254142211
DR2 | 900 | Demand Readings and History | Demand Real Power Total | Demand Real Power | Demand Real Power | 403764 | F32-4321 | R | 254141185
|  | Demand Readings and History | Demand Real Power Total | Demand Real Power (KWD) - Present | Demand Real Power (KWD) - Present | 403766 | F32-4321 | R | 254141186
|  | Demand Readings and History | Demand Real Power Total | DT Peak Demand Real Power | DT Peak Demand Real Power | 403772 | DateTime3_IEC870_UTC | R | 166724628
|  | Demand Readings and History | Demand Real Power Total | Peak Demand Real Power | Peak Demand Real Power | 403770 | F32-4321 | R | 254141188
|  | Demand Readings and History | Demand Real Power Total | Predicted KW Demand | Predicted KW Demand | 403768 | F32-4321 | R | 254141187
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Digital Output Association | EPO1 Digital Output Association | 402131 | UINT16 | R | 205522439 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Energy Channel | EPO1 Energy Channel | 402130 | UINT16 | R | 205522438 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 1 | EPO1 Pulse Weight | EPO1 Pulse Weight | 402132 | UINT32 | R | 205522437
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Digital Output Association | EPO2 Digital Output Association | 402135 | UINT16 | R | 205522690 |  |  |  | EPDIOAssoc
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Energy Channel | EPO2 Energy Channel | 402134 | UINT16 | R | 205522689 |  |  |  | EPChannel
|  | Digital Input Output | Energy Pulse Output 2 | EPO2 Pulse Weight | EPO2 Pulse Weight | 402136 | UINT32 | R | 205522691
|  | Power Meters | Power Meter | PM1 CT Count | PM1 CT Count | 402029 | UINT16 | R | 65555 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Location | PM1 CT Location | 402034 | UINT16 | R | 65554 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Current | PM1 Nominal Current | 402020 | F32-4321 | R | 65544 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Frequency | PM1 Nominal Frequency | 402017 | UINT16 | R | 65542
|  | Power Meters | Power Meter | PM1 Nominal Phase Rotation | PM1 Nominal Phase Rotation | 402024 | UINT16 | R | 65547 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Nominal Power Factor | PM1 Nominal Power Factor | 402022 | PF32 | R | 65545 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Power Factor Load Direction | PM1 Nominal Power Factor Load Direction | 402022 | F32-4321 | R | 65548 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 Nominal Voltage | PM1 Nominal Voltage | 402018 | F32-4321 | R | 65543 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Connection Type | PM1 VT Connection Type | 402036 | UINT16 | R | 65541 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Count | PM1 VT Count | 402025 | UINT16 | R | 65552 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Location | PM1 VT Location | 402035 | UINT16 | R | 65553 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 Volts Mode | PM1 Volts Mode | 402016 | UINT16 | R | 30720 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Primary | PM1 CT Primary | 402030 | UINT16 | R | 65539 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 CT Secondary | PM1 CT Secondary | 402031 | UINT16 | R | 65540 |  |  |  |  | 1
|  | Power Meters | Power Meter | PM1 VT Primary | PM1 VT Primary | 402026 | F32-4321 | R | 65537 |  |  |  |  | 2
|  | Power Meters | Power Meter | PM1 VT Secondary | PM1 VT Secondary | 402028 | UINT16 | R | 65538 |  |  |  |  | 1
|  | Diagnostics | Meter | Calibration Error | Calibration Error | 420007 | MaskedBool | R | 157286669 | 0x0010
|  | Diagnostics | Meter | Cause of Last Meter Reset | Cause of Last Meter Reset | 401836 | UINT16 | R | 157286668
|  | Diagnostics | Meter | Clipping Detected | Clipping Detected | 420007 | MaskedBool | R | 157286662 | 0x0020
|  | Diagnostics | Meter | Control Power Outage Counter | Control Power Outage Counter | 401829 | UINT16 | R | 157286670
|  | Diagnostics | Meter | DT Last Control Power Outage | DT Last Control Power Outage | 401830 | DateTime3_IEC870_UTC | R | 157286671
|  | Diagnostics | Meter | DT Last Unit Restart | DT Last Unit Restart | 401824 | DateTime3_IEC870_UTC | R | 157286664
|  | Diagnostics | Meter | Meter Error Detected | Meter Error Detected | 420007 | MaskedBool | R | 157286657 | 0x0001
|  | Diagnostics | Meter | Metering System Restart Counter | Metering System Restart Counter | 401828 | UINT16 | R | 157286665
|  | Diagnostics | Meter | NVRAM Error | NVRAM Error | 420007 | MaskedBool | R | 157286672 | 0x0004
|  | Diagnostics | Meter | Over Run Energy Pulse Output | Over Run Energy Pulse Output | 420007 | MaskedBool | R | 157286663 | 0x0040
|  | Diagnostics | Meter | RAM Error | RAM Error | 420007 | MaskedBool | R | 157286673 | 0x0002
|  | Diagnostics | Meter | RTC Error | RTC Error | 420007 | MaskedBool | R | 157286674 | 0x0008
DR1 | 900 | Energies | Apparent Energy | Apparent Energy | Apparent Energy | 403244 | S64-87-21 | R | 256238595 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Delivered-Received | Apparent Energy Delivered-Received | 403248 | S64-87-21 | R | 256238596 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Into the Load | Apparent Energy Into the Load | 403236 | S64-87-21 | R | 256238593 |  | 1000
|  | Energies | Apparent Energy | Apparent Energy Out of the Load | Apparent Energy Out of the Load | 403240 | S64-87-21 | R | 256238594 |  | 1000
|  | Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | DT Last Reset Accum Energies | 403200 | DateTime3_IEC870_UTC | R | 169869321
|  | Energies | Reactive Energy | Reactive Energy Absolute | Reactive Energy Absolute | 403228 | S64-87-21 | R | 256238339 |  | 1000
DR1 | 900 | Energies | Reactive Energy | Reactive Energy Into the Load | Reactive Energy Into the Load | 403220 | S64-87-21 | R | 256238337 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Out of the Load | Reactive Energy Out of the Load | 403224 | S64-87-21 | R | 256238338 |  | 1000
|  | Energies | Reactive Energy | Reactive Energy Signed | Reactive Energy Signed | 403232 | S64-87-21 | R | 256238340 |  | 1000
|  | Energies | Real Energy | Real Energy Absolute | Real Energy Absolute | 403212 | S64-87-21 | R | 256238083 |  | 1000
DR1 | 900 | Energies | Real Energy | Real Energy Into the Load | Real Energy Into the Load | 403204 | S64-87-21 | R | 256238081 |  | 1000
|  | Energies | Real Energy | Real Energy Out of the Load | Real Energy Out of the Load | 403208 | S64-87-21 | R | 256238082 |  | 1000
|  | Energies | Real Energy | Real Energy Signed | Real Energy Signed | 403216 | S64-87-21 | R | 256238084 |  | 1000
|  | Maximum Readings | Max Current | Max Current A | Max Current A | 427694 | F32-4321 | R | 177209601 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current Avg | Max Current Avg | 427704 | F32-4321 | R | 177209607 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current B | Max Current B | 427696 | F32-4321 | R | 177209602 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current C | Max Current C | 427698 | F32-4321 | R | 177209604 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current N | Max Current N | 427700 | F32-4321 | R | 177209603 |  |  |  |  | 2
|  | Maximum Readings | Max Current | Max Current G | Max Current G | 427702 | F32-4321 | R | 177209605
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance A | Max Current Unbalance A | 427706 | F32-4321 | R | 177209857 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance B | Max Current Unbalance B | 427708 | F32-4321 | R | 177209858 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance C | Max Current Unbalance C | 427710 | F32-4321 | R | 177209859 |  |  |  |  | 2
|  | Maximum Readings | Max Current Unbalance | Max Current Unbalance Worst | Max Current Unbalance Worst | 427712 | F32-4321 | R | 177209860 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A | Max Displacement Power Factor A | 427790 | PF32 | R | 177210113 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor A | Max Displacement Power Factor A Load Direction | Max Displacement Power Factor A Load Direction | 427790 | F32-4321 | R | 177210114 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B | Max Displacement Power Factor B | 427792 | PF32 | R | 177210369 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor B | Max Displacement Power Factor B Load Direction | Max Displacement Power Factor B Load Direction | 427792 | F32-4321 | R | 177210370 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C | Max Displacement Power Factor C | 427794 | PF32 | R | 177210625 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor C | Max Displacement Power Factor C Load Direction | Max Displacement Power Factor C Load Direction | 427794 | F32-4321 | R | 177210626 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total | Max Displacement Power Factor Total | 427796 | PF32 | R | 177211137 |  |  |  |  | 2
|  | Maximum Readings | Max Displacement Power Factor Total | Max Displacement Power Factor Total Load Direction | Max Displacement Power Factor Total Load Direction | 427796 | F32-4321 | R | 177211138 |  |  |  |  | 2
|  | Maximum Readings | Max Frequency | Max Frequency | Max Frequency | 428092 | F32-4321 | R | 177210881 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power A | Max Apparent Power A | 427764 | F32-4321 | R | 177213449 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power B | Max Apparent Power B | 427766 | F32-4321 | R | 177213450 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power C | Max Apparent Power C | 427768 | F32-4321 | R | 177213451 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Apparent Power Total | Max Apparent Power Total | 427770 | F32-4321 | R | 177213452 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power A | Max Reactive Power A | 427756 | F32-4321 | R | 177213445 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power B | Max Reactive Power B | 427758 | F32-4321 | R | 177213446 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power C | Max Reactive Power C | 427760 | F32-4321 | R | 177213447 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Reactive Power Total | Max Reactive Power Total | 427762 | F32-4321 | R | 177213448 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power A | Max Real Power A | 427748 | F32-4321 | R | 177213441 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power B | Max Real Power B | 427750 | F32-4321 | R | 177213442 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power C | Max Real Power C | 427752 | F32-4321 | R | 177213443 |  |  |  |  | 2
|  | Maximum Readings | Max Power | Max Real Power Total | Max Real Power Total | 427754 | F32-4321 | R | 177213444 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A | Max Power Factor A | 427782 | PF32 | R | 177211393 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor A | Max Power Factor A Load Direction | Max Power Factor A Load Direction | 427782 | F32-4321 | R | 177211394 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B | Max Power Factor B | 427784 | PF32 | R | 177211649 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor B | Max Power Factor B Load Direction | Max Power Factor B Load Direction | 427784 | F32-4321 | R | 177211650 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C | Max Power Factor C | 427786 | PF32 | R | 177211905 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor C | Max Power Factor C Load Direction | Max Power Factor C Load Direction | 427786 | F32-4321 | R | 177211906 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total | Max Power Factor Total | 427788 | PF32 | R | 177212161 |  |  |  |  | 2
|  | Maximum Readings | Max Power Factor Total | Max Power Factor Total Load Direction | Max Power Factor Total Load Direction | 427788 | F32-4321 | R | 177212162 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current A | Max THD Current A | 427814 | F32-4321 | R | 177214466 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current B | Max THD Current B | 427816 | F32-4321 | R | 177214467 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current C | Max THD Current C | 427818 | F32-4321 | R | 177214468 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current N | Max THD Current N | 427820 | F32-4321 | R | 177214469 |  |  |  |  | 2
|  | Maximum Readings | Max THD Current | Max THD Current G | Max THD Current G | 427822 | F32-4321 | R | 177214465
|  | Maximum Readings | Max thd Current | Max thd_Current A | Max thd_Current A | 427824 | F32-4321 | R | 177214209 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current B | Max thd_Current B | 427826 | F32-4321 | R | 177214210 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current C | Max thd_Current C | 427828 | F32-4321 | R | 177214211 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current N | Max thd_Current N | 427830 | F32-4321 | R | 177214212 |  |  |  |  | 2
|  | Maximum Readings | Max thd Current | Max thd_Current G | Max thd_Current G | 427832 | F32-4321 | R | 177214213
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-B | Max THD Voltage A-B | 427836 | F32-4321 | R | 177214977 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage A-N | Max THD Voltage A-N | 427844 | F32-4321 | R | 177214984 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-C | Max THD Voltage B-C | 427838 | F32-4321 | R | 177214978 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage B-N | Max THD Voltage B-N | 427846 | F32-4321 | R | 177214985 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-A | Max THD Voltage C-A | 427840 | F32-4321 | R | 177214979 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage C-N | Max THD Voltage C-N | 427848 | F32-4321 | R | 177214986 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-L | Max THD Voltage L-L | 427842 | F32-4321 | R | 177214980 |  |  |  |  | 2
|  | Maximum Readings | Max THD Voltage | Max THD Voltage L-N | Max THD Voltage L-N | 427852 | F32-4321 | R | 177214987 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-B | Max thd_Voltage A-B | 427854 | F32-4321 | R | 177214721 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage A-N | Max thd_Voltage A-N | 427862 | F32-4321 | R | 177214724 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-C | Max thd_Voltage B-C | 427856 | F32-4321 | R | 177214722 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage B-N | Max thd_Voltage B-N | 427864 | F32-4321 | R | 177214725 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-A | Max thd_Voltage C-A | 427858 | F32-4321 | R | 177214723 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage C-N | Max thd_Voltage C-N | 427866 | F32-4321 | R | 177214726 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-L | Max thd_Voltage L-L | 427860 | F32-4321 | R | 177214727 |  |  |  |  | 2
|  | Maximum Readings | Max thd Voltage | Max thd_Voltage L-N | Max thd_Voltage L-N | 427870 | F32-4321 | R | 177214728 |  |  |  |  | 2
|  | Maximum Readings | Max Total Demand Distortion | Max Total Demand Distortion | Max Total Demand Distortion | 427834 | F32-4321 | R | 177209345 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-B | Max Voltage A-B | 427714 | F32-4321 | R | 177215489 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage A-N | Max Voltage A-N | 427722 | F32-4321 | R | 177215497 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-C | Max Voltage B-C | 427716 | F32-4321 | R | 177215490 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage B-N | Max Voltage B-N | 427724 | F32-4321 | R | 177215498 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-A | Max Voltage C-A | 427718 | F32-4321 | R | 177215491 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage C-N | Max Voltage C-N | 427726 | F32-4321 | R | 177215499 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-L Avg | Max Voltage L-L Avg | 427720 | F32-4321 | R | 177215493 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage | Max Voltage L-N Avg | Max Voltage L-N Avg | 427730 | F32-4321 | R | 177215501 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-B | Max Voltage Unbalance A-B | 427732 | F32-4321 | R | 177215745 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance A-N | Max Voltage Unbalance A-N | 427740 | F32-4321 | R | 177215753 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-C | Max Voltage Unbalance B-C | 427734 | F32-4321 | R | 177215746 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance B-N | Max Voltage Unbalance B-N | 427742 | F32-4321 | R | 177215754 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-A | Max Voltage Unbalance C-A | 427736 | F32-4321 | R | 177215747 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance C-N | Max Voltage Unbalance C-N | 427744 | F32-4321 | R | 177215755 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-L Worst | Max Voltage Unbalance L-L Worst | 427738 | F32-4321 | R | 177215748 |  |  |  |  | 2
|  | Maximum Readings | Max Voltage Unbalance | Max Voltage Unbalance L-N Worst | Max Voltage Unbalance L-N Worst | 427746 | F32-4321 | R | 177215756 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current A | Min Current A | 427218 | F32-4321 | R | 178258178 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current Avg | Min Current Avg | 427228 | F32-4321 | R | 178258183 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current B | Min Current B | 427220 | F32-4321 | R | 178258179 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current C | Min Current C | 427222 | F32-4321 | R | 178258180 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current N | Min Current N | 427224 | F32-4321 | R | 178258181 |  |  |  |  | 2
|  | Minimum Readings | Min Current | Min Current G | Min Current G | 427226 | F32-4321 | R | 178258177 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance A | Min Current Unbalance A | 427230 | F32-4321 | R | 178258433 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance B | Min Current Unbalance B | 427232 | F32-4321 | R | 178258434 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance C | Min Current Unbalance C | 427234 | F32-4321 | R | 178258435 |  |  |  |  | 2
|  | Minimum Readings | Min Current Unbalance | Min Current Unbalance Worst | Min Current Unbalance Worst | 427236 | F32-4321 | R | 178258436 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A | Min Displacement Power Factor A | 427314 | PF32 | R | 178258689 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor A | Min Displacement Power Factor A Load Direction | Min Displacement Power Factor A Load Direction | 427314 | F32-4321 | R | 178258690 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B | Min Displacement Power Factor B | 427316 | PF32 | R | 178258945 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor B | Min Displacement Power Factor B Load Direction | Min Displacement Power Factor B Load Direction | 427316 | F32-4321 | R | 178258946 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C | Min Displacement Power Factor C | 427318 | PF32 | R | 178259201 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor C | Min Displacement Power Factor C Load Direction | Min Displacement Power Factor C Load Direction | 427318 | F32-4321 | R | 178259202 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total | Min Displacement Power Factor Total | 427320 | PF32 | R | 178259713 |  |  |  |  | 2
|  | Minimum Readings | Min Displacement Power Factor Total | Min Displacement Power Factor Total Load Direction | Min Displacement Power Factor Total Load Direction | 427320 | F32-4321 | R | 178259714 |  |  |  |  | 2
|  | Minimum Readings | Min Frequency | Min Frequency | Min Frequency | 427616 | F32-4321 | R | 178259457 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power A | Min Apparent Power A | 427288 | F32-4321 | R | 178262017 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power B | Min Apparent Power B | 427290 | F32-4321 | R | 178262018 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power C | Min Apparent Power C | 427292 | F32-4321 | R | 178262019 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Apparent Power Total | Min Apparent Power Total | 427294 | F32-4321 | R | 178262020 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power A | Min Reactive Power A | 427280 | F32-4321 | R | 178262022 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power B | Min Reactive Power B | 427282 | F32-4321 | R | 178262023 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power C | Min Reactive Power C | 427284 | F32-4321 | R | 178262024 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Reactive Power Total | Min Reactive Power Total | 427286 | F32-4321 | R | 178262025 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power A | Min Real Power A | 427272 | F32-4321 | R | 178262027 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power B | Min Real Power B | 427274 | F32-4321 | R | 178262028 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power C | Min Real Power C | 427276 | F32-4321 | R | 178262029 |  |  |  |  | 2
|  | Minimum Readings | Min Power | Min Real Power Total | Min Real Power Total | 427278 | F32-4321 | R | 178262030 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A | Min Power Factor A | 427306 | PF32 | R | 178259969 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor A | Min Power Factor A Load Direction | Min Power Factor A Load Direction | 427306 | F32-4321 | R | 178259970 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B | Min Power Factor B | 427308 | PF32 | R | 178260225 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor B | Min Power Factor B Load Direction | Min Power Factor B Load Direction | 427308 | F32-4321 | R | 178260226 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C | Min Power Factor C | 427310 | PF32 | R | 178260481 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor C | Min Power Factor C Load Direction | Min Power Factor C Load Direction | 427310 | F32-4321 | R | 178260482 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total | Min Power Factor Total | 427312 | PF32 | R | 178260737 |  |  |  |  | 2
|  | Minimum Readings | Min Power Factor Total | Min Power Factor Total Load Direction | Min Power Factor Total Load Direction | 427312 | F32-4321 | R | 178260738 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current A | Min THD Current A | 427338 | F32-4321 | R | 178263042 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current B | Min THD Current B | 427340 | F32-4321 | R | 178263043 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current C | Min THD Current C | 427342 | F32-4321 | R | 178263044 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current N | Min THD Current N | 427344 | F32-4321 | R | 178263045 |  |  |  |  | 2
|  | Minimum Readings | Min THD Current | Min THD Current G | Min THD Current G | 427346 | F32-4321 | R | 178263041
|  | Minimum Readings | Min thd Current | Min thd_Current A | Min thd_Current A | 427348 | F32-4321 | R | 178262785 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current B | Min thd_Current B | 427350 | F32-4321 | R | 178262786 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current C | Min thd_Current C | 427352 | F32-4321 | R | 178262787 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current N | Min thd_Current N | 427354 | F32-4321 | R | 178262788 |  |  |  |  | 2
|  | Minimum Readings | Min thd Current | Min thd_Current G | Min thd_Current G | 427356 | F32-4321 | R | 178262789
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-B | Min THD Voltage A-B | 427360 | F32-4321 | R | 178263553 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage A-N | Min THD Voltage A-N | 427368 | F32-4321 | R | 178263556 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-C | Min THD Voltage B-C | 427362 | F32-4321 | R | 178263554 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage B-N | Min THD Voltage B-N | 427370 | F32-4321 | R | 178263557 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-A | Min THD Voltage C-A | 427364 | F32-4321 | R | 178263555 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage C-N | Min THD Voltage C-N | 427372 | F32-4321 | R | 178263558 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-L | Min THD Voltage L-L | 427366 | F32-4321 | R | 178263559 |  |  |  |  | 2
|  | Minimum Readings | Min THD Voltage | Min THD Voltage L-N | Min THD Voltage L-N | 427376 | F32-4321 | R | 178263563 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-B | Min thd_Voltage A-B | 427378 | F32-4321 | R | 178263297 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage A-N | Min thd_Voltage A-N | 427386 | F32-4321 | R | 178263300 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-C | Min thd_Voltage B-C | 427380 | F32-4321 | R | 178263298 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage B-N | Min thd_Voltage B-N | 427388 | F32-4321 | R | 178263301 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-A | Min thd_Voltage C-A | 427382 | F32-4321 | R | 178263299 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage C-N | Min thd_Voltage C-N | 427390 | F32-4321 | R | 178263302 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-L | Min thd_Voltage L-L | 427384 | F32-4321 | R | 178263303 |  |  |  |  | 2
|  | Minimum Readings | Min thd Voltage | Min thd_Voltage L-N | Min thd_Voltage L-N | 427394 | F32-4321 | R | 178263304 |  |  |  |  | 2
|  | Minimum Readings | Min Total Demand Distortion | Min Total Demand Distortion | Min Total Demand Distortion | 427358 | F32-4321 | R | 178257921 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-B | Min Voltage A-B | 427238 | F32-4321 | R | 178264065 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage A-N | Min Voltage A-N | 427246 | F32-4321 | R | 178264068 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-C | Min Voltage B-C | 427240 | F32-4321 | R | 178264066 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage B-N | Min Voltage B-N | 427248 | F32-4321 | R | 178264069 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-A | Min Voltage C-A | 427242 | F32-4321 | R | 178264067 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage C-N | Min Voltage C-N | 427250 | F32-4321 | R | 178264070 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-L Avg | Min Voltage L-L Avg | 427244 | F32-4321 | R | 178264072 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage | Min Voltage L-N Avg | Min Voltage L-N Avg | 427254 | F32-4321 | R | 178264077 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-B | Min Voltage Unbalance A-B | 427256 | F32-4321 | R | 178264321 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance A-N | Min Voltage Unbalance A-N | 427264 | F32-4321 | R | 178264324 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-C | Min Voltage Unbalance B-C | 427258 | F32-4321 | R | 178264322 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance B-N | Min Voltage Unbalance B-N | 427266 | F32-4321 | R | 178264325 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-A | Min Voltage Unbalance C-A | 427260 | F32-4321 | R | 178264323 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance C-N | Min Voltage Unbalance C-N | 427268 | F32-4321 | R | 178264326 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-L Worst | Min Voltage Unbalance L-L Worst | 427262 | F32-4321 | R | 178264331 |  |  |  |  | 2
|  | Minimum Readings | Min Voltage Unbalance | Min Voltage Unbalance L-N Worst | Min Voltage Unbalance L-N Worst | 427270 | F32-4321 | R | 178264336 |  |  |  |  | 2
|  | Miscellaneous | Active Load Timer | Active Load Timer | Active Load Timer | 402002 | UINT32 | R | 179307265
|  | Miscellaneous | Active Load Timer | Active Load Timer Setpoint | Active Load Timer Setpoint | 402050 | F32-4321 | R | 179307266
|  | Miscellaneous | Cycle Count | Cycle Count | Cycle Count | 402006 | UINT32 | R | 179307521
|  | Miscellaneous | DT Last Reset MinMax | DT Last Reset MinMax | DT Last Reset MinMax | 427214 | DateTime3_IEC870_UTC | R | 179308289
|  | Miscellaneous | Frequency | Frequency | Frequency | 403110 | F32-4321 | R | 179307009
|  | Miscellaneous | LED Mode | LED Mode | LED Mode | 402126 | UINT16 | R | 179306753
|  | Miscellaneous | Meter ON Duration | Meter ON Duration | Meter ON Duration | 402004 | UINT32 | R | 179308545 |  | 3600
|  | Miscellaneous | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | Peak Current Demand Over Last Year | 402048 | F32-4321 | R | 179308033
|  | Miscellaneous | Revenue Security Status | Revenue Security Status | Revenue Security Status | 401921 | UINT16 | R | 179307777
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A | Displacement Power Factor A | 403086 | PF32 | R | 186647553
|  | Power Factors | Displacement Power Factor A | Displacement Power Factor A Load Direction | Displacement Power Factor A Load Direction | 403086 | F32-4321 | R | 186647554
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B | Displacement Power Factor B | 403088 | PF32 | R | 186647809
|  | Power Factors | Displacement Power Factor B | Displacement Power Factor B Load Direction | Displacement Power Factor B Load Direction | 403088 | F32-4321 | R | 186647810
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C | Displacement Power Factor C | 403090 | PF32 | R | 186648065
|  | Power Factors | Displacement Power Factor C | Displacement Power Factor C Load Direction | Displacement Power Factor C Load Direction | 403090 | F32-4321 | R | 186648066
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total | Displacement Power Factor Total | 403092 | PF32 | R | 186648321
|  | Power Factors | Displacement Power Factor Total | Displacement Power Factor Total Load Direction | Displacement Power Factor Total Load Direction | 403092 | F32-4321 | R | 186648322
|  | Power Factors | Power Factor A | Power Factor A | Power Factor A | 403078 | PF32 | R | 186646529
|  | Power Factors | Power Factor A | Power Factor A Load Direction | Power Factor A Load Direction | 403078 | F32-4321 | R | 186646530
|  | Power Factors | Power Factor B | Power Factor B | Power Factor B | 403080 | PF32 | R | 186646785
|  | Power Factors | Power Factor B | Power Factor B Load Direction | Power Factor B Load Direction | 403080 | F32-4321 | R | 186646786
|  | Power Factors | Power Factor C | Power Factor C | Power Factor C | 403082 | PF32 | R | 186647041
|  | Power Factors | Power Factor C | Power Factor C Load Direction | Power Factor C Load Direction | 403082 | F32-4321 | R | 186647042
DR1 | 900 | Power Factors | Power Factor Total | Power Factor Total | Power Factor Total | 403084 | PF32 | R | 186647297
|  | Power Factors | Power Factor Total | Power Factor Total Load Direction | Power Factor Total Load Direction | 403084 | F32-4321 | R | 186647298
|  | Power Quality | THD Current | THD Current A | THD Current A | 421300 | F32-4321 | R | 187696897 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current B | THD Current B | 421302 | F32-4321 | R | 187696898 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current C | THD Current C | 421304 | F32-4321 | R | 187696899 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current N | THD Current N | 421306 | F32-4321 | R | 187696900 |  |  |  |  | 2
|  | Power Quality | THD Current | THD Current G | THD Current G | 421308 | F32-4321 | R | 187696901
|  | Power Quality | THD Voltage | THD Voltage A-B | THD Voltage A-B | 421322 | F32-4321 | R | 187697153 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage A-N | THD Voltage A-N | 421330 | F32-4321 | R | 187697156 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-C | THD Voltage B-C | 421324 | F32-4321 | R | 187697154 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage B-N | THD Voltage B-N | 421332 | F32-4321 | R | 187697157 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-A | THD Voltage C-A | 421326 | F32-4321 | R | 187697155 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage C-N | THD Voltage C-N | 421334 | F32-4321 | R | 187697158 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-L | THD Voltage L-L | 421328 | F32-4321 | R | 187697159 |  |  |  |  | 2
|  | Power Quality | THD Voltage | THD Voltage L-N | THD Voltage L-N | 421338 | F32-4321 | R | 187697160 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current A | thd_Current A | 421310 | F32-4321 | R | 187697665 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current B | thd_Current B | 421312 | F32-4321 | R | 187697666 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current C | thd_Current C | 421314 | F32-4321 | R | 187697667 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current N | thd_Current N | 421316 | F32-4321 | R | 187697668 |  |  |  |  | 2
|  | Power Quality | thd_Current | thd_Current G | thd_Current G | 421318 | F32-4321 | R | 187697669
|  | Power Quality | thd_Voltage | thd_Voltage A-B | thd_Voltage A-B | 421340 | F32-4321 | R | 187697921 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage A-N | thd_Voltage A-N | 421348 | F32-4321 | R | 187697924 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-C | thd_Voltage B-C | 421342 | F32-4321 | R | 187697922 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage B-N | thd_Voltage B-N | 421350 | F32-4321 | R | 187697925 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-A | thd_Voltage C-A | 421344 | F32-4321 | R | 187697923 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage C-N | thd_Voltage C-N | 421352 | F32-4321 | R | 187697926 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-L | thd_Voltage L-L | 421346 | F32-4321 | R | 187697927 |  |  |  |  | 2
|  | Power Quality | thd_Voltage | thd_Voltage L-N | thd_Voltage L-N | 421356 | F32-4321 | R | 187697928 |  |  |  |  | 2
|  | Power Quality | Total Demand Distortion | Total Demand Distortion | Total Demand Distortion | 421320 | F32-4321 | R | 187698177 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power A | Apparent Power A | 403070 | F32-4321 | R | 190840841 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power B | Apparent Power B | 403072 | F32-4321 | R | 190840842 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power C | Apparent Power C | 403074 | F32-4321 | R | 190840843 |  |  |  |  | 2
|  | Powers | Apparent Power | Apparent Power Total | Apparent Power Total | 403076 | F32-4321 | R | 190840844 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power A | Reactive Power A | 403062 | F32-4321 | R | 190840837 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power B | Reactive Power B | 403064 | F32-4321 | R | 190840838 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power C | Reactive Power C | 403066 | F32-4321 | R | 190840839 |  |  |  |  | 2
|  | Powers | Reactive Power | Reactive Power Total | Reactive Power Total | 403068 | F32-4321 | R | 190840840 |  |  |  |  | 2
|  | Powers | Real Power | Real Power A | Real Power A | 403054 | F32-4321 | R | 190840833 |  |  |  |  | 2
|  | Powers | Real Power | Real Power B | Real Power B | 403056 | F32-4321 | R | 190840834 |  |  |  |  | 2
|  | Powers | Real Power | Real Power C | Real Power C | 403058 | F32-4321 | R | 190840835 |  |  |  |  | 2
|  | Powers | Real Power | Real Power Total | Real Power Total | 403060 | F32-4321 | R | 190840836 |  |  |  |  | 2
|  | Resets and Triggers | Resets | Accumulated Energy Reset | Accumulated Energy Reset | 405250 | U16-21-ARRAY | CW | 156237828
|  | Resets and Triggers | Resets | All Demand Interval Reset | All Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237839
|  | Resets and Triggers | Resets | Current Demand Interval Reset | Current Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237829
|  | Resets and Triggers | Resets | Current Demand Reset | Current Demand Reset | 405250 | U16-21-ARRAY | CW | 156237837
|  | Resets and Triggers | Resets | Min Max Reset | Min Max Reset | 405250 | U16-21-ARRAY | CW | 156237840
|  | Resets and Triggers | Resets | Peak Demand Current Reset | Peak Demand Current Reset | 405250 | U16-21-ARRAY | CW | 156237825
|  | Resets and Triggers | Resets | Power Demand Interval Reset | Power Demand Interval Reset | 405250 | U16-21-ARRAY | CW | 156237830
|  | Resets and Triggers | Resets | Reset Active Load Timer | Reset Active Load Timer | 405250 | U16-21-ARRAY | CW | 156237831
|  | Spectral Components | Current A Harmonics | H1 Current A Magnitude | H1 Current A Magnitude | 424428 | F32-4321 | R | 257287937
|  | Spectral Components | Current A Harmonics | H2 Current A Magnitude | H2 Current A Magnitude | 424434 | F32-4321 | R | 257287939
|  | Spectral Components | Current A Harmonics | H3 Current A Magnitude | H3 Current A Magnitude | 424440 | F32-4321 | R | 257287941
|  | Spectral Components | Current A Harmonics | H4 Current A Magnitude | H4 Current A Magnitude | 424446 | F32-4321 | R | 257287943
|  | Spectral Components | Current A Harmonics | H5 Current A Magnitude | H5 Current A Magnitude | 424452 | F32-4321 | R | 257287945
|  | Spectral Components | Current A Harmonics | H6 Current A Magnitude | H6 Current A Magnitude | 424458 | F32-4321 | R | 257287947
|  | Spectral Components | Current A Harmonics | H7 Current A Magnitude | H7 Current A Magnitude | 424464 | F32-4321 | R | 257287949
|  | Spectral Components | Current A Harmonics | H8 Current A Magnitude | H8 Current A Magnitude | 424470 | F32-4321 | R | 257287951
|  | Spectral Components | Current A Harmonics | H9 Current A Magnitude | H9 Current A Magnitude | 424476 | F32-4321 | R | 257287953
|  | Spectral Components | Current A Harmonics | H10 Current A Magnitude | H10 Current A Magnitude | 424482 | F32-4321 | R | 257287955
|  | Spectral Components | Current A Harmonics | H11 Current A Magnitude | H11 Current A Magnitude | 424488 | F32-4321 | R | 257287957
|  | Spectral Components | Current A Harmonics | H12 Current A Magnitude | H12 Current A Magnitude | 424494 | F32-4321 | R | 257287959
|  | Spectral Components | Current A Harmonics | H13 Current A Magnitude | H13 Current A Magnitude | 424500 | F32-4321 | R | 257287961
|  | Spectral Components | Current A Harmonics | H14 Current A Magnitude | H14 Current A Magnitude | 424506 | F32-4321 | R | 257287963
|  | Spectral Components | Current A Harmonics | H15 Current A Magnitude | H15 Current A Magnitude | 424512 | F32-4321 | R | 257287965
|  | Spectral Components | Current B Harmonics | H1 Current B Magnitude | H1 Current B Magnitude | 424816 | F32-4321 | R | 257288193
|  | Spectral Components | Current B Harmonics | H2 Current B Magnitude | H2 Current B Magnitude | 424822 | F32-4321 | R | 257288195
|  | Spectral Components | Current B Harmonics | H3 Current B Magnitude | H3 Current B Magnitude | 424828 | F32-4321 | R | 257288197
|  | Spectral Components | Current B Harmonics | H4 Current B Magnitude | H4 Current B Magnitude | 424834 | F32-4321 | R | 257288199
|  | Spectral Components | Current B Harmonics | H5 Current B Magnitude | H5 Current B Magnitude | 424840 | F32-4321 | R | 257288201
|  | Spectral Components | Current B Harmonics | H6 Current B Magnitude | H6 Current B Magnitude | 424846 | F32-4321 | R | 257288203
|  | Spectral Components | Current B Harmonics | H7 Current B Magnitude | H7 Current B Magnitude | 424852 | F32-4321 | R | 257288205
|  | Spectral Components | Current B Harmonics | H8 Current B Magnitude | H8 Current B Magnitude | 424858 | F32-4321 | R | 257288207
|  | Spectral Components | Current B Harmonics | H9 Current B Magnitude | H9 Current B Magnitude | 424864 | F32-4321 | R | 257288209
|  | Spectral Components | Current B Harmonics | H10 Current B Magnitude | H10 Current B Magnitude | 424870 | F32-4321 | R | 257288211
|  | Spectral Components | Current B Harmonics | H11 Current B Magnitude | H11 Current B Magnitude | 424876 | F32-4321 | R | 257288213
|  | Spectral Components | Current B Harmonics | H12 Current B Magnitude | H12 Current B Magnitude | 424882 | F32-4321 | R | 257288215
|  | Spectral Components | Current B Harmonics | H13 Current B Magnitude | H13 Current B Magnitude | 424888 | F32-4321 | R | 257288217
|  | Spectral Components | Current B Harmonics | H14 Current B Magnitude | H14 Current B Magnitude | 424894 | F32-4321 | R | 257288219
|  | Spectral Components | Current B Harmonics | H15 Current B Magnitude | H15 Current B Magnitude | 424900 | F32-4321 | R | 257288221
|  | Spectral Components | Current C Harmonics | H1 Current C Magnitude | H1 Current C Magnitude | 425204 | F32-4321 | R | 257288449
|  | Spectral Components | Current C Harmonics | H2 Current C Magnitude | H2 Current C Magnitude | 425210 | F32-4321 | R | 257288451
|  | Spectral Components | Current C Harmonics | H3 Current C Magnitude | H3 Current C Magnitude | 425216 | F32-4321 | R | 257288453
|  | Spectral Components | Current C Harmonics | H4 Current C Magnitude | H4 Current C Magnitude | 425222 | F32-4321 | R | 257288455
|  | Spectral Components | Current C Harmonics | H5 Current C Magnitude | H5 Current C Magnitude | 425228 | F32-4321 | R | 257288457
|  | Spectral Components | Current C Harmonics | H6 Current C Magnitude | H6 Current C Magnitude | 425234 | F32-4321 | R | 257288459
|  | Spectral Components | Current C Harmonics | H7 Current C Magnitude | H7 Current C Magnitude | 425240 | F32-4321 | R | 257288461
|  | Spectral Components | Current C Harmonics | H8 Current C Magnitude | H8 Current C Magnitude | 425246 | F32-4321 | R | 257288463
|  | Spectral Components | Current C Harmonics | H9 Current C Magnitude | H9 Current C Magnitude | 425252 | F32-4321 | R | 257288465
|  | Spectral Components | Current C Harmonics | H10 Current C Magnitude | H10 Current C Magnitude | 425258 | F32-4321 | R | 257288467
|  | Spectral Components | Current C Harmonics | H11 Current C Magnitude | H11 Current C Magnitude | 425264 | F32-4321 | R | 257288469
|  | Spectral Components | Current C Harmonics | H12 Current C Magnitude | H12 Current C Magnitude | 425270 | F32-4321 | R | 257288471
|  | Spectral Components | Current C Harmonics | H13 Current C Magnitude | H13 Current C Magnitude | 425276 | F32-4321 | R | 257288473
|  | Spectral Components | Current C Harmonics | H14 Current C Magnitude | H14 Current C Magnitude | 425282 | F32-4321 | R | 257288475
|  | Spectral Components | Current C Harmonics | H15 Current C Magnitude | H15 Current C Magnitude | 425288 | F32-4321 | R | 257288477
|  | Spectral Components | Voltage A-B Harmonics | H1 Voltage A-B Magnitude | H1 Voltage A-B Magnitude | 421712 | F32-4321 | R | 257286401
|  | Spectral Components | Voltage A-B Harmonics | H2 Voltage A-B Magnitude | H2 Voltage A-B Magnitude | 421718 | F32-4321 | R | 257286403
|  | Spectral Components | Voltage A-B Harmonics | H3 Voltage A-B Magnitude | H3 Voltage A-B Magnitude | 421724 | F32-4321 | R | 257286405
|  | Spectral Components | Voltage A-B Harmonics | H4 Voltage A-B Magnitude | H4 Voltage A-B Magnitude | 421730 | F32-4321 | R | 257286407
|  | Spectral Components | Voltage A-B Harmonics | H5 Voltage A-B Magnitude | H5 Voltage A-B Magnitude | 421736 | F32-4321 | R | 257286409
|  | Spectral Components | Voltage A-B Harmonics | H6 Voltage A-B Magnitude | H6 Voltage A-B Magnitude | 421742 | F32-4321 | R | 257286411
|  | Spectral Components | Voltage A-B Harmonics | H7 Voltage A-B Magnitude | H7 Voltage A-B Magnitude | 421748 | F32-4321 | R | 257286413
|  | Spectral Components | Voltage A-B Harmonics | H8 Voltage A-B Magnitude | H8 Voltage A-B Magnitude | 421754 | F32-4321 | R | 257286415
|  | Spectral Components | Voltage A-B Harmonics | H9 Voltage A-B Magnitude | H9 Voltage A-B Magnitude | 421760 | F32-4321 | R | 257286417
|  | Spectral Components | Voltage A-B Harmonics | H10 Voltage A-B Magnitude | H10 Voltage A-B Magnitude | 421766 | F32-4321 | R | 257286419
|  | Spectral Components | Voltage A-B Harmonics | H11 Voltage A-B Magnitude | H11 Voltage A-B Magnitude | 421772 | F32-4321 | R | 257286421
|  | Spectral Components | Voltage A-B Harmonics | H12 Voltage A-B Magnitude | H12 Voltage A-B Magnitude | 421778 | F32-4321 | R | 257286423
|  | Spectral Components | Voltage A-B Harmonics | H13 Voltage A-B Magnitude | H13 Voltage A-B Magnitude | 421784 | F32-4321 | R | 257286425
|  | Spectral Components | Voltage A-B Harmonics | H14 Voltage A-B Magnitude | H14 Voltage A-B Magnitude | 421790 | F32-4321 | R | 257286427
|  | Spectral Components | Voltage A-B Harmonics | H15 Voltage A-B Magnitude | H15 Voltage A-B Magnitude | 421796 | F32-4321 | R | 257286429
|  | Spectral Components | Voltage A-N Harmonics | H1 Voltage A-N Magnitude | H1 Voltage A-N Magnitude | 422876 | F32-4321 | R | 257287169
|  | Spectral Components | Voltage A-N Harmonics | H2 Voltage A-N Magnitude | H2 Voltage A-N Magnitude | 422882 | F32-4321 | R | 257287171
|  | Spectral Components | Voltage A-N Harmonics | H3 Voltage A-N Magnitude | H3 Voltage A-N Magnitude | 422888 | F32-4321 | R | 257287173
|  | Spectral Components | Voltage A-N Harmonics | H4 Voltage A-N Magnitude | H4 Voltage A-N Magnitude | 422894 | F32-4321 | R | 257287175
|  | Spectral Components | Voltage A-N Harmonics | H5 Voltage A-N Magnitude | H5 Voltage A-N Magnitude | 422900 | F32-4321 | R | 257287177
|  | Spectral Components | Voltage A-N Harmonics | H6 Voltage A-N Magnitude | H6 Voltage A-N Magnitude | 422906 | F32-4321 | R | 257287179
|  | Spectral Components | Voltage A-N Harmonics | H7 Voltage A-N Magnitude | H7 Voltage A-N Magnitude | 422912 | F32-4321 | R | 257287181
|  | Spectral Components | Voltage A-N Harmonics | H8 Voltage A-N Magnitude | H8 Voltage A-N Magnitude | 422918 | F32-4321 | R | 257287183
|  | Spectral Components | Voltage A-N Harmonics | H9 Voltage A-N Magnitude | H9 Voltage A-N Magnitude | 422924 | F32-4321 | R | 257287185
|  | Spectral Components | Voltage A-N Harmonics | H10 Voltage A-N Magnitude | H10 Voltage A-N Magnitude | 422930 | F32-4321 | R | 257287187
|  | Spectral Components | Voltage A-N Harmonics | H11 Voltage A-N Magnitude | H11 Voltage A-N Magnitude | 422936 | F32-4321 | R | 257287189
|  | Spectral Components | Voltage A-N Harmonics | H12 Voltage A-N Magnitude | H12 Voltage A-N Magnitude | 422942 | F32-4321 | R | 257287191
|  | Spectral Components | Voltage A-N Harmonics | H13 Voltage A-N Magnitude | H13 Voltage A-N Magnitude | 422948 | F32-4321 | R | 257287193
|  | Spectral Components | Voltage A-N Harmonics | H14 Voltage A-N Magnitude | H14 Voltage A-N Magnitude | 422954 | F32-4321 | R | 257287195
|  | Spectral Components | Voltage A-N Harmonics | H15 Voltage A-N Magnitude | H15 Voltage A-N Magnitude | 422960 | F32-4321 | R | 257287197
|  | Spectral Components | Voltage B-C Harmonics | H1 Voltage B-C Magnitude | H1 Voltage B-C Magnitude | 422100 | F32-4321 | R | 257286657
|  | Spectral Components | Voltage B-C Harmonics | H2 Voltage B-C Magnitude | H2 Voltage B-C Magnitude | 422106 | F32-4321 | R | 257286659
|  | Spectral Components | Voltage B-C Harmonics | H3 Voltage B-C Magnitude | H3 Voltage B-C Magnitude | 422112 | F32-4321 | R | 257286661
|  | Spectral Components | Voltage B-C Harmonics | H4 Voltage B-C Magnitude | H4 Voltage B-C Magnitude | 422118 | F32-4321 | R | 257286663
|  | Spectral Components | Voltage B-C Harmonics | H5 Voltage B-C Magnitude | H5 Voltage B-C Magnitude | 422124 | F32-4321 | R | 257286665
|  | Spectral Components | Voltage B-C Harmonics | H6 Voltage B-C Magnitude | H6 Voltage B-C Magnitude | 422130 | F32-4321 | R | 257286667
|  | Spectral Components | Voltage B-C Harmonics | H7 Voltage B-C Magnitude | H7 Voltage B-C Magnitude | 422136 | F32-4321 | R | 257286669
|  | Spectral Components | Voltage B-C Harmonics | H8 Voltage B-C Magnitude | H8 Voltage B-C Magnitude | 422142 | F32-4321 | R | 257286671
|  | Spectral Components | Voltage B-C Harmonics | H9 Voltage B-C Magnitude | H9 Voltage B-C Magnitude | 422148 | F32-4321 | R | 257286673
|  | Spectral Components | Voltage B-C Harmonics | H10 Voltage B-C Magnitude | H10 Voltage B-C Magnitude | 422154 | F32-4321 | R | 257286675
|  | Spectral Components | Voltage B-C Harmonics | H11 Voltage B-C Magnitude | H11 Voltage B-C Magnitude | 422160 | F32-4321 | R | 257286677
|  | Spectral Components | Voltage B-C Harmonics | H12 Voltage B-C Magnitude | H12 Voltage B-C Magnitude | 422166 | F32-4321 | R | 257286679
|  | Spectral Components | Voltage B-C Harmonics | H13 Voltage B-C Magnitude | H13 Voltage B-C Magnitude | 422172 | F32-4321 | R | 257286681
|  | Spectral Components | Voltage B-C Harmonics | H14 Voltage B-C Magnitude | H14 Voltage B-C Magnitude | 422178 | F32-4321 | R | 257286683
|  | Spectral Components | Voltage B-C Harmonics | H15 Voltage B-C Magnitude | H15 Voltage B-C Magnitude | 422184 | F32-4321 | R | 257286685
|  | Spectral Components | Voltage B-N Harmonics | H1 Voltage B-N Magnitude | H1 Voltage B-N Magnitude | 423264 | F32-4321 | R | 257287425
|  | Spectral Components | Voltage B-N Harmonics | H2 Voltage B-N Magnitude | H2 Voltage B-N Magnitude | 423270 | F32-4321 | R | 257287427
|  | Spectral Components | Voltage B-N Harmonics | H3 Voltage B-N Magnitude | H3 Voltage B-N Magnitude | 423276 | F32-4321 | R | 257287429
|  | Spectral Components | Voltage B-N Harmonics | H4 Voltage B-N Magnitude | H4 Voltage B-N Magnitude | 423282 | F32-4321 | R | 257287431
|  | Spectral Components | Voltage B-N Harmonics | H5 Voltage B-N Magnitude | H5 Voltage B-N Magnitude | 423288 | F32-4321 | R | 257287433
|  | Spectral Components | Voltage B-N Harmonics | H6 Voltage B-N Magnitude | H6 Voltage B-N Magnitude | 423294 | F32-4321 | R | 257287435
|  | Spectral Components | Voltage B-N Harmonics | H7 Voltage B-N Magnitude | H7 Voltage B-N Magnitude | 423300 | F32-4321 | R | 257287437
|  | Spectral Components | Voltage B-N Harmonics | H8 Voltage B-N Magnitude | H8 Voltage B-N Magnitude | 423306 | F32-4321 | R | 257287439
|  | Spectral Components | Voltage B-N Harmonics | H9 Voltage B-N Magnitude | H9 Voltage B-N Magnitude | 423312 | F32-4321 | R | 257287441
|  | Spectral Components | Voltage B-N Harmonics | H10 Voltage B-N Magnitude | H10 Voltage B-N Magnitude | 423318 | F32-4321 | R | 257287443
|  | Spectral Components | Voltage B-N Harmonics | H11 Voltage B-N Magnitude | H11 Voltage B-N Magnitude | 423324 | F32-4321 | R | 257287445
|  | Spectral Components | Voltage B-N Harmonics | H12 Voltage B-N Magnitude | H12 Voltage B-N Magnitude | 423330 | F32-4321 | R | 257287447
|  | Spectral Components | Voltage B-N Harmonics | H13 Voltage B-N Magnitude | H13 Voltage B-N Magnitude | 423336 | F32-4321 | R | 257287449
|  | Spectral Components | Voltage B-N Harmonics | H14 Voltage B-N Magnitude | H14 Voltage B-N Magnitude | 423342 | F32-4321 | R | 257287451
|  | Spectral Components | Voltage B-N Harmonics | H15 Voltage B-N Magnitude | H15 Voltage B-N Magnitude | 423348 | F32-4321 | R | 257287453
|  | Spectral Components | Voltage C-A Harmonics | H1 Voltage C-A Magnitude | H1 Voltage C-A Magnitude | 422488 | F32-4321 | R | 257286913
|  | Spectral Components | Voltage C-A Harmonics | H2 Voltage C-A Magnitude | H2 Voltage C-A Magnitude | 422494 | F32-4321 | R | 257286915
|  | Spectral Components | Voltage C-A Harmonics | H3 Voltage C-A Magnitude | H3 Voltage C-A Magnitude | 422500 | F32-4321 | R | 257286917
|  | Spectral Components | Voltage C-A Harmonics | H4 Voltage C-A Magnitude | H4 Voltage C-A Magnitude | 422506 | F32-4321 | R | 257286919
|  | Spectral Components | Voltage C-A Harmonics | H5 Voltage C-A Magnitude | H5 Voltage C-A Magnitude | 422512 | F32-4321 | R | 257286921
|  | Spectral Components | Voltage C-A Harmonics | H6 Voltage C-A Magnitude | H6 Voltage C-A Magnitude | 422518 | F32-4321 | R | 257286923
|  | Spectral Components | Voltage C-A Harmonics | H7 Voltage C-A Magnitude | H7 Voltage C-A Magnitude | 422524 | F32-4321 | R | 257286925
|  | Spectral Components | Voltage C-A Harmonics | H8 Voltage C-A Magnitude | H8 Voltage C-A Magnitude | 422530 | F32-4321 | R | 257286927
|  | Spectral Components | Voltage C-A Harmonics | H9 Voltage C-A Magnitude | H9 Voltage C-A Magnitude | 422536 | F32-4321 | R | 257286929
|  | Spectral Components | Voltage C-A Harmonics | H10 Voltage C-A Magnitude | H10 Voltage C-A Magnitude | 422542 | F32-4321 | R | 257286931
|  | Spectral Components | Voltage C-A Harmonics | H11 Voltage C-A Magnitude | H11 Voltage C-A Magnitude | 422548 | F32-4321 | R | 257286933
|  | Spectral Components | Voltage C-A Harmonics | H12 Voltage C-A Magnitude | H12 Voltage C-A Magnitude | 422554 | F32-4321 | R | 257286935
|  | Spectral Components | Voltage C-A Harmonics | H13 Voltage C-A Magnitude | H13 Voltage C-A Magnitude | 422560 | F32-4321 | R | 257286937
|  | Spectral Components | Voltage C-A Harmonics | H14 Voltage C-A Magnitude | H14 Voltage C-A Magnitude | 422566 | F32-4321 | R | 257286939
|  | Spectral Components | Voltage C-A Harmonics | H15 Voltage C-A Magnitude | H15 Voltage C-A Magnitude | 422572 | F32-4321 | R | 257286941
|  | Spectral Components | Voltage C-N Harmonics | H1 Voltage C-N Magnitude | H1 Voltage C-N Magnitude | 423652 | F32-4321 | R | 257287681
|  | Spectral Components | Voltage C-N Harmonics | H2 Voltage C-N Magnitude | H2 Voltage C-N Magnitude | 423658 | F32-4321 | R | 257287683
|  | Spectral Components | Voltage C-N Harmonics | H3 Voltage C-N Magnitude | H3 Voltage C-N Magnitude | 423664 | F32-4321 | R | 257287685
|  | Spectral Components | Voltage C-N Harmonics | H4 Voltage C-N Magnitude | H4 Voltage C-N Magnitude | 423670 | F32-4321 | R | 257287687
|  | Spectral Components | Voltage C-N Harmonics | H5 Voltage C-N Magnitude | H5 Voltage C-N Magnitude | 423676 | F32-4321 | R | 257287689
|  | Spectral Components | Voltage C-N Harmonics | H6 Voltage C-N Magnitude | H6 Voltage C-N Magnitude | 423682 | F32-4321 | R | 257287691
|  | Spectral Components | Voltage C-N Harmonics | H7 Voltage C-N Magnitude | H7 Voltage C-N Magnitude | 423688 | F32-4321 | R | 257287693
|  | Spectral Components | Voltage C-N Harmonics | H8 Voltage C-N Magnitude | H8 Voltage C-N Magnitude | 423694 | F32-4321 | R | 257287695
|  | Spectral Components | Voltage C-N Harmonics | H9 Voltage C-N Magnitude | H9 Voltage C-N Magnitude | 423700 | F32-4321 | R | 257287697
|  | Spectral Components | Voltage C-N Harmonics | H10 Voltage C-N Magnitude | H10 Voltage C-N Magnitude | 423706 | F32-4321 | R | 257287699
|  | Spectral Components | Voltage C-N Harmonics | H11 Voltage C-N Magnitude | H11 Voltage C-N Magnitude | 423712 | F32-4321 | R | 257287701
|  | Spectral Components | Voltage C-N Harmonics | H12 Voltage C-N Magnitude | H12 Voltage C-N Magnitude | 423718 | F32-4321 | R | 257287703
|  | Spectral Components | Voltage C-N Harmonics | H13 Voltage C-N Magnitude | H13 Voltage C-N Magnitude | 423724 | F32-4321 | R | 257287705
|  | Spectral Components | Voltage C-N Harmonics | H14 Voltage C-N Magnitude | H14 Voltage C-N Magnitude | 423730 | F32-4321 | R | 257287707
|  | Spectral Components | Voltage C-N Harmonics | H15 Voltage C-N Magnitude | H15 Voltage C-N Magnitude | 423736 | F32-4321 | R | 257287709
|  | Unbalances | Current Unbalance | Current Unbalance A | Current Unbalance A | 403012 | F32-4321 | R | 198180865 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance B | Current Unbalance B | 403014 | F32-4321 | R | 198180866 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance C | Current Unbalance C | 403016 | F32-4321 | R | 198180867 |  |  |  |  | 2
|  | Unbalances | Current Unbalance | Current Unbalance Worst | Current Unbalance Worst | 403018 | F32-4321 | R | 198180868 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-B | Voltage Unbalance A-B | 403038 | F32-4321 | R | 198181121 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance A-N | Voltage Unbalance A-N | 403046 | F32-4321 | R | 198181125 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-C | Voltage Unbalance B-C | 403040 | F32-4321 | R | 198181122 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance B-N | Voltage Unbalance B-N | 403048 | F32-4321 | R | 198181126 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-A | Voltage Unbalance C-A | 403042 | F32-4321 | R | 198181123 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance C-N | Voltage Unbalance C-N | 403050 | F32-4321 | R | 198181127 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-L Worst | Voltage Unbalance L-L Worst | 403044 | F32-4321 | R | 198181124 |  |  |  |  | 2
|  | Unbalances | Voltage Unbalance | Voltage Unbalance L-N Worst | Voltage Unbalance L-N Worst | 403052 | F32-4321 | R | 198181128 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage A-B | Voltage A-B | 403020 | F32-4321 | R | 201326593 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage A-N | Voltage A-N | 403028 | F32-4321 | R | 201326597 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage B-C | Voltage B-C | 403022 | F32-4321 | R | 201326594 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage B-N | Voltage B-N | 403030 | F32-4321 | R | 201326598 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage C-A | Voltage C-A | 403024 | F32-4321 | R | 201326595 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage C-N | Voltage C-N | 403032 | F32-4321 | R | 201326599 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage L-L Avg | Voltage L-L Avg | 403026 | F32-4321 | R | 201326596 |  |  |  |  | 2
DR1 | 900 | Voltages | Voltage | Voltage L-N Avg | Voltage L-N Avg | 403036 | F32-4321 | R | 201326600 |  |  |  |  | 2
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Trigger |  |  |  |  | 202375171
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Period |  |  |  |  | 202375169
|  | PeriodicTimer Modules | Periodic Tmr 1 | PT1 Sync Mode |  |  |  |  | 202375170
|  | Feedback Modules | Feedback 1 | FBK1 Pulse Out |  |  |  |  | 203423745
|  | DataRecorder Modules | Data Rec 1 | RE1 Data Log |  |  |  |  | 204472321
|  | DataRecorder Modules | Data Rec 1 | RE1 Log State |  |  |  |  | 204472322
|  | DataRecorder Modules | Data Rec 1 | RE1 Records Left |  |  |  |  | 204472323
|  | DataRecorder Modules | Data Rec 1 | RE1 Record Complete |  |  |  |  | 204472324
|  | DataRecorder Modules | Data Rec 1 | RE1 Depth |  |  |  |  | 204472325
|  | DataRecorder Modules | Data Rec 1 | RE1 RecordMode |  |  |  |  | 204472326
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Threshold |  |  |  |  | 204472327
|  | DataRecorder Modules | Data Rec 1 | RE1 Staleness Action |  |  |  |  | 204472328
|  | DataRecorder Modules | Data Rec 2 | RE2 Data Log |  |  |  |  | 204472577
|  | DataRecorder Modules | Data Rec 2 | RE2 Log State |  |  |  |  | 204472578
|  | DataRecorder Modules | Data Rec 2 | RE2 Records Left |  |  |  |  | 204472579
|  | DataRecorder Modules | Data Rec 2 | RE2 Record Complete |  |  |  |  | 204472580
|  | DataRecorder Modules | Data Rec 2 | RE2 Depth |  |  |  |  | 204472581
|  | DataRecorder Modules | Data Rec 2 | RE2 RecordMode |  |  |  |  | 204472582
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Threshold |  |  |  |  | 204472583
|  | DataRecorder Modules | Data Rec 2 | RE2 Staleness Action |  |  |  |  | 204472584